## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2020-11-01 | 53230 | 53.23 | 7.14 | 7.69 | 150 | 14 | 240 | 29 | NA | 600 | 0.5 | 28 | 1400000 | Plant Availability is 100%
2020-11-02 | 56730 | 56.73 | 7.32 | 7.59 | 135 | 18 | 260 | 24 | NA | - | 0.4 | - | - | 1) Testing samples for Fecal coliform of Effluent & Sludge are not kept. 2) Testing sample for sludge consistency not kept. 3) Plant Availability is 100%
2020-11-03 | 59920 | 59.92 | 7.19 | 7.74 | 140 | 16 | 280 | 26 | NA | - | 0.5 | - | - | 1) Testing samples for Fecal coliform of Effluent & Sludge are not kept. 2) Testing sample for sludge consistency not kept. 3) Plant Availability is 100%
2020-11-04 | 58020 | 58.02 | 7.32 | 7.74 | 145 | 14 | 260 | 21 | NA | 600 | 0.5 | 20 | 1200000 | Plant Availability is 100%
2020-11-05 | 59590 | 59.59 | 7.14 | 7.86 | 135 | 15 | 240 | 26 | NA | 400 | 0.5 | 20 | 1200000 | Plant Availability is 100%
2020-11-06 | 55570 | 55.57 | 7.26 | 7.84 | 150 | 17 | 280 | 22 | NA | 600 | 0.5 | 24 | 1400000 | Plant Availability is 100%
2020-11-07 | 60010 | 60.01 | 7.24 | 7.8 | 140 | 14 | 240 | 24 | NA | 500 | 0.5 | 22 | 1300000 | 1) Testing from Composite samples is started from 07.11.2020
2020-11-08 | 60640 | 60.64 | 7.26 | 7.8 | 130 | 16 | 280 | 26 | NA | 600 | 0.5 | 20 | 1700000 | Plant Availability is 100%
2020-11-09 | 58300 | 58.3 | 7.19 | 7.74 | 140 | 15 | 260 | 28 | NA | 400 | 0.5 | 24.4 | 1100000 | Plant Availability is 100%
2020-11-10 | 56020 | 56.02 | 7.16 | 7.84 | 135 | 12 | 240 | 26 | NA | 500 | 0.6 | 22.6 | 1400000 | Plant Availability is 100%
2020-11-11 | 56850 | 56.85 | 7.19 | 7.6 | 150 | 14 | 280 | 24 | NA | 400 | 0.4 | 24.2 | 1200000 | Plant Availability is 100%
2020-11-12 | 61030 | 61.03 | 7.24 | 7.84 | 140 | 16 | 240 | 26 | NA | 600 | 0.5 | 22.4 | 1400000 | Plant Availability is 100%
2020-11-13 | 58900 | 58.9 | 7.14 | 7.9 | 150 | 15 | 280 | 24 | NA | 500 | 0.5 | 20.6 | 1300000 | Plant Availability is 100%
2020-11-14 | 62930 | 62.93 | 7.19 | 7.94 | 145 | 14 | 260 | 21 | NA | 600 | 0.6 | 22.4 | 1400000 | Plant Availability is 100%
2020-11-15 | 62690 | 62.69 | 7.24 | 7.84 | 140 | 16 | 240 | 28 | NA | 400 | 0.6 | 21.6 | 1200000 | Plant Availability is 100%
2020-11-16 | 57270 | 57.27 | 7.24 | 7.94 | 145 | 14 | 220 | 23 | NA | 500 | 0.5 | 20.6 | 1400000 | Plant Availability is 100%
2020-11-17 | 51220 | 51.22 | 7.4 | 7.84 | 150 | 18 | 240 | 20 | NA | 700 | 0.6 | 22.4 | 1200000 | Plant Availability is 100%
2020-11-18 | 53440 | 53.44 | 7.24 | 7.74 | 160 | 15 | 280 | 24 | NA | 600 | 0.5 | 20.6 | 1400000 | Plant Availability is 100%
2020-11-19 | 47300 | 47.3 | 7.28 | 7.64 | 150 | 14 | 240 | 26 | NA | 500 | 0.5 | 24.2 | 1200000 | Plant Availability is 100%
2020-11-20 | 50550 | 50.55 | 7.25 | 7.84 | 140 | 15 | 260 | 28 | NA | 600 | 0.5 | 22.1 | 1400000 | Plant Availability is 100%
2020-11-21 | 59930 | 59.93 | 7.2 | 7.9 | 150 | 12 | 280 | 26 | NA | 400 | 0.6 | 20.6 | 1300000 | Plant Availability is 100%
2020-11-22 | 63530 | 63.53 | 7.24 | 7.92 | 140 | 16 | 260 | 24 | NA | 500 | 0.5 | 22.4 | 1200000 | Plant Availability is 100%
2020-11-23 | 61480 | 61.48 | 7.19 | 7.72 | 145 | 14 | 240 | 28 | NA | 700 | 0.6 | 20.6 | 1400000 | Plant Availability is 100%
2020-11-24 | 61760 | 61.76 | 7.12 | 7.68 | 160 | 17 | 220 | 24 | NA | 600 | 0.5 | 24.2 | 1200000 | Plant Availability is 100%
2020-11-25 | 59650 | 59.65 | 7.14 | 7.64 | 135 | 16 | 240 | 24 | NA | 700 | 0.5 | 20.6 | 1300000 | Plant Availability is 100%
2020-11-26 | 62360 | 62.36 | 7.27 | 7.89 | 130 | 15 | 260 | 26 | NA | 500 | 0.6 | 22.4 | 1400000 | Plant Availability is 100%
2020-11-27 | 62180 | 62.18 | 7.24 | 7.98 | 140 | 15 | 240 | 24 | NA | 400 | 0.5 | 22.7 | 1200000 | Plant Availability is 100%
2020-11-28 | 61920 | 61.92 | 7.19 | 7.86 | 155 | 16 | 260 | 26 | NA | 600 | 0.5 | 20.6 | 1700000 | Plant Availability is 100%
2020-11-29 | 62950 | 62.95 | 7.24 | 7.84 | 150 | 14 | 220 | 20 | NA | 700 | 0.5 | 21.43 | 1400000 | Plant Availability is 100%
2020-11-30 | 60780 | 60.78 | 7.19 | 7.84 | 150 | 15 | 260 | 22 | NA | 600 | 0.5 | 26.5 | 1400000 | Plant Availability is 100%
Average | 58558.3333 | 58.5583 | 7.2217 | 7.801 | 144.1667 | 15.0667 | 253.3333 | 24.6667 | #DIV/0! | 546.4286 | 0.51667 | 22.2904 | 1332142.8571
Max |  | 63.53 | 7.4 | 7.98 | 160 | 18 | 280 | 29 |  | 700 | 0.6 | 28 | 1700000
Min |  | 47.3 | 7.12 | 7.59 | 130 | 12 | 220 | 20 |  | 400 | 0.4 | 20 | 1100000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2020-11-01 | 23750 | 23.75 | 7.59 | 7.54 | 135 | 16 | 299 | 32 | NA | 500 | 0.5 | 22 | 900000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-02 | 24400 | 24.4 | 7.63 | 7.62 | 156 | 14 | 306 | 30 | NA | - | 0.4 | - | - | 1) Testing samples for Fecal coliform of Effluent & Sludge are not kept. 2) Testing sample for Sludge concentration is not kept. 3) Plant Availablity is 100%
2020-11-03 | 26200 | 26.2 | 7.71 | 7.49 | 158 | 12 | 314 | 28 | NA | - | 0.3 | - | - | 1) Testing samples for Fecal coliform of Effluent & Sludge are not kept. 2) Testing sample for Sludge concentration is not kept 3) Plant Availablity is 100%
2020-11-04 | 27400 | 27.4 | 7.65 | 7.52 | 152 | 10 | 321 | 25 | NA | 500 | 0.4 | 20.6 | 1100000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-05 | 34490 | 34.49 | 7.51 | 7.45 | 154 | 12 | 310 | 23 | NA | 600 | 0.3 | 21 | 1700000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-06 | 38550 | 38.55 | 7.48 | 7.65 | 150 | 15 | 306 | 21 | NA | 500 | 0.3 | 22 | 1300000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-07 | 36200 | 36.2 | 7.56 | 7.68 | 153 | 16 | 308 | 24 | NA | 400 | 0.4 | 20 | 1700000 | 1) Testing from Composite samples is started from 07.11.2020 2) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 3) Plant Availability is 100%
2020-11-08 | 34400 | 34.4 | 7.7 | 7.51 | 158 | 14 | 314 | 22 | NA | 500 | 0.5 | 21 | 1300000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-09 | 35120 | 35.12 | 7.76 | 7.58 | 152 | 16 | 309 | 19 | NA | 700 | 0.3 | 23.4 | 1400000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-10 | 33350 | 33.35 | 7.54 | 7.61 | 155 | 18 | 299 | 20 | NA | 600 | 0.5 | 23.4 | 1300000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-11 | 31750 | 31.75 | 7.63 | 7.66 | 153 | 16 | 306 | 22 | NA | 500 | 0.4 | 22.5 | 1700000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-12 | 35550 | 35.55 | 7.54 | 7.74 | 156 | 19 | 314 | 24 | NA | 400 | 0.5 | 21.4 | 1300000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-13 | 36310 | 36.31 | 7.68 | 7.53 | 150 | 18 | 303 | 22 | NA | 700 | 0.4 | 20.6 | 1400000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-14 | 35310 | 35.31 | 7.44 | 7.48 | 154 | 16 | 299 | 24 | NA | 500 | 0.5 | 21.6 | 1700000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-15 | 32400 | 32.4 | 7.49 | 7.56 | 156 | 18 | 306 | 21 | NA | 700 | 0.3 | 20.6 | 1400000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-16 | 32400 | 32.4 | 7.56 | 7.59 | 152 | 14 | 309 | 25 | NA | 600 | 0.4 | 23.4 | 1700000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-17 | 31900 | 31.9 | 7.61 | 7.58 | 154 | 16 | 306 | 28 | NA | 500 | 0.5 | 20.1 | 1300000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-18 | 33150 | 33.15 | 7.53 | 7.59 | 156 | 18 | 299 | 26 | NA | 400 | 0.4 | 21.6 | 1700000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-19 | 31720 | 31.72 | 7.42 | 7.5 | 153 | 15 | 310 | 24 | NA | 600 | 0.3 | 20.6 | 1300000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-20 | 31430 | 31.43 | 7.45 | 7.38 | 159 | 17 | 316 | 26 | NA | 500 | 0.4 | 21.6 | 1400000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-21 | 29650 | 29.65 | 7.32 | 7.44 | 156 | 19 | 304 | 22 | NA | 700 | 0.5 | 20.6 | 1300000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-22 | 30500 | 30.5 | 7.31 | 7.42 | 150 | 18 | 310 | 25 | NA | 400 | 0.3 | 21.6 | 1400000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-23 | 31530 | 31.53 | 7.29 | 7.4 | 153 | 14 | 314 | 28 | NA | 600 | 0.5 | 20.6 | 1300000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-24 | 32770 | 32.77 | 7.35 | 7.45 | 156 | 17 | 309 | 24 | NA | 500 | 0.4 | 22.5 | 1700000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-25 | 31280 | 31.28 | 7.4 | 7.39 | 153 | 19 | 313 | 20 | NA | 600 | 0.3 | 21.1 | 1400000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-26 | 29160 | 29.16 | 7.45 | 7.5 | 156 | 22 | 306 | 26 | NA | 400 | 0.5 | 20.6 | 1300000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-27 | 31400 | 31.4 | 7.32 | 7.42 | 163 | 24 | 299 | 21 | NA | 700 | 0.3 | 21.3 | 1500000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-28 | 31520 | 31.52 | 7.42 | 7.52 | 153 | 21 | 308 | 23 | NA | 500 | 0.4 | 22.5 | 1700000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-29 | 35220 | 35.22 | 7.45 | 7.38 | 160 | 23 | 312 | 20 | NA | 400 | 0.7 | 23.85 | 1300000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2020-11-30 | 30660 | 30.66 | 7.4 | 7.33 | 156 | 20 | 318 | 22 | NA | 600 | 0.5 | 21.9 | 1400000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
Average | 31982.3333 | 31.9823 | 7.5063 | 7.517 | 154.0667 | 16.9 | 308.2333 | 23.9 | #DIV/0! | 539.2857 | 0.41333 | 21.5696 | 1425000
Max |  | 38.55 | 7.76 | 7.74 | 163 | 24 | 321 | 32 |  | 700 | 0.7 | 23.85 | 1700000
Min |  | 23.75 | 7.29 | 7.33 | 135 | 10 | 299 | 19 |  | 400 | 0.3 | 20 | 900000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2020-11-01 | 22210 | 22.21 | 6.85 | 7.47 | 125 | 16 | 288 | 20 | NA | 700 | 0.4 | 25.9 | 650000 | Plant Availability is 100%
2020-11-02 | 21310 | 21.31 | 6.84 | 7.54 | 112 | 13 | 260 | 17 | NA | - | 0.5 | 25.3 | - | 1) Testing samples for Fecal coliform of Effluent & Sludge are not kept. 2) Plant Availability is 100%
2020-11-03 | 22770 | 22.77 | 6.79 | 7.85 | 118 | 12 | 246 | 15 | NA | 700 | 0.5 | 23.4 | 800000 | Plant Availability is 100%
2020-11-04 | 15270 | 15.27 | 7.23 | 7.74 | 125 | 14 | 260 | 19 | NA | 700 | 0.5 | 27.8 | 900000 | Flow is less as plant was in shutdown for modification in outlet pipeline regarding electromagnetic flowmeter in outlet pipeline.
2020-11-05 | 22030 | 22.03 | 6.64 | 7.54 | 132 | 11 | 256 | 17 | NA | 500 | 0.3 | 30.5 | 500000 | Plant Availability is 100%
2020-11-06 | 22800 | 22.8 | 7.24 | 7.84 | 128 | 13 | 238 | 15 | NA | 400 | 0.4 | 29.2 | 920000 | Plant Availability is 100%
2020-11-07 | 21850 | 21.85 | 7.34 | 7.74 | 135 | 15 | 296 | 18 | NA | 420 | 0.5 | 44.72 | 1200000 | 1) Testing from Composite samples is started from 07.11.2020 2) Plant Availability is 100%
2020-11-08 | 21850 | 21.85 | 7.15 | 7.83 | 130 | 12 | 308 | 22 | NA | 500 | 0.5 | 28.5 | 1000000 | Plant Availability is 100%
2020-11-09 | 22370 | 22.37 | 7.26 | 7.65 | 126 | 14 | 283 | 16 | NA | 550 | 0.3 | 34.63 | 1200000 | Plant Availability is 100%
2020-11-10 | 22620 | 22.62 | 7.34 | 7.56 | 138 | 11 | 246 | 24 | NA | 430 | 0.5 | 31.33 | 1300000 | Plant Availability is 100%
2020-11-11 | 23220 | 23.22 | 7.19 | 7.85 | 140 | 15 | 270 | 26 | NA | 620 | 0.5 | 30.49 | 1100000 | Plant Availability is 100%
2020-11-12 | 22270 | 22.27 | 7.26 | 7.69 | 125 | 11 | 287 | 20 | NA | 700 | 0.4 | 33.86 | 1400000 | Plant Availability is 100%
2020-11-13 | 23220 | 23.22 | 7.32 | 7.85 | 130 | 13 | 298 | 22 | NA | 420 | 0.3 | 29.22 | 1100000 | Plant Availability is 100%
2020-11-14 | 24900 | 24.9 | 7.34 | 7.53 | 120 | 12 | 294 | 19 | NA | 400 | 0.5 | 32.56 | 1600000 | Plant Availability is 100%
2020-11-15 | 23500 | 23.5 | 7.22 | 7.68 | 128 | 15 | 311 | 23 | NA | 600 | 0.5 | 26.78 | 1700000 | Plant Availability is 100%
2020-11-16 | 23550 | 23.55 | 7.15 | 7.84 | 135 | 11 | 280 | 18 | NA | 400 | 0.4 | 27.45 | 1600000 | Plant Availability is 100%
2020-11-17 | 22800 | 22.8 | 7.3 | 7.92 | 132 | 14 | 262 | 22 | NA | 600 | 0.5 | 29.64 | 1500000 | Plant Availability is 100%
2020-11-18 | 20880 | 20.88 | 6.79 | 7.52 | 138 | 12 | 306 | 23 | NA | 500 | 0.5 | 32.64 | 1000000 | Plant Availability is 100%
2020-11-19 | 21060 | 21.06 | 7.05 | 7.64 | 136 | 14 | 270 | 25 | NA | 450 | 0.3 | 24.15 | 1200000 | Plant Availability is 100%
2020-11-20 | 22770 | 22.77 | 7.15 | 7.89 | 130 | 11 | 278 | 20 | NA | 700 | 0.5 | 24.73 | 1400000 | Plant Availability is 100%
2020-11-21 | 23480 | 23.48 | 7.27 | 7.64 | 140 | 15 | 296 | 23 | NA | 450 | 0.5 | 25.18 | 1200000 | Plant Availability is 100%
2020-11-22 | 22580 | 22.58 | 7.19 | 7.84 | 125 | 13 | 276 | 20 | NA | 600 | 0.5 | 33.98 | 1000000 | Plant Availability is 100%
2020-11-23 | 22310 | 22.31 | 7.31 | 7.67 | 135 | 15 | 305 | 22 | NA | 550 | 0.5 | 25.7 | 1200000 | Plant Availability is 100%
2020-11-24 | 22930 | 22.93 | 7.26 | 7.73 | 140 | 12 | 290 | 24 | NA | 700 | 0.5 | 28.86 | 1500000 | Plant Availability is 100%
2020-11-25 | 23190 | 23.19 | 7.34 | 7.56 | 136 | 14 | 300 | 20 | NA | 500 | 0.5 | 29.9 | 1400000 | Plant Availability is 100%
2020-11-26 | 23740 | 23.74 | 7.13 | 7.87 | 125 | 16 | 289 | 25 | NA | 550 | 0.3 | 30.75 | 1200000 | Plant Availability is 100%
2020-11-27 | 23810 | 23.81 | 7.33 | 7.67 | 132 | 13 | 295 | 18 | NA | 400 | 0.5 | 26.76 | 1400000 | Plant Availability is 100%
2020-11-28 | 23530 | 23.53 | 7.29 | 7.8 | 140 | 15 | 276 | 24 | NA | 700 | 0.5 | 24.67 | 1100000 | Plant Availability is 100%
2020-11-29 | 24230 | 24.23 | 7.19 | 7.75 | 135 | 16 | 260 | 26 | NA | 600 | 0.5 | 20.6 | 1300000 | Plant Availability is 100%
2020-11-30 | 24850 | 24.85 | 7.17 | 7.8 | 126 | 14 | 279 | 18 | NA | 500 | 0.5 | 23.74 | 1200000 | Plant Availability is 100%
Average | 22596.6667 | 22.5967 | 7.1643 | 7.7167 | 130.5667 | 13.4 | 280.1 | 20.7 | NA | 546.2069 | 0.45333 | 28.7647 | 1192068.9655
|  | 677.9 | 214.93 | 231.5 | 3917 | 402 | 8403 | 621 |  | 15840 | 13.6 | 862.94 | 34570000
Max |  | 24.9 | 7.34 | 7.92 | 140 | 16 | 311 | 26 |  | 700 | 0.5 | 44.72 | 1700000
Min |  | 15.27 | 6.64 | 7.47 | 112 | 11 | 238 | 15 |  | 400 | 0.3 | 20.6 | 500000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2020-11-01 | 6956 | 6.956 | 7.34 | 7.72 | 140 | 17 | 269 | 20 | NA | 550 | 0.4 | 21.5 | 680000 | Plant Availability is 100%
2020-11-02 | 6801 | 6.801 | 7.37 | 7.79 | 138 | 15 | 271 | 22 | NA | 650 | 0.5 | 23.3 | 650000 | Plant Availability is 100%
2020-11-03 | 6865 | 6.865 | 7.39 | 7.73 | 142 | 16 | 261 | 20 | NA | 700 | 0.5 | 22.8 | 620000 | Plant Availability is 100%
2020-11-04 | 7051 | 7.051 | 7.32 | 7.68 | 138 | 18 | 273 | 22 | NA | 600 | 0.4 | 21.7 | 650000 | Plant Availability is 100%
2020-11-05 | 4980 | 4.98 | 7.27 | 7.78 | 135 | 17 | 267 | 21 | NA | 550 | 0.5 | 22.4 | 550000 | Flow is less as plant was in shutdown for modification in outlet pipeline regarding electromagnetic flowmeter in outlet pipeline.
2020-11-06 | 6974 | 6.974 | 7.11 | 7.69 | 140 | 15 | 258 | 20 | NA | 600 | 0.5 | 23.1 | 500000 | Plant Availability is 100%
2020-11-07 | 7018 | 7.018 | 7.18 | 7.81 | 132 | 16 | 249 | 18 | NA | 500 | 0.5 | 21.9 | 920000 | 1) Testing from Composite samples is started from 07.11.2020. 2) Plant Availabilty is 100%.
2020-11-08 | 6923 | 6.923 | 7.08 | 7.55 | 130 | 17 | 229 | 17 | NA | 700 | 0.5 | 22.2 | 1200000 | Plant Availability is 100%
2020-11-09 | 6859 | 6.859 | 7.2 | 7.79 | 135 | 17 | 240 | 18 | NA | 600 | 0.5 | 20.4 | 1100000 | Plant Availability is 100%
2020-11-10 | 6958 | 6.958 | 7.24 | 7.72 | 128 | 15 | 256 | 29 | NA | 500 | 0.5 | 22 | 1000000 | Plant Availability is 100%
2020-11-11 | 6726 | 6.726 | 7.16 | 7.77 | 136 | 16 | 276 | 22 | NA | 600 | 0.5 | 21.5 | 1300000 | Plant Availability is 100%
2020-11-12 | 6833 | 6.833 | 7.18 | 7.83 | 140 | 15 | 264 | 24 | NA | 700 | 0.5 | 23.2 | 1400000 | Plant Availability is 100%
2020-11-13 | 7657 | 7.657 | 7.24 | 7.76 | 135 | 16 | 270 | 21 | NA | 650 | 0.5 | 21.4 | 1200000 | Plant Availability is 100%
2020-11-14 | 7886 | 7.886 | 7.29 | 7.72 | 130 | 15 | 273 | 23 | NA | 600 | 0.5 | 22.3 | 1400000 | Plant Availability is 100%
2020-11-15 | 7463 | 7.463 | 7.21 | 7.63 | 128 | 14 | 261 | 22 | NA | 500 | 0.5 | 22.5 | 1200000 | Plant Availability is 100%
2020-11-16 | 6946 | 6.946 | 7.26 | 7.71 | 132 | 15 | 269 | 23 | NA | 600 | 0.5 | 23.3 | 1000000 | Plant Availability is 100%
2020-11-17 | 7532 | 7.532 | 7.11 | 7.73 | 145 | 16 | 274 | 20 | NA | 400 | 0.5 | 22.7 | 1600000 | Plant Availability is 100%
2020-11-18 | 7199 | 7.199 | 7.16 | 7.57 | 148 | 17 | 259 | 21 | NA | 500 | 0.5 | 21.2 | 1300000 | Plant Availability is 100%
2020-11-19 | 6980 | 6.98 | 7.19 | 7.74 | 145 | 16 | 240 | 22 | NA | 600 | 0.5 | 23.6 | 1200000 | Plant Availability is 100%
2020-11-20 | 7435 | 7.435 | 7.22 | 7.7 | 140 | 15 | 256 | 21 | NA | 500 | 0.5 | 22.4 | 1100000 | Plant Availability is 100%
2020-11-21 | 6401 | 6.401 | 7.17 | 7.72 | 145 | 16 | 263 | 22 | NA | 700 | 0.5 | 21.8 | 1400000 | Plant Availability is 100%
2020-11-22 | 7062 | 7.062 | 7.2 | 7.67 | 148 | 17 | 270 | 23 | NA | 500 | 0.5 | 22.6 | 1600000 | Plant Availability is 100%
2020-11-23 | 6737 | 6.737 | 7.24 | 7.79 | 140 | 16 | 266 | 24 | NA | 600 | 0.5 | 23.2 | 1300000 | Plant Availability is 100%
2020-11-24 | 6951 | 6.951 | 7.29 | 7.75 | 145 | 17 | 276 | 23 | NA | 500 | 0.5 | 22.5 | 1200000 | Plant Availability is 100%
2020-11-25 | 6737 | 6.737 | 7.16 | 7.63 | 140 | 16 | 273 | 22 | NA | 600 | 0.5 | 21.8 | 1400000 | Plant Availability is 100%
2020-11-26 | 7227 | 7.227 | 7.23 | 7.67 | 142 | 17 | 269 | 21 | NA | 700 | 0.5 | 22.4 | 1600000 | Plant Availability is 100%
2020-11-27 | 7091 | 7.091 | 7.36 | 7.49 | 148 | 16 | 261 | 24 | NA | 600 | 0.5 | 23.5 | 1400000 | Plant Availability is 100%
2020-11-28 | 6955 | 6.955 | 7.26 | 7.37 | 140 | 15 | 275 | 23 | NA | 550 | 0.5 | 22.6 | 1300000 | Plant Availability is 100%
2020-11-29 | 7172 | 7.172 | 7.18 | 7.44 | 145 | 16 | 268 | 24 | NA | 600 | 0.5 | 23.1 | 1400000 | Plant Availability is 100%
2020-11-30 | 7265 | 7.265 | 7.29 | 7.58 | 142 | 17 | 272 | 23 | NA | 500 | 0.5 | 21.8 | 1200000 | Plant Availability is 100%
Average | 6988 | 6.988 | 7.23 | 7.6843 | 139.0667 | 16.0333 | 263.6 | 21.8333 | #DIV/0! | 581.6667 | 0.49333 | 22.3567 | 1145666.6667
209.64
Max |  | 7.886 | 7.39 | 7.83 | 148 | 18 | 276 | 29 |  | 700 | 0.5 | 23.6 | 1600000
Min |  | 4.98 | 7.08 | 7.37 | 128 | 14 | 229 | 17 |  | 400 | 0.4 | 20.4 | 500000