## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-04-01 | 61040 | 61.04 | 7.21 | 7.75 | 135 | 13 | 228 | 20 | NA | 500 | 0.5 | 24.4 | 1200000
2021-04-02 | 65770 | 65.77 | 7.18 | 7.68 | 160 | 16 | 222 | 22 | NA | 600 | 0.4 | 22.1 | 1400000
2021-04-03 | 60460 | 60.46 | 7.14 | 7.64 | 150 | 17 | 270 | 24 | NA | 700 | 0.4 | 21.38 | 1300000
2021-04-04 | 61150 | 61.15 | 7.16 | 7.84 | 145 | 15 | 252 | 20 | NA | 600 | 0.5 | 22.04 | 1200000
2021-04-05 | 59310 | 59.31 | 7.26 | 7.84 | 140 | 15 | 298 | 24 | NA | 500 | 0.4 | 24.43 | 1200000
2021-04-06 | 63840 | 63.84 | 7.21 | 7.78 | 145 | 14 | 262 | 28 | NA | 700 | 0.4 | 24.4 | 1700000
2021-04-07 | 62210 | 62.21 | 7.18 | 7.76 | 150 | 17 | 290 | 26 | NA | 500 | 0.6 | 23.87 | 1400000
2021-04-08 | 60610 | 60.61 | 7.17 | 7.64 | 135 | 16 | 258 | 22 | NA | 600 | 0.4 | 25.22 | 1400000
2021-04-09 | 60880 | 60.88 | 7.28 | 7.74 | 145 | 14 | 246 | 26 | NA | 500 | 0.5 | 21.11 | 1200000
2021-04-10 | 60910 | 60.91 | 7.19 | 7.64 | 155 | 14 | 240 | 24 | NA | 600 | 0.4 | 21.69 | 1700000
2021-04-11 | 61290 | 61.29 | 7.18 | 7.69 | 135 | 18 | 270 | 26 | NA | 500 | 0.5 | 20.27 | 1400000
2021-04-12 | 60700 | 60.7 | 7.27 | 7.56 | 130 | 14 | 220 | 24 | NA | 700 | 0.4 | 21.75 | 1300000
2021-04-13 | 57700 | 57.7 | 7.24 | 7.82 | 150 | 18 | 268 | 28 | NA | 500 | 0.5 | 23.75 | 1200000
2021-04-14 | 58320 | 58.32 | 7.22 | 7.84 | 130 | 16 | 290 | 26 | NA | 600 | 0.2 | 23.54 | 1400000
2021-04-15 | 60920 | 60.92 | 7.28 | 7.64 | 140 | 15 | 228 | 28 | NA | 500 | 0.2 | 25.25 | 1400000
2021-04-16 | 62910 | 62.91 | 7.15 | 7.74 | 145 | 14 | 220 | 22 | NA | 600 | 0.2 | 23.54 | 1200000
2021-04-17 | 57910 | 57.91 | 7.16 | 7.84 | 150 | 16 | 284 | 28 | NA | 500 | 0.3 | 22.99 | 1400000
2021-04-18 | 42290 | 42.29 | 7.19 | 7.8 | 140 | 12 | 270 | 26 | NA | 700 | 0.2 | 23.75 | 1300000 | Ghaghar Nalla MPS was in shutdown from 07:00 PM on 18.04.2021 to 11:00 AM on 19.04.2021 for maintenance work of header line from Ghagharnalla MPS to Numayadahi STP.
2021-04-19 | 33510 | 33.51 | 7.29 | 7.64 | 130 | 17 | 256 | 20 | NA | 500 | 0.2 | 25.72 | 1400000 | Ghaghar Nalla MPS was in shutdown from 07:00 PM on 18.04.2021 to 11:00 AM on 19.04.2021 for maintenance work of header line from Ghagharnalla MPS to Numayadahi STP.
2021-04-20 | 62320 | 62.32 | 7.16 | 7.74 | 140 | 15 | 240 | 28 | NA | 600 | 0.3 | 21.86 | 1200000
2021-04-21 | 65500 | 65.5 | 7.19 | 7.8 | 130 | 16 | 232 | 26 | NA | 500 | 0.2 | 23.23 | 1400000
2021-04-22 | 60480 | 60.48 | 7.24 | 7.64 | 140 | 15 | 284 | 26 | NA | 700 | 0.3 | 23.23 | 1300000
2021-04-23 | 55760 | 55.76 | 7.15 | 7.84 | 130 | 14 | 236 | 28 | NA | 600 | 0.2 | 22.44 | 1400000
2021-04-24 | 58250 | 58.25 | 7.18 | 7.72 | 145 | 12 | 246 | 26 | NA | 400 | 0.2 | 20.7 | 1400000
2021-04-25 | 61420 | 61.42 | 7.26 | 7.87 | 140 | 18 | 252 | 24 | NA | 600 | 0.2 | 21.86 | 1400000
2021-04-26 | 62320 | 62.32 | 7.21 | 7.69 | 150 | 16 | 232 | 28 | NA | 700 | 0.3 | 22.59 | 1700000
2021-04-27 | 60360 | 60.36 | 7.24 | 7.64 | 145 | 14 | 228 | 24 | NA | 500 | 0.2 | 23.1 | 1400000
2021-04-28 | 64290 | 64.29 | 7.16 | 7.74 | 150 | 18 | 264 | 24 | NA | 600 | 0.2 | 21.58 | 1300000
2021-04-29 | 62820 | 62.82 | 7.17 | 7.88 | 145 | 12 | 228 | 26 | NA | 500 | 0.3 | 23 | 1200000
2021-04-30 | 63350 | 63.35 | 7.16 | 7.76 | 150 | 15 | 252 | 28 | NA | 700 | 0.3 | 24.94 | 1700000
Average | 59620 | 59.62 | 7.2027 | 7.74 | 142.5 | 15.2 | 252.2 | 25.0667 | NA | 576.6667 | 0.33 | 22.991 | 1370000
1788.6
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 33510 | 33.51 | 7.14 | 7.56 | 130 | 12 | 220 | 20 |  | 400 | 0.2 | 20.27 | 1200000
Max | 65770 | 65.77 | 7.29 | 7.88 | 160 | 18 | 298 | 28 |  | 700 | 0.6 | 25.72 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-04-01 | 36880 | 36.88 | 7.44 | 7.55 | 159 | 22 | 311 | 36 | NA | 600 | 0.4 | 22.1 | 1400000
2021-04-02 | 34360 | 34.36 | 7.35 | 7.61 | 163 | 24 | 315 | 38 | NA | 500 | 0.5 | 23.8 | 1700000
2021-04-03 | 34780 | 34.78 | 7.41 | 7.58 | 156 | 21 | 319 | 40 | NA | 600 | 0.4 | 22.2 | 1300000
2021-04-04 | 34490 | 34.49 | 7.33 | 7.52 | 153 | 23 | 314 | 37 | NA | 700 | 0.3 | 24.5 | 1700000
2021-04-05 | 32270 | 32.27 | 7.38 | 7.62 | 159 | 22 | 312 | 39 | NA | 500 | 0.5 | 23.3 | 1400000
2021-04-06 | 34740 | 34.74 | 7.42 | 7.59 | 163 | 19 | 319 | 34 | NA | 600 | 0.4 | 22.4 | 1100000
2021-04-07 | 36930 | 36.93 | 7.35 | 7.55 | 166 | 20 | 313 | 36 | NA | 700 | 0.3 | 21.9 | 1300000
2021-04-08 | 32730 | 32.73 | 7.43 | 7.57 | 159 | 23 | 308 | 38 | NA | 600 | 0.4 | 23.1 | 1700000
2021-04-09 | 30860 | 30.86 | 7.45 | 7.62 | 166 | 21 | 303 | 35 | NA | 500 | 0.5 | 24.9 | 1400000
2021-04-10 | 28940 | 28.94 | 7.38 | 7.65 | 169 | 24 | 307 | 37 | NA | 700 | 0.3 | 25.5 | 1100000
2021-04-11 | 31010 | 31.01 | 7.42 | 7.58 | 163 | 22 | 312 | 39 | NA | 600 | 0.4 | 22.1 | 1300000
2021-04-12 | 27820 | 27.82 | 7.35 | 7.55 | 159 | 20 | 318 | 41 | NA | 700 | 0.3 | 25.8 | 1400000
2021-04-13 | 30500 | 30.5 | 7.28 | 7.61 | 156 | 19 | 322 | 42 | NA | 600 | 0.4 | 26.9 | 1100000
2021-04-14 | 28800 | 28.8 | 7.31 | 7.65 | 153 | 21 | 316 | 38 | NA | 700 | 0.3 | 23.7 | 1700000
2021-04-15 | 28340 | 28.34 | 7.41 | 7.63 | 159 | 23 | 313 | 36 | NA | 600 | 0.5 | 24.6 | 1400000
2021-04-16 | 29400 | 29.4 | 7.35 | 7.57 | 156 | 22 | 319 | 34 | NA | 700 | 0.4 | 21.4 | 1600000
2021-04-17 | 29550 | 29.55 | 7.37 | 7.67 | 153 | 24 | 322 | 36 | NA | 800 | 0.3 | 22.2 | 1500000
2021-04-18 | 30200 | 30.2 | 7.44 | 7.52 | 159 | 21 | 328 | 33 | NA | 700 | 0.2 | 23.4 | 1300000
2021-04-19 | 27880 | 27.88 | 7.46 | 7.55 | 163 | 20 | 332 | 32 | NA | 800 | 0.3 | 22.5 | 1400000
2021-04-20 | 28210 | 28.21 | 7.38 | 7.58 | 166 | 22 | 325 | 30 | NA | 600 | 0.4 | 24.5 | 1700000
2021-04-21 | 29310 | 29.31 | 7.35 | 7.61 | 173 | 19 | 315 | 35 | NA | 800 | 0.3 | 23.3 | 1300000
2021-04-22 | 28700 | 28.7 | 7.42 | 7.51 | 159 | 21 | 321 | 33 | NA | 700 | 0.2 | 25.9 | 1100000
2021-04-23 | 28840 | 28.84 | 7.44 | 7.55 | 163 | 23 | 318 | 30 | NA | 600 | 0.3 | 22.1 | 1300000
2021-04-24 | 31190 | 31.19 | 7.37 | 7.52 | 156 | 25 | 312 | 32 | NA | 500 | 0.4 | 21.9 | 1700000
2021-04-25 | 30870 | 30.87 | 7.39 | 7.65 | 159 | 22 | 308 | 34 | NA | 700 | 0.2 | 24.3 | 1100000
2021-04-26 | 22130 | 22.13 | 7.35 | 7.61 | 153 | 20 | 303 | 36 | NA | 800 | 0.3 | 25.4 | 1400000 | Plant availability is less than 100% due to maintenance of drain valve of clarisettler no. 1.
2021-04-27 | 21700 | 21.7 | 7.42 | 7.55 | 156 | 18 | 310 | 33 | NA | 700 | 0.2 | 25.8 | 1300000
2021-04-28 | 22270 | 22.27 | 7.44 | 7.59 | 163 | 16 | 316 | 35 | NA | 800 | 0.2 | 28.6 | 1700000
2021-04-29 | 27230 | 27.23 | 7.47 | 7.63 | 159 | 18 | 325 | 37 | NA | 700 | 0.2 | 26.2 | 1100000
2021-04-30 | 29010 | 29.01 | 7.38 | 7.55 | 153 | 20 | 333 | 39 | NA | 800 | 0.2 | 23.9 | 1300000
Average | 29998 | 29.998 | 7.3913 | 7.5847 | 159.8 | 21.1667 | 316.3 | 35.8333 | NA | 663.3333 | 0.33333 | 23.94 | 1393333.3333
899.94
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 21700 | 21.7 | 7.28 | 7.51 | 153 | 16 | 303 | 30 |  | 500 | 0.2 | 21.4 | 1100000
Max | 36930 | 36.93 | 7.47 | 7.67 | 173 | 25 | 333 | 42 |  | 800 | 0.5 | 28.6 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-04-01 | 24700 | 24.7 | 7.15 | 7.78 | 128 | 14 | 256 | 22 | NA | 600 | 0.3 | 24.53 | 1300000
2021-04-02 | 23780 | 23.78 | 7.25 | 7.54 | 125 | 13 | 264 | 20 | NA | 400 | 0.2 | 23.25 | 1700000
2021-04-03 | 23750 | 23.75 | 7.11 | 7.63 | 130 | 15 | 250 | 24 | NA | 500 | 0.3 | 25.43 | 1400000
2021-04-04 | 25640 | 25.64 | 7.28 | 7.78 | 138 | 13 | 276 | 21 | NA | 400 | 0.3 | 23.4 | 1700000
2021-04-05 | 25720 | 25.72 | 7.14 | 7.82 | 142 | 15 | 256 | 20 | NA | 600 | 0.3 | 25.3 | 1300000
2021-04-06 | 25740 | 25.74 | 7.18 | 7.79 | 132 | 14 | 280 | 22 | NA | 500 | 0.3 | 24.01 | 1200000
2021-04-07 | 25510 | 25.51 | 7.25 | 7.64 | 140 | 16 | 260 | 25 | NA | 400 | 0.3 | 23.96 | 1400000
2021-04-08 | 25150 | 25.15 | 7.17 | 7.69 | 138 | 14 | 273 | 21 | NA | 600 | 0.4 | 24.83 | 1700000
2021-04-09 | 24850 | 24.85 | 7.18 | 7.73 | 145 | 13 | 260 | 20 | NA | 500 | 0.3 | 23.65 | 1300000
2021-04-10 | 26220 | 26.22 | 7.15 | 7.69 | 136 | 15 | 253 | 19 | NA | 400 | 0.3 | 24.72 | 1700000
2021-04-11 | 25860 | 25.86 | 7.1 | 7.62 | 140 | 14 | 275 | 23 | NA | 600 | 0.2 | 25.32 | 1300000
2021-04-12 | 26270 | 26.27 | 7.09 | 7.69 | 150 | 16 | 283 | 20 | NA | 400 | 0.3 | 23.42 | 1700000
2021-04-13 | 26320 | 26.32 | 7.13 | 7.78 | 138 | 13 | 253 | 22 | NA | 500 | 0.3 | 23.73 | 1400000
2021-04-14 | 26710 | 26.71 | 7.21 | 7.62 | 148 | 12 | 274 | 18 | NA | 700 | 0.4 | 24.17 | 1200000
2021-04-15 | 25200 | 25.2 | 7.17 | 7.64 | 140 | 13 | 248 | 23 | NA | 600 | 0.2 | 23.18 | 1300000
2021-04-16 | 26830 | 26.83 | 7.24 | 7.77 | 142 | 11 | 269 | 20 | NA | 700 | 0.3 | 25.22 | 1700000
2021-04-17 | 25470 | 25.47 | 7.12 | 7.64 | 135 | 13 | 261 | 21 | NA | 400 | 0.3 | 22.57 | 1200000
2021-04-18 | 26400 | 26.4 | 7.2 | 7.6 | 132 | 12 | 240 | 19 | NA | 600 | 0.3 | 21.17 | 1700000
2021-04-19 | 25500 | 25.5 | 7.13 | 7.8 | 128 | 14 | 273 | 20 | NA | 700 | 0.2 | 24.64 | 1300000
2021-04-20 | 25370 | 25.37 | 7.1 | 7.78 | 132 | 11 | 256 | 18 | NA | 400 | 0.3 | 25.14 | 1200000
2021-04-21 | 26410 | 26.41 | 7.22 | 7.88 | 130 | 13 | 263 | 21 | NA | 600 | 0.2 | 23.11 | 1400000
2021-04-22 | 25860 | 25.86 | 7.3 | 7.64 | 125 | 12 | 248 | 20 | NA | 700 | 0.2 | 22.15 | 1700000
2021-04-23 | 25410 | 25.41 | 7.13 | 7.54 | 132 | 14 | 259 | 23 | NA | 500 | 0.3 | 23.88 | 1300000
2021-04-24 | 26810 | 26.81 | 7.2 | 7.69 | 144 | 13 | 278 | 20 | NA | 700 | 0.2 | 25.54 | 1200000
2021-04-25 | 26610 | 26.61 | 7.16 | 7.76 | 138 | 11 | 262 | 19 | NA | 500 | 0.3 | 24.85 | 1700000
2021-04-26 | 26070 | 26.07 | 7.24 | 7.61 | 148 | 14 | 280 | 21 | NA | 600 | 0.2 | 25.48 | 1300000
2021-04-27 | 26300 | 26.3 | 7.15 | 7.45 | 132 | 12 | 259 | 18 | NA | 700 | 0.2 | 27.02 | 1700000
2021-04-28 | 25260 | 25.26 | 7.19 | 7.69 | 138 | 13 | 284 | 20 | NA | 500 | 0.2 | 25.48 | 1400000
2021-04-29 | 24950 | 24.95 | 7.03 | 7.54 | 150 | 15 | 290 | 22 | NA | 700 | 0.2 | 26.04 | 1700000
2021-04-30 | 24920 | 24.92 | 7.24 | 7.68 | 160 | 16 | 265 | 20 | NA | 600 | 0.3 | 24.98 | 1700000
Average | 25653 | 25.653 | 7.1737 | 7.6837 | 137.8667 | 13.4667 | 264.9333 | 20.7333 | NA | 553.3333 | 0.27 | 24.339 | 1460000
769.59
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 23750 | 23.75 | 7.03 | 7.45 | 125 | 11 | 240 | 18 |  | 400 | 0.2 | 21.17 | 1200000
Max | 26830 | 26.83 | 7.3 | 7.88 | 160 | 16 | 290 | 25 |  | 700 | 0.4 | 27.02 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-04-01 | 7452 | 7.452 | 7.34 | 7.54 | 140 | 14 | 266 | 22 | NA | 400 | 0.5 | 21.19 | 1200000
2021-04-02 | 7410 | 7.41 | 7.16 | 7.44 | 135 | 16 | 246 | 20 | NA | 600 | 0.5 | 23.11 | 1400000
2021-04-03 | 7219 | 7.219 | 7.22 | 7.61 | 142 | 14 | 255 | 23 | NA | 500 | 0.3 | 22.41 | 1300000
2021-04-04 | 7013 | 7.013 | 7.17 | 7.39 | 132 | 15 | 263 | 25 | NA | 400 | 0.3 | 20.52 | 1200000
2021-04-05 | 7622 | 7.622 | 7.26 | 7.46 | 135 | 16 | 270 | 22 | NA | 500 | 0.2 | 21.32 | 1400000
2021-04-06 | 7721 | 7.721 | 7.14 | 7.36 | 130 | 14 | 252 | 20 | NA | 400 | 0.3 | 22.16 | 1300000
2021-04-07 | 7256 | 7.256 | 7.21 | 7.49 | 137 | 16 | 267 | 22 | NA | 500 | 0.2 | 20.63 | 1200000
2021-04-08 | 7522 | 7.522 | 7.3 | 7.51 | 132 | 14 | 248 | 24 | NA | 400 | 0.3 | 21.83 | 1400000
2021-04-09 | 7640 | 7.64 | 7.41 | 7.58 | 135 | 15 | 256 | 21 | NA | 500 | 0.4 | 22.24 | 1300000
2021-04-10 | 7920 | 7.92 | 7.28 | 7.43 | 140 | 17 | 264 | 23 | NA | 600 | 0.2 | 21.56 | 1600000
2021-04-11 | 7225 | 7.225 | 7.33 | 7.62 | 136 | 14 | 251 | 22 | NA | 400 | 0.3 | 22.19 | 1200000
2021-04-12 | 7523 | 7.523 | 7.24 | 7.44 | 142 | 16 | 262 | 20 | NA | 500 | 0.4 | 23.31 | 1400000
2021-04-13 | 7342 | 7.342 | 7.15 | 7.32 | 137 | 15 | 256 | 23 | NA | 400 | 0.2 | 21.76 | 1300000
2021-04-14 | 7435 | 7.435 | 7.22 | 7.46 | 140 | 13 | 268 | 21 | NA | 500 | 0.3 | 22.49 | 1600000
2021-04-15 | 7316 | 7.316 | 7.29 | 7.52 | 132 | 15 | 246 | 24 | NA | 400 | 0.2 | 23.15 | 1400000
2021-04-16 | 7699 | 7.699 | 7.18 | 7.41 | 142 | 14 | 259 | 22 | NA | 500 | 0.3 | 20.64 | 1300000
2021-04-17 | 7504 | 7.504 | 7.31 | 7.56 | 135 | 15 | 252 | 20 | NA | 400 | 0.2 | 21.33 | 1200000
2021-04-18 | 7431 | 7.431 | 7.16 | 7.29 | 130 | 13 | 263 | 23 | NA | 500 | 0.2 | 22.17 | 1400000
2021-04-19 | 7588 | 7.588 | 7.26 | 7.41 | 135 | 15 | 260 | 21 | NA | 400 | 0.3 | 21.4 | 1300000
2021-04-20 | 7667 | 7.667 | 7.11 | 7.26 | 140 | 14 | 271 | 23 | NA | 500 | 0.2 | 22.53 | 1200000
2021-04-21 | 7968 | 7.968 | 7.27 | 7.38 | 145 | 15 | 266 | 20 | NA | 400 | 0.2 | 23.16 | 1400000
2021-04-22 | 7560 | 7.56 | 7.19 | 7.37 | 135 | 14 | 255 | 22 | NA | 600 | 0.2 | 20.72 | 1700000
2021-04-23 | 7320 | 7.32 | 7.24 | 7.44 | 142 | 13 | 255 | 19 | NA | 500 | 0.3 | 21.59 | 1400000
2021-04-24 | 7319 | 7.319 | 7.2 | 7.64 | 145 | 15 | 264 | 21 | NA | 400 | 0.2 | 22.76 | 1300000
2021-04-25 | 6917 | 6.917 | 7.18 | 7.48 | 138 | 13 | 247 | 23 | NA | 500 | 0.2 | 23.29 | 1200000
2021-04-26 | 7701 | 7.701 | 7.13 | 7.39 | 132 | 15 | 254 | 20 | NA | 600 | 0.3 | 20.81 | 1400000
2021-04-27 | 7695 | 7.695 | 7.28 | 7.46 | 136 | 14 | 263 | 22 | NA | 400 | 0.2 | 24.14 | 1600000
2021-04-28 | 7275 | 7.275 | 7.13 | 7.29 | 130 | 13 | 250 | 20 | NA | 500 | 0.2 | 22.69 | 1300000
2021-04-29 | 7137 | 7.137 | 7.23 | 7.36 | 132 | 14 | 258 | 23 | NA | 400 | 0.2 | 20.32 | 1200000
2021-04-30 | 7340 | 7.34 | 7.31 | 7.49 | 140 | 15 | 269 | 21 | NA | 500 | 0.2 | 23.24 | 1400000
Average | 7457.9 | 7.4579 | 7.23 | 7.4467 | 136.7333 | 14.5333 | 258.5333 | 21.7333 | NA | 470 | 0.26667 | 22.022 | 1350000
223.737
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 6917 | 6.917 | 7.11 | 7.26 | 130 | 13 | 246 | 19 |  | 400 | 0.2 | 20.32 | 1200000
Max | 7968 | 7.968 | 7.41 | 7.64 | 145 | 17 | 271 | 25 |  | 600 | 0.5 | 24.14 | 1700000