## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-08-01 | 49810 | 49.81 | 7.15 | 7.69 | 140 | 12 | 304 | 36 | 240 | 28 | NA | 500 | 0.2 | 22.87 | 1300000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-08-02 | 45990 | 45.99 | 7.19 | 7.82 | 150 | 14 | 328 | 40 | 244 | 24 | NA | 400 | 0.3 | 24.57 | 1200000
2021-08-03 | 49510 | 49.51 | 7.27 | 7.68 | 130 | 14 | 344 | 36 | 264 | 26 | NA | 600 | 0.2 | 22.53 | 1200000
2021-08-04 | 58120 | 58.12 | 7.26 | 7.84 | 150 | 13 | 328 | 32 | 232 | 28 | NA | 500 | 0.3 | 24.2 | 1300000 | 1. Inlet gate of Ghagharnalla MPS is closed upto 90% and bypass gate at tapping point is opened due to rise in river level due to flood on 04.08.2021. Accordingly, Raw sewage is pumped to Numayadahi STP on 04.08.2021. Accordingly, Raw sewage is pumped to Numayadahi STP. 2. Raw sewage from Sasur Kadheri SPS & Lukerganj SPS is pumped to Ghaghanalla MPS.
2021-08-05 | 41310 | 41.31 | 7.26 | 7.72 | 140 | 16 | 284 | 32 | 262 | 20 | NA | 500 | 0.2 | 22.56 | 1200000 | 1. Inlet gate of Ghagharnalla MPS is closed upto 90% and bypass gate at tapping point is opened due to rise in river level due to flood on 04.08.2021. Accordingly, Raw sewage is pumped to Numayadahi STP. 2. Sasur Kadheri SPS is shut down at 11 AM on 05.08.2021 due to rise in river level due to flood. 3. Raw sewage from Lukerganj SPS only is pumped to Ghaghanalla MPS.
2021-08-06 | 17200 | 17.2 | 7.17 | 7.69 | 145 | 15 | 304 | 36 | 232 | 24 | NA | 600 | 0.3 | 23.31 | 1300000
2021-08-07 | 18420 | 18.42 | 7.08 | 7.62 | 145 | 13 | 360 | 44 | 296 | 28 | NA | 700 | 0.2 | 22.67 | 1200000
2021-08-08 | 42470 | 42.47 | 7.19 | 7.84 | 130 | 14 | 352 | 44 | 280 | 26 | NA | 600 | 0.3 | 22.15 | 1300000
2021-08-09 | 77120 | 77.12 | 7.12 | 7.82 | 130 | 12 | 328 | 40 | 288 | 28 | NA | 400 | 0.3 | 22.61 | 1700000
2021-08-10 | 40980 | 40.98 | 7.16 | 7.89 | 140 | 14 | 356 | 44 | 276 | 26 | NA | 500 | 0.2 | 22.93 | 1200000
2021-08-11 | 33200 | 33.2 | 7.24 | 7.54 | 145 | 13 | 344 | 40 | 290 | 28 | NA | 600 | 0.3 | 24.58 | 1700000
2021-08-12 | 33140 | 33.14 | 7.21 | 7.75 | 150 | 14 | 332 | 36 | 272 | 24 | NA | 700 | 0.2 | 22.61 | 1700000
2021-08-13 | 31740 | 31.74 | 7.18 | 7.62 | 140 | 16 | 320 | 40 | 284 | 26 | NA | 500 | 0.3 | 26.09 | 1200000
2021-08-14 | 55110 | 55.11 | 7.19 | 7.74 | 145 | 13 | 325 | 36 | 264 | 28 | NA | 600 | 0.2 | 22.02 | 1200000 | 1. Inlet gate of tapping point at Ghagharnalla is opened on 14.08.2021 due to fall in river level after flood on 14.08.2021. Accordingly, Raw sewage is pumped to Numayadahi STP. 2. Sasur Kadheri SPS is in shut down as tapping point is submerged in raw water due to flood. 3. Raw sewage from Lukerganj SPS only is pumped to Ghaghanalla MPS.
2021-08-15 | 76340 | 76.34 | 7.18 | 7.6 | 130 | 16 | 312 | 40 | 276 | 26 | NA | 600 | 0.3 | 24.25 | 1300000
2021-08-16 | 40080 | 40.08 | 7.14 | 7.69 | 135 | 12 | 304 | 44 | 214 | 24 | NA | 500 | 0.2 | 22.82 | 1200000
2021-08-17 | 20110 | 20.11 | 7.16 | 7.64 | 140 | 12 | 336 | 40 | 288 | 26 | NA | 700 | 0.2 | 22.33 | 1700000
2021-08-18 | 22760 | 22.76 | 7.18 | 7.84 | 135 | 14 | 304 | 36 | 264 | 24 | NA | 500 | 0.2 | 22.5 | 1300000
2021-08-19 | 22340 | 22.34 | 7.22 | 7.48 | 130 | 16 | 344 | 36 | 292 | 24 | NA | 700 | 0.3 | 24.6 | 1400000
2021-08-20 | 23890 | 23.89 | 7.27 | 7.78 | 140 | 18 | 328 | 40 | 276 | 18 | NA | 700 | 0.2 | 24.1 | 1400000
2021-08-21 | 22830 | 22.83 | 7.22 | 7.64 | 135 | 14 | 308 | 40 | 256 | 26 | NA | 600 | 0.2 | 23.26 | 1300000
2021-08-22 | 13940 | 13.94 | 7.16 | 7.62 | 140 | 13 | 324 | 40 | 248 | 24 | NA | 500 | 0.2 | 23.53 | 1300000
2021-08-23 | 2950 | 2.95 | - | - | - | - | - | - | - | - | - | - | - | 22.33 | - | 1. Shutdown of Numyadahi STP, Ghagharnalla MPS & Sasur Kadheri SPS was taken into shutdown at 0100 hrs at 23.08.2021. 2. Alternate treatment through Bio-remediation is in place at Ghagharnalla MPS & Sasur Kadheri SPS. 3. Raw sewage from Lukerganj SPS is pumped to Ghaghanalla MPS and then bypassed to river.
2021-08-24 | Plant is in Shutdown for replacement of header line of HNC pumps at Ghagharnalla MPS | [12 empty] | 23.38 | Plant is in Shutdown for replacement of header line of HNC pumps at Ghagharnalla MPS
2021-08-25 | [13 empty] | 22.4
2021-08-26 | [13 empty] | 23.35
2021-08-27 | [13 empty] | 24.6
2021-08-28 | [13 empty] | 22.33
2021-08-29 | [13 empty] | 24.1
2021-08-30 | [13 empty] | 22.4
2021-08-31 | [13 empty] | 22.33
Average | 36493.913 | 36.4939 | 7.1909 | 7.7068 | 139.3182 | 14 | 325.8636 | 38.7273 | 265.3636 | 25.2727 | NA | 568.1818 | 0.24091 | 23.2358 | 1345454.5455
839.36
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 2950 | 2.95 | 7.08 | 7.48 | 130 | 12 | 284 | 32 | 214 | 18 |  | 400 | 0.2 | 22.02 | 1200000
Max | 77120 | 77.12 | 7.27 | 7.89 | 150 | 18 | 360 | 44 | 296 | 28 |  | 700 | 0.3 | 26.09 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-08-01 | 21950 | 21.95 | 7.51 | 7.43 | 147 | 21 | 360 | 32 | 314 | 33 | NA | 500 | 0.2 | 24.3 | 1300000 | 1) Raw sewage received at site is less as outlet gate at Amitabh Bachchan Culvert is closed on 01.08.2021 at 1640 hrs due to rise in river level due to flood. 2) Raw sewage from Allahpur drain and local house connections is received at site only.
2021-08-02 | 8770 | 8.77 | 7.54 | 7.36 | 145 | 18 | 356 | 36 | 310 | 38 | NA | 700 | 0.3 | 22.6 | 1200000 | 1) Raw sewage received at site is less as outlet gate at Amitabh Bachchan Culvert is closed on 01.08.2021 at 1640 hrs due to rise in river level due to flood. 2) Raw sewage received at site is less as raw sewage from Allahapur drain is stopped on 02.08.2021 at 0430 hrs due to rise in river level due to flood. 3) Raw sewage from local house connections is received at site only.
2021-08-03 | 4570 | 4.57 | 7.47 | 7.38 | 153 | 16 | 352 | 40 | 304 | 31 | NA | 800 | 0.2 | 25.1 | 1700000
2021-08-04 | 4660 | 4.66 | 7.57 | 7.42 | 149 | 18 | 364 | 48 | 312 | 35 | NA | 600 | 0.2 | 24.8 | 1400000
2021-08-05 | 3330 | 3.33 | 7.42 | 7.51 | 105 | 15 | 360 | 44 | 317 | 40 | NA | 700 | 0.3 | 26.3 | 1100000
2021-08-06 | 3700 | 3.7 | 7.39 | 7.48 | 100 | 14 | 356 | 36 | 325 | 34 | NA | 500 | 0.3 | 23.5 | 1400000
2021-08-07 | 2980 | 2.98 | 7.44 | 7.52 | 113 | 15 | 360 | 40 | 319 | 32 | NA | 800 | 0.2 | 25.4 | 1300000
2021-08-08 | 6390 | 6.39 | 7.38 | 7.47 | 110 | 12 | 352 | 32 | 315 | 35 | NA | 600 | 0.2 | 24 | 1200000
2021-08-09 | 4720 | 4.72 | 7.5 | 7.48 | 117 | 19 | 364 | 44 | 318 | 31 | NA | 500 | 0.2 | 24.7 | 1700000
2021-08-10 | 8700 | 8.7 | 7.41 | 7.49 | 107 | 17 | 360 | 36 | 320 | 30 | NA | 700 | 0.3 | 25.5 | 1300000
2021-08-11 | 14220 | 14.22 | 7.32 | 7.43 | 113 | 14 | 252 | 32 | 235 | 32 | NA | 500 | 0.2 | 24.8 | 1200000
2021-08-12 | 9340 | 9.34 | 7.36 | 7.52 | 103 | 12 | 260 | 36 | 242 | 29 | NA | 700 | 0.2 | 25.1 | 1100000
2021-08-13 | 8030 | 8.03 | 7.41 | 7.56 | 120 | 16 | 256 | 40 | 238 | 25 | NA | 800 | 0.3 | 23.1 | 1700000
2021-08-14 | 7910 | 7.91 | 7.45 | 7.53 | 107 | 13 | 252 | 32 | 234 | 30 | NA | 600 | 0.3 | 23.4 | 1100000
2021-08-15 | 6300 | 6.3 | 7.34 | 7.51 | 100 | 11 | 268 | 36 | 241 | 24 | NA | 500 | 0.2 | 24.4 | 1400000
2021-08-16 | 5340 | 5.34 | 7.43 | 7.54 | 117 | 18 | 264 | 40 | 237 | 28 | NA | 800 | 0.2 | 25.2 | 1300000
2021-08-17 | 5570 | 5.57 | 7.38 | 7.49 | 137 | 17 | 348 | 32 | 301 | 33 | NA | 700 | 0.2 | 24.2 | 1400000
2021-08-18 | 11250 | 11.25 | 7.46 | 7.55 | 153 | 20 | 356 | 44 | 316 | 31 | NA | 500 | 0.3 | 22.3 | 1700000 | 1) Raw sewage from Allahapur is started on 18.08.2021 at 1000 hrs due to fall in river level after flood. 2) Raw sewage received at site is less as outlet gate at Amitabh Bachchan Culvert is closed on 01.08.2021 at 1640 hrs due to rise in river level due to flood. 3) Currently, raw sewage from Allahpur drain & local house connections is received at site.
2021-08-19 | 17080 | 17.08 | 7.37 | 7.47 | 147 | 19 | 352 | 36 | 303 | 30 | NA | 700 | 0.2 | 25.5 | 1400000
2021-08-20 | 21180 | 21.18 | 7.45 | 7.52 | 155 | 23 | 360 | 40 | 315 | 32 | NA | 600 | 0.3 | 24.1 | 1300000
2021-08-21 | 28080 | 28.08 | 7.32 | 7.44 | 145 | 25 | 356 | 32 | 319 | 34 | NA | 800 | 0.2 | 24.8 | 1100000 | 1) Raw sewage from outlet gate at Amitabh Bachchan Culvert is started on 21.08.2021 at 1500 hrs due to fall in river level after flood. 2) Currently, complete sewage is received at site.
2021-08-22 | 30840 | 30.84 | 7.28 | 7.53 | 150 | 22 | 364 | 40 | 325 | 38 | NA | 700 | 0.2 | 22.4 | 1300000 | Plant availability is 100%
2021-08-23 | 33790 | 33.79 | 7.41 | 7.56 | 153 | 23 | 360 | 44 | 312 | 35 | NA | 500 | 0.2 | 24.6 | 1700000 | Plant availability is 100%
2021-08-24 | 38000 | 38 | 7.38 | 7.48 | 155 | 21 | 356 | 32 | 308 | 40 | NA | 800 | 0.2 | 23.5 | 1400000 | Plant availability is 100%
2021-08-25 | 45140 | 45.14 | 7.43 | 7.64 | 162 | 26 | 348 | 32 | 304 | 36 | NA | 600 | 0.3 | 24.5 | 1600000 | Plant availability is 100%
2021-08-26 | 43020 | 43.02 | 7.35 | 7.42 | 158 | 23 | 352 | 36 | 298 | 39 | NA | 700 | 0.3 | 23.2 | 1300000 | Plant availability is 100%
2021-08-27 | 42910 | 42.91 | 7.37 | 7.54 | 160 | 25 | 360 | 40 | 304 | 34 | NA | 500 | 0.2 | 24 | 1400000 | Plant availability is 100%
2021-08-28 | 40930 | 40.93 | 7.35 | 7.51 | 157 | 24 | 364 | 44 | 315 | 37 | NA | 700 | 0.2 | 24.6 | 1100000 | Plant availability is 100%
2021-08-29 | 38460 | 38.46 | 7.42 | 7.55 | 155 | 23 | 352 | 40 | 323 | 32 | NA | 800 | 0.3 | 25.1 | 1300000 | Plant availability is 100%
2021-08-30 | 45310 | 45.31 | 7.38 | 7.59 | 158 | 26 | 360 | 36 | 326 | 41 | NA | 600 | 0.2 | 24.8 | 1200000 | Plant availability is 100%
2021-08-31 | 44770 | 44.77 | 7.34 | 7.52 | 160 | 24 | 356 | 40 | 312 | 33 | NA | 500 | 0.2 | 24.4 | 1200000 | Plant availability is 100%
Average | 19588.3871 | 19.5884 | 7.4074 | 7.4981 | 135.8387 | 19.0323 | 338.0645 | 37.8065 | 298.7742 | 33.2903 | NA | 645.1613 | 0.23548 | 24.329 | 1348387.0968
607.24
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 2980 | 2.98 | 7.28 | 7.36 | 100 | 11 | 252 | 32 | 234 | 24 |  | 500 | 0.2 | 22.3 | 1100000
Max | 45310 | 45.31 | 7.57 | 7.64 | 162 | 26 | 364 | 48 | 326 | 41 |  | 800 | 0.3 | 26.3 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-08-01 | 27610 | 27.61 | 7.33 | 7.44 | 129 | 12 | 344 | 40 | 286 | 20 | NA | 600 | 0.3 | 25 | 1400000 | Plant availability is 100%
2021-08-02 | 25640 | 25.64 | 7.19 | 7.36 | 135 | 14 | 352 | 36 | 278 | 22 | NA | 700 | 0.2 | 24.5 | 1200000 | Plant availability is 100%
2021-08-03 | 25280 | 25.28 | 7.32 | 7.48 | 133 | 11 | 348 | 32 | 294 | 21 | NA | 400 | 0.3 | 24 | 1500000 | Plant availability is 100%
2021-08-04 | 28630 | 28.63 | 7.36 | 7.49 | 133 | 12 | 328 | 44 | 292 | 23 | NA | 600 | 0.2 | 24.3 | 1300000 | Plant availability is 100%
2021-08-05 | 25930 | 25.93 | 7.18 | 7.36 | 125 | 14 | 312 | 40 | 272 | 24 | NA | 400 | 0.3 | 24.4 | 1500000 | Plant availability is 100%
2021-08-06 | 27070 | 27.07 | 7.24 | 7.44 | 110 | 13 | 316 | 36 | 286 | 22 | NA | 700 | 0.2 | 24.5 | 1400000 | Plant availability is 100%
2021-08-07 | 26810 | 26.81 | 7.36 | 7.48 | 100 | 11 | 304 | 32 | 274 | 20 | NA | 500 | 0.3 | 24 | 1200000 | Plant availability is 100%
2021-08-08 | 23760 | 23.76 | 7.19 | 7.36 | 95 | 13 | 296 | 40 | 272 | 21 | NA | 600 | 0.2 | 24.1 | 1600000 | Plant availability is 100%
2021-08-09 | 19070 | 19.07 | 7.16 | 7.25 | 90 | 12 | 284 | 36 | 266 | 19 | NA | 400 | 0.3 | 24.1 | 1500000 | 1) Inlet gate of nearby nalla is closed and bypass gate is opened due to flood. 2) Raw sewage from Kalimandir SPS & Vivekanand park SPS is received in the plant only.
2021-08-10 | 24970 | 24.97 | 7.19 | 7.23 | 85 | 14 | 260 | 40 | 236 | 21 | NA | 700 | 0.2 | 24.4 | 1300000
2021-08-11 | 22900 | 22.9 | 7.24 | 7.36 | 80 | 11 | 220 | 32 | 214 | 20 | NA | 800 | 0.3 | 24.6 | 1600000
2021-08-12 | 20240 | 20.24 | 7.31 | 7.49 | 85 | 13 | 204 | 40 | 210 | 23 | NA | 500 | 0.2 | 24.9 | 1400000
2021-08-13 | 25610 | 25.61 | 7.29 | 7.36 | 90 | 12 | 208 | 44 | 196 | 20 | NA | 400 | 0.3 | 24 | 1500000
2021-08-14 | 25450 | 25.45 | 7.28 | 7.39 | 93 | 13 | 196 | 36 | 188 | 22 | NA | 600 | 0.2 | 24.3 | 1200000
2021-08-15 | 24660 | 24.66 | 7.33 | 7.46 | 90 | 14 | 212 | 40 | 204 | 23 | NA | 700 | 0.3 | 24.5 | 1400000 | 1) Inlet gate is opened and bypass gate is closed due to fall in river level after flood. 2) Complete raw sewage is received in the plant.
2021-08-16 | 26180 | 26.18 | 7.28 | 7.36 | 126 | 12 | 244 | 32 | 228 | 20 | NA | 500 | 0.2 | 25 | 1700000 | Plant availability is 100%
2021-08-17 | 25400 | 25.4 | 7.35 | 7.49 | 132 | 13 | 296 | 36 | 276 | 19 | NA | 600 | 0.3 | 24.2 | 1300000 | Plant availability is 100%
2021-08-18 | 25360 | 25.36 | 7.33 | 7.44 | 135 | 11 | 328 | 40 | 302 | 20 | NA | 700 | 0.2 | 24.6 | 1400000 | Plant availability is 100%
2021-08-19 | 24830 | 24.83 | 7.39 | 7.47 | 141 | 13 | 324 | 36 | 295 | 21 | NA | 800 | 0.2 | 24.4 | 1600000 | Plant availability is 100%
2021-08-20 | 24980 | 24.98 | 7.31 | 7.43 | 135 | 12 | 312 | 40 | 288 | 19 | NA | 700 | 0.3 | 24.5 | 1400000 | Plant availability is 100%
2021-08-21 | 25360 | 25.36 | 7.24 | 7.36 | 144 | 13 | 328 | 44 | 292 | 22 | NA | 600 | 0.2 | 24.3 | 1200000 | Plant availability is 100%
2021-08-22 | 25980 | 25.98 | 7.41 | 7.49 | 138 | 11 | 332 | 44 | 304 | 23 | NA | 700 | 0.3 | 24.6 | 1300000 | Plant availability is 100%
2021-08-23 | 25780 | 25.78 | 7.34 | 7.51 | 141 | 13 | 320 | 36 | 292 | 19 | NA | 600 | 0.2 | 25.2 | 1400000 | Plant availability is 100%
2021-08-24 | 25800 | 25.8 | 7.39 | 7.48 | 135 | 12 | 336 | 44 | 307 | 22 | NA | 700 | 0.2 | 24.8 | 1300000 | Plant availability is 100%
2021-08-25 | 26690 | 26.69 | 7.43 | 7.51 | 141 | 13 | 324 | 40 | 304 | 20 | NA | 600 | 0.2 | 24.6 | 1200000 | Plant availability is 100%
2021-08-26 | 21010 | 21.01 | 7.37 | 7.46 | 144 | 12 | 312 | 36 | 298 | 21 | NA | 700 | 0.3 | 24.5 | 1400000 | Raw sewage received is less due breakage of retaining wall at near-by nalla
2021-08-27 | 18860 | 18.86 | 7.45 | 7.57 | 141 | 11 | 320 | 40 | 305 | 19 | NA | 600 | 0.2 | 24.7 | 1300000
2021-08-28 | 23770 | 23.77 | 7.31 | 7.43 | 147 | 14 | 328 | 44 | 292 | 18 | NA | 500 | 0.2 | 24.4 | 1400000 | Plant availability is 100%
2021-08-29 | 23940 | 23.94 | 7.42 | 7.52 | 141 | 12 | 332 | 40 | 302 | 17 | NA | 600 | 0.2 | 24.5 | 1200000 | Plant availability is 100%
2021-08-30 | 24870 | 24.87 | 7.51 | 7.61 | 144 | 13 | 324 | 36 | 296 | 18 | NA | 700 | 0.3 | 25.2 | 1400000 | Plant availability is 100%
2021-08-31 | 26730 | 26.73 | 7.39 | 7.48 | 138 | 11 | 320 | 40 | 297 | 20 | NA | 600 | 0.2 | 24.3 | 1300000 | Plant availability is 100%
Average | 24811.9355 | 24.8119 | 7.319 | 7.4374 | 122.4516 | 12.4194 | 298.8387 | 38.5806 | 272.4516 | 20.6129 | NA | 606.4516 | 0.24194 | 24.4968 | 1380645.1613
769.17
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 18860 | 18.86 | 7.16 | 7.23 | 80 | 11 | 196 | 32 | 188 | 17 |  | 400 | 0.2 | 24 | 1200000
Max | 28630 | 28.63 | 7.51 | 7.61 | 147 | 14 | 352 | 44 | 307 | 24 |  | 800 | 0.3 | 25.2 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-08-01 | 7980 | 7.98 | 7.11 | 7.39 | 135 | 15 | 304 | 38 | 246 | 23 | NA | 600 | 0.3 | 22.14 | 1400000 | Plant availability is 100%
2021-08-02 | 7950 | 7.95 | 7.21 | 7.67 | 140 | 16 | 312 | 42 | 255 | 24 | NA | 500 | 0.2 | 23.33 | 1600000 | Plant availability is 100%
2021-08-03 | 7920 | 7.92 | 7.29 | 7.48 | 132 | 14 | 296 | 36 | 262 | 22 | NA | 400 | 0.2 | 21.54 | 1700000 | Plant availability is 100%
2021-08-04 | 7790 | 7.79 | 7.15 | 7.36 | 135 | 16 | 308 | 40 | 250 | 20 | NA | 500 | 0.3 | 23.42 | 1400000 | Plant availability is 100%
2021-08-05 | 7910 | 7.91 | 7.24 | 7.59 | 110 | 15 | 314 | 44 | 264 | 25 | NA | 400 | 0.2 | 22.24 | 1300000 | Plant availability is 100%
2021-08-06 | 7990 | 7.99 | 7.17 | 7.51 | 105 | 16 | 300 | 40 | 271 | 21 | NA | 500 | 0.2 | 20.86 | 1600000 | Plant availability is 100%
2021-08-07 | 7940 | 7.94 | 7.25 | 7.63 | 100 | 17 | 292 | 36 | 266 | 22 | NA | 600 | 0.3 | 21.16 | 1400000 | Plant availability is 100%
2021-08-08 | 7500 | 7.5 | 7.14 | 7.55 | 95 | 16 | 288 | 42 | 276 | 24 | NA | 500 | 0.2 | 22.46 | 1700000 | Plant availability is 100%
2021-08-09 | 7760 | 7.76 | 7.12 | 7.71 | 90 | 14 | 296 | 38 | 259 | 23 | NA | 700 | 0.2 | 21.64 | 1400000 | Plant availability is 100%
2021-08-10 | 6804 | 6.804 | 7.33 | 7.58 | 85 | 15 | 276 | 36 | 270 | 22 | NA | 600 | 0.2 | 23.29 | 1600000 | Plant availability is 100%
2021-08-11 | 5880 | 5.88 | 7.13 | 7.42 | 80 | 16 | 268 | 40 | 265 | 24 | NA | 500 | 0.3 | 21.11 | 1300000 | Plant availability is 100%
2021-08-12 | 7690 | 7.69 | 7.18 | 7.33 | 105 | 17 | 280 | 44 | 294 | 26 | NA | 600 | 0.2 | 20.13 | 1400000 | Plant availability is 100%
2021-08-13 | 7890 | 7.89 | 7.26 | 7.64 | 115 | 16 | 292 | 36 | 285 | 23 | NA | 500 | 0.3 | 21.22 | 1600000 | Plant availability is 100%
2021-08-14 | 7680 | 7.68 | 7.19 | 7.54 | 125 | 14 | 288 | 38 | 268 | 25 | NA | 400 | 0.2 | 20.34 | 1200000 | Plant availability is 100%
2021-08-15 | 7600 | 7.6 | 7.29 | 7.71 | 135 | 15 | 304 | 42 | 260 | 22 | NA | 500 | 0.2 | 21.49 | 1300000 | Plant availability is 100%
2021-08-16 | 7700 | 7.7 | 7.24 | 7.61 | 130 | 14 | 296 | 36 | 277 | 24 | NA | 600 | 0.2 | 22.66 | 1600000 | Plant availability is 100%
2021-08-17 | 7820 | 7.82 | 7.31 | 7.43 | 138 | 16 | 308 | 40 | 256 | 21 | NA | 500 | 0.3 | 23.36 | 1400000 | Plant availability is 100%
2021-08-18 | 7900 | 7.9 | 7.16 | 7.32 | 145 | 15 | 312 | 44 | 267 | 23 | NA | 400 | 0.2 | 21.41 | 1300000 | Plant availability is 100%
2021-08-19 | 7460 | 7.46 | 7.27 | 7.54 | 140 | 14 | 300 | 38 | 248 | 22 | NA | 500 | 0.3 | 22.21 | 1600000 | Plant availability is 100%
2021-08-20 | 7410 | 7.41 | 7.22 | 7.47 | 146 | 13 | 316 | 36 | 260 | 20 | NA | 600 | 0.2 | 20.77 | 1400000 | Plant availability is 100%
2021-08-21 | 7510 | 7.51 | 7.15 | 7.31 | 136 | 15 | 304 | 40 | 255 | 24 | NA | 500 | 0.2 | 21.78 | 1700000 | Plant availability is 100%
2021-08-22 | 7420 | 7.42 | 7.36 | 7.66 | 130 | 16 | 292 | 44 | 246 | 21 | NA | 400 | 0.2 | 22.62 | 1300000 | Plant availability is 100%
2021-08-23 | 7620 | 7.62 | 7.17 | 7.59 | 135 | 14 | 308 | 38 | 272 | 23 | NA | 500 | 0.3 | 23.32 | 1400000 | Plant availability is 100%
2021-08-24 | 7910 | 7.91 | 7.11 | 7.44 | 142 | 15 | 320 | 42 | 261 | 22 | NA | 600 | 0.2 | 21.42 | 1600000 | Plant availability is 100%
2021-08-25 | 7950 | 7.95 | 7.27 | 7.63 | 140 | 14 | 312 | 36 | 242 | 20 | NA | 500 | 0.3 | 22.17 | 1400000 | Plant availability is 100%
2021-08-26 | 7390 | 7.39 | 7.14 | 7.57 | 136 | 15 | 300 | 40 | 258 | 21 | NA | 400 | 0.2 | 20.67 | 1200000 | Plant availability is 100%
2021-08-27 | 7830 | 7.83 | 7.23 | 7.72 | 145 | 16 | 310 | 44 | 268 | 23 | NA | 500 | 0.2 | 23.15 | 1400000 | Plant availability is 100%
2021-08-28 | 7540 | 7.54 | 7.31 | 7.64 | 138 | 14 | 316 | 38 | 254 | 22 | NA | 400 | 0.2 | 21.58 | 1600000 | Plant availability is 100%
2021-08-29 | 7500 | 7.5 | 7.17 | 7.34 | 135 | 15 | 304 | 42 | 241 | 20 | NA | 500 | 0.3 | 22.26 | 1700000 | Plant availability is 100%
2021-08-30 | 7630 | 7.63 | 7.25 | 7.59 | 130 | 14 | 296 | 36 | 260 | 23 | NA | 600 | 0.2 | 20.68 | 1300000 | Plant availability is 100%
2021-08-31 | 7880 | 7.88 | 7.16 | 7.48 | 132 | 16 | 308 | 40 | 255 | 21 | NA | 500 | 0.2 | 21.88 | 1400000 | Plant availability is 100%
Average | 7637.2258 | 7.6372 | 7.2123 | 7.5306 | 125.3226 | 15.0968 | 300.6452 | 39.5484 | 261.6452 | 22.4516 | NA | 509.6774 | 0.23226 | 21.881 | 1458064.5161
236.754
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 5880 | 5.88 | 7.11 | 7.31 | 80 | 13 | 268 | 36 | 241 | 20 |  | 400 | 0.2 | 20.13 | 1200000
Max | 7990 | 7.99 | 7.36 | 7.72 | 146 | 17 | 320 | 44 | 294 | 26 |  | 700 | 0.3 | 23.42 | 1700000