## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2020-12-01 | 60240 | 60.24 | 7.18 | 7.89 | 130 | 12 | 260 | 26 | NA | 400 | 0.5 | 21.4 | 1200000
2020-12-02 | 61780 | 61.78 | 7.21 | 7.8 | 150 | 14 | 240 | 24 | NA | 500 | 0.6 | 20.6 | 1700000
2020-12-03 | 50620 | 50.62 | 7.16 | 7.69 | 150 | 15 | 290 | 18 | NA | 400 | 0.5 | 24.4 | 1700000 | MPS was in shutdown as Inlet Gate of Receiving chamber fell down at 09:25 PM on 03.12.2020.
2020-12-04 | 16970 | 16.97 | 7.24 | 7.67 | 165 | 13 | 250 | 20 | NA | 600 | 0.5 | 20.1 | 1400000 | Inlet gate of receiving chamber was repaired on 04.12.2020 at 11:50 AM on 04.12.2020. During this, due to accumulation of sewage, temporary retaining wall was broken. Its repaing was started.
2020-12-05 | 44990 | 44.99 | 7.34 | 7.82 | 130 | 17 | 260 | 22 | NA | 500 | 0.4 | 26.5 | 1400000 | Repairing of temporay retaining wall is completed.
2020-12-06 | 58120 | 58.12 | 7.19 | 7.84 | 140 | 11 | 208 | 26 | NA | 600 | 0.5 | 31.3 | 1200000
2020-12-07 | 52380 | 52.38 | 7.24 | 7.88 | 130 | 12 | 250 | 20 | NA | 700 | 0.4 | 20.1 | 1400000
2020-12-08 | 62370 | 62.37 | 7.19 | 7.84 | 155 | 14 | 260 | 22 | NA | 400 | 0.5 | 21.5 | 1200000
2020-12-09 | 61800 | 61.8 | 7.24 | 7.64 | 135 | 16 | 236 | 24 | NA | 600 | 0.6 | 22.7 | 1400000
2020-12-10 | 47090 | 47.09 | 7.15 | 7.75 | 140 | 15 | 240 | 28 | NA | 700 | 0.5 | 25.4 | 1300000
2020-12-11 | 59120 | 59.12 | 7.32 | 7.54 | 135 | 17 | 300 | 24 | NA | 500 | 0.4 | 21.76 | 1700000
2020-12-12 | 61730 | 61.73 | 7.34 | 7.67 | 132 | 16 | 208 | 26 | NA | 600 | 0.5 | 20.1 | 1400000
2020-12-13 | 58130 | 58.13 | 7.24 | 7.84 | 140 | 15 | 228 | 28 | NA | 500 | 0.4 | 25.4 | 1200000
2020-12-14 | 60540 | 60.54 | 7.25 | 7.89 | 146 | 14 | 260 | 22 | NA | 600 | 0.5 | 22.7 | 1300000
2020-12-15 | 63250 | 63.25 | 7.22 | 7.77 | 140 | 15 | 267 | 24 | NA | 400 | 0.5 | 23.5 | 1400000
2020-12-16 | 34990 | 34.99 | 7.3 | 7.69 | 135 | 16 | 258 | 21 | NA | 600 | 0.5 | 22.3 | 1600000 | Retaining wall at Ghagharnalla MPS is broken due to heavy rains in night.
2020-12-17 | 30810 | 30.81 | 7.36 | 7.52 | 130 | 14 | 268 | 24 | NA | 500 | 0.3 | 22.1 | 1300000 | Retaining wall at Ghagharnalla MPS is broken due to heavy rains in night. Repairing work is in progress.
2020-12-18 | 40580 | 40.58 | 7.26 | 7.61 | 140 | 13 | 254 | 19 | NA | 600 | 0.5 | 24.4 | 1700000 | Retaining wall at Ghagharnalla MPS is broken due to heavy rains in night. Repairing work is in progress.
2020-12-19 | 46210 | 46.21 | 7.32 | 7.53 | 136 | 15 | 268 | 22 | NA | 700 | 0.4 | 25.1 | 1400000 | Retaining wall at Ghagharnalla MPS is broken due to heavy rains in night. Repairing work is completed
2020-12-20 | 56540 | 56.54 | 7.2 | 7.46 | 145 | 14 | 276 | 20 | NA | 400 | 0.5 | 23.5 | 1200000
2020-12-21 | 55050 | 55.05 | 7.28 | 7.59 | 130 | 16 | 262 | 23 | NA | 600 | 0.4 | 22.6 | 1600000
2020-12-22 | 52020 | 52.02 | 7.16 | 7.42 | 140 | 17 | 255 | 21 | NA | 500 | 0.5 | 25.2 | 1400000
2020-12-23 | 56550 | 56.55 | 7.27 | 7.55 | 135 | 13 | 266 | 24 | NA | 600 | 0.4 | 24.3 | 1300000
2020-12-24 | 47600 | 47.6 | 7.32 | 7.68 | 150 | 15 | 273 | 22 | NA | 700 | 0.5 | 23.6 | 1700000
2020-12-25 | 51210 | 51.21 | 7.39 | 7.54 | 145 | 13 | 281 | 18 | NA | 600 | 0.4 | 22.8 | 1400000
2020-12-26 | 57240 | 57.24 | 7.4 | 7.84 | 150 | 16 | 268 | 22 | NA | 500 | 0.5 | 21.7 | 1200000
2020-12-27 | 55860 | 55.86 | 7.19 | 7.8 | 140 | 17 | 254 | 24 | NA | 400 | 0.6 | 22.1 | 1400000 | Aeration tank no. 3 is under maintenance due to problem in diffusers.
2020-12-28 | 59310 | 59.31 | 7.21 | 7.64 | 130 | 13 | 260 | 26 | NA | 600 | 0.4 | 22.3 | 1700000 | Aeration tank no. 3 is under maintenance due to problem in diffusers.
2020-12-29 | 57650 | 57.65 | 7.24 | 7.78 | 145 | 17 | 240 | 28 | NA | 700 | 0.5 | 24.4 | 1300000 | 1) Maintenace for Aeration tank no. 3 is completed & it is taken into operation. 2) Aeration tank no. 2 is under maintenance due to problem in diffusers.
2020-12-30 | 57910 | 57.91 | 7.14 | 7.64 | 135 | 16 | 208 | 26 | NA | 500 | 0.4 | 20.1 | 1400000 | Aeration tank no. 2 is under maintenance due to problem in diffusers.
2020-12-31 | 60570 | 60.57 | 7.24 | 7.62 | 150 | 12 | 284 | 28 | NA | 600 | 0.5 | 25.5 | 1400000 | Aeration tank no. 2 is under maintenance due to problem in diffusers.
Average | 52878.3871 | 52.8784 | 7.2513 | 7.6916 | 140.4516 | 14.6129 | 255.871 | 23.2903 |  | 551.6129 | 0.47097 | 23.2084 | 1416129.0323
Sum | 1639230 | 1639.23 | 224.79 | 238.44 | 4354 | 453 | 7932 | 722 | NA | 17100 | 14.6 | 719.46 | 43900000
Source: | Logbook of Labarotory at Sewage Treament Plant
Max |  | 63.25 | 7.4 | 7.89 | 165 | 17 | 300 | 28 | 0 | 700 | 0.6 | 31.3 | 1700000
Min |  | 16.97 | 7.14 | 7.42 | 130 | 11 | 208 | 18 | 0 | 400 | 0.3 | 20.1 | 1200000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2020-12-01 | 31460 | 31.46 | 7.38 | 7.44 | 153 | 22 | 309 | 25 | NA | 400 | 0.4 | 20.5 | 1300000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate.
2020-12-02 | 33010 | 33.01 | 7.35 | 7.42 | 156 | 23 | 316 | 22 | NA | 500 | 0.3 | 23.1 | 1700000
2020-12-03 | 33510 | 33.51 | 7.31 | 7.41 | 153 | 20 | 299 | 20 | NA | 700 | 0.4 | 20 | 1400000
2020-12-04 | 31500 | 31.5 | 7.29 | 7.38 | 156 | 22 | 304 | 23 | NA | 400 | 0.5 | 21.9 | 1700000
2020-12-05 | 28830 | 28.83 | 7.28 | 7.59 | 159 | 25 | 318 | 21 | NA | 500 | 0.4 | 23.8 | 1300000
2020-12-06 | 33510 | 33.51 | 7.31 | 7.43 | 150 | 23 | 310 | 20 | NA | 400 | 0.3 | 20.1 | 1400000
2020-12-07 | 32710 | 32.71 | 7.35 | 7.4 | 153 | 20 | 321 | 18 | NA | 700 | 0.5 | 21.3 | 1700000
2020-12-08 | 27320 | 27.32 | 7.33 | 7.42 | 156 | 18 | 299 | 20 | NA | 500 | 0.4 | 24.2 | 1300000
2020-12-09 | 30880 | 30.88 | 7.29 | 7.5 | 153 | 21 | 306 | 23 | NA | 400 | 0.3 | 23.8 | 1400000
2020-12-10 | 31100 | 31.1 | 7.31 | 7.41 | 160 | 23 | 313 | 25 | NA | 500 | 0.4 | 20.5 | 1300000
2020-12-11 | 27950 | 27.95 | 7.35 | 7.51 | 157 | 20 | 320 | 23 | NA | 700 | 0.5 | 23.2 | 1700000
2020-12-12 | 25660 | 25.66 | 7.28 | 7.45 | 153 | 22 | 315 | 21 | NA | 600 | 0.3 | 25.5 | 1100000
2020-12-13 | 29050 | 29.05 | 7.32 | 7.48 | 150 | 18 | 312 | 19 | NA | 400 | 0.4 | 21.9 | 1400000
2020-12-14 | 29660 | 29.66 | 7.18 | 7.43 | 156 | 20 | 305 | 22 | NA | 500 | 0.5 | 22.7 | 1300000
2020-12-15 | 35190 | 35.19 | 7.2 | 7.45 | 159 | 22 | 310 | 20 | NA | 600 | 0.4 | 21.4 | 1700000
2020-12-16 | 36540 | 36.54 | 7.19 | 7.42 | 153 | 19 | 314 | 17 | NA | 700 | 0.3 | 23 | 1400000
2020-12-17 | 35580 | 35.58 | 7.22 | 7.45 | 156 | 21 | 318 | 20 | NA | 500 | 0.4 | 20.3 | 1100000
2020-12-18 | 33370 | 33.37 | 7.26 | 7.38 | 160 | 18 | 306 | 18 | NA | 600 | 0.5 | 23.13 | 1400000
2020-12-19 | 31970 | 31.97 | 7.28 | 7.41 | 153 | 20 | 302 | 21 | NA | 400 | 0.4 | 20.5 | 1300000
2020-12-20 | 31780 | 31.78 | 7.19 | 7.37 | 157 | 22 | 299 | 23 | NA | 700 | 0.3 | 24.9 | 1700000
2020-12-21 | 30420 | 30.42 | 7.25 | 7.51 | 159 | 17 | 314 | 21 | NA | 600 | 0.4 | 24.2 | 1100000
2020-12-22 | 32330 | 32.33 | 7.18 | 7.35 | 163 | 18 | 308 | 18 | NA | 400 | 0.3 | 21.7 | 1400000
2020-12-23 | 34530 | 34.53 | 7.29 | 7.41 | 156 | 20 | 320 | 20 | NA | 600 | 0.4 | 26.9 | 1300000
2020-12-24 | 33810 | 33.81 | 7.17 | 7.32 | 153 | 22 | 312 | 21 | NA | 500 | 0.5 | 20.3 | 1700000
2020-12-25 | 35610 | 35.61 | 7.21 | 7.38 | 150 | 23 | 306 | 17 | NA | 700 | 0.4 | 22.2 | 1400000
2020-12-26 | 36130 | 36.13 | 7.25 | 7.45 | 157 | 17 | 313 | 19 | NA | 600 | 0.5 | 25.8 | 1100000
2020-12-27 | 37920 | 37.92 | 7.31 | 7.51 | 153 | 19 | 299 | 20 | NA | 400 | 0.4 | 27.9 | 1300000
2020-12-28 | 34020 | 34.02 | 7.35 | 7.53 | 160 | 16 | 305 | 22 | NA | 500 | 0.3 | 24.3 | 1400000
2020-12-29 | 33920 | 33.92 | 7.28 | 7.48 | 163 | 18 | 310 | 18 | NA | 700 | 0.4 | 23.3 | 1100000
2020-12-30 | 38280 | 38.28 | 7.38 | 7.57 | 156 | 20 | 316 | 20 | NA | 400 | 0.5 | 25.7 | 1700000
2020-12-31 | 34020 | 34.02 | 7.26 | 7.43 | 153 | 17 | 318 | 18 | NA | 700 | 0.4 | 23.1 | 1300000
Average | 32631.2903 | 32.6313 | 7.2774 | 7.4416 | 155.6774 | 20.1935 | 310.2258 | 20.4839 | NA | 541.9355 | 0.4 | 22.9397 | 1400000
Sum | 1011570 | 1011.57 | 225.6 | 230.69 | 4826 | 626 | 9617 | 635 | NA | 16800 | 12.4 | 711.13 | 43400000
Source: | Logbook of Labarotory at Sewage Treament Plant
Max |  | 38.28 | 7.38 | 7.59 | 163 | 25 | 321 | 25 | 0 | 700 | 0.5 | 27.9 | 1700000
Min |  | 25.66 | 7.17 | 7.32 | 150 | 16 | 299 | 17 | 0 | 400 | 0.3 | 20 | 1100000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2020-12-01 | 25280 | 25.28 | 7.3 | 7.72 | 130 | 15 | 286 | 25 | NA | 700 | 0.4 | 27.69 | 1400000
2020-12-02 | 24110 | 24.11 | 7.08 | 7.47 | 145 | 13 | 314 | 22 | NA | 500 | 0.5 | 34.82 | 1200000
2020-12-03 | 24150 | 24.15 | 7.18 | 7.53 | 136 | 15 | 270 | 26 | NA | 600 | 0.5 | 26.62 | 1400000
2020-12-04 | 24460 | 24.46 | 6.97 | 7.63 | 140 | 17 | 298 | 28 | NA | 400 | 0.4 | 21.3 | 1100000
2020-12-05 | 24240 | 24.24 | 7.24 | 7.54 | 137 | 14 | 280 | 25 | NA | 600 | 0.5 | 26.66 | 1300000
2020-12-06 | 24500 | 24.5 | 7.05 | 7.47 | 145 | 16 | 306 | 27 | NA | 400 | 0.5 | 28.75 | 1300000
2020-12-07 | 24300 | 24.3 | 7.23 | 7.69 | 130 | 13 | 290 | 25 | NA | 450 | 0.5 | 25.62 | 1400000
2020-12-08 | 24850 | 24.85 | 6.92 | 7.64 | 122 | 15 | 282 | 27 | NA | 700 | 0.5 | 26.99 | 1300000
2020-12-09 | 23810 | 23.81 | 7.18 | 7.72 | 140 | 17 | 292 | 22 | NA | 500 | 0.4 | 26.37 | 1400000
2020-12-10 | 22550 | 22.55 | 7.26 | 7.88 | 152 | 16 | 310 | 25 | NA | 600 | 0.6 | 25.88 | 1200000
2020-12-11 | 24600 | 24.6 | 7.16 | 7.71 | 132 | 14 | 276 | 23 | NA | 500 | 0.4 | 24.8 | 1300000
2020-12-12 | 22010 | 22.01 | 7.28 | 7.89 | 142 | 17 | 260 | 18 | NA | 500 | 0.5 | 25.57 | 1400000
2020-12-13 | 24640 | 24.64 | 6.79 | 7.91 | 150 | 15 | 296 | 25 | NA | 700 | 0.5 | 26.15 | 1300000
2020-12-14 | 23920 | 23.92 | 7.27 | 7.88 | 146 | 13 | 263 | 22 | NA | 500 | 0.4 | 29.55 | 1300000
2020-12-15 | 25130 | 25.13 | 7.13 | 7.43 | 152 | 15 | 303 | 24 | NA | 600 | 0.5 | 31.69 | 1200000
2020-12-16 | 23900 | 23.9 | 7.25 | 7.45 | 150 | 12 | 260 | 27 | NA | 400 | 0.4 | 24.65 | 1400000
2020-12-17 | 23780 | 23.78 | 7.33 | 7.78 | 154 | 13 | 255 | 18 | NA | 600 | 0.5 | 30.22 | 1200000
2020-12-18 | 23210 | 23.21 | 7.3 | 7.73 | 144 | 15 | 270 | 25 | NA | 500 | 0.5 | 31.75 | 1300000
2020-12-19 | 23990 | 23.99 | 7.24 | 7.59 | 156 | 14 | 296 | 20 | NA | 400 | 0.5 | 32.11 | 1400000
2020-12-20 | 25120 | 25.12 | 7.26 | 7.69 | 138 | 13 | 302 | 23 | NA | 600 | 0.3 | 28.73 | 1700000
2020-12-21 | 22670 | 22.67 | 7.18 | 7.84 | 156 | 15 | 293 | 25 | NA | 500 | 0.4 | 27.43 | 1400000
2020-12-22 | 23350 | 23.35 | 7.13 | 7.54 | 144 | 14 | 287 | 19 | NA | 400 | 0.5 | 24 | 1200000
2020-12-23 | 23720 | 23.72 | 6.94 | 7.47 | 138 | 16 | 273 | 24 | NA | 600 | 0.5 | 26.58 | 1300000
2020-12-24 | 23760 | 23.76 | 7.16 | 7.69 | 125 | 13 | 268 | 25 | NA | 400 | 0.5 | 23.73 | 1400000
2020-12-25 | 25420 | 25.42 | 7.3 | 7.81 | 135 | 14 | 296 | 20 | NA | 600 | 0.3 | 25.99 | 1200000
2020-12-26 | 23950 | 23.95 | 7.28 | 7.64 | 142 | 12 | 304 | 25 | NA | 500 | 0.4 | 27 | 1400000
2020-12-27 | 26160 | 26.16 | 7.31 | 7.72 | 148 | 15 | 290 | 20 | NA | 400 | 0.5 | 25.37 | 1700000
2020-12-28 | 23120 | 23.12 | 7.26 | 7.73 | 152 | 13 | 284 | 23 | NA | 600 | 0.5 | 24.67 | 1300000
2020-12-29 | 23020 | 23.02 | 7.34 | 7.84 | 145 | 16 | 293 | 19 | NA | 500 | 0.3 | 22.38 | 1600000
2020-12-30 | 24890 | 24.89 | 7.23 | 7.78 | 140 | 17 | 286 | 26 | NA | 500 | 0.4 | 24.72 | 1300000
2020-12-31 | 23490 | 23.49 | 7.27 | 7.63 | 145 | 16 | 300 | 20 | NA | 700 | 0.6 | 25.64 | 1400000
Average | 24067.7419 | 24.0677 | 7.1877 | 7.6787 | 142.2903 | 14.6129 | 286.5484 | 23.3226 | NA | 530.6452 | 0.45806 | 26.8848 | 1345161.2903
Sum | 746100 | 746.1 | 222.82 | 238.04 | 4411 | 453 | 8883 | 723 | NA | 16450 | 14.2 | 833.43 | 41700000
Source: | Logbook of Labarotory at Sewage Treament Plant
Max |  | 26.16 | 7.34 | 7.91 | 156 | 17 | 314 | 28 | 0 | 700 | 0.6 | 34.82 | 1700000
Min |  | 22.01 | 6.79 | 7.43 | 122 | 12 | 255 | 18 | 0 | 400 | 0.3 | 21.3 | 1100000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2020-12-01 | 8103 | 8.103 | 7.23 | 7.62 | 138 | 16 | 276 | 24 | NA | 600 | 0.5 | 22.2 | 1600000
2020-12-02 | 7195 | 7.195 | 7.26 | 7.69 | 135 | 17 | 271 | 23 | NA | 700 | 0.5 | 23.5 | 1400000
2020-12-03 | 7676 | 7.676 | 7.3 | 7.58 | 140 | 16 | 263 | 22 | NA | 600 | 0.5 | 21.8 | 1600000
2020-12-04 | 7101 | 7.101 | 7.18 | 7.61 | 135 | 17 | 260 | 25 | NA | 500 | 0.5 | 22.7 | 1200000
2020-12-05 | 8610 | 8.61 | 7.26 | 7.54 | 142 | 16 | 268 | 24 | NA | 650 | 0.5 | 23.1 | 1300000
2020-12-06 | 7895 | 7.895 | 7.33 | 7.75 | 136 | 17 | 264 | 22 | NA | 500 | 0.5 | 21.8 | 1600000
2020-12-07 | 7664 | 7.664 | 7.22 | 7.75 | 138 | 15 | 258 | 23 | NA | 600 | 0.5 | 22.3 | 1300000
2020-12-08 | 7812 | 7.812 | 7.31 | 7.47 | 145 | 16 | 264 | 22 | NA | 500 | 0.5 | 23.5 | 1200000
2020-12-09 | 7773 | 7.773 | 7.37 | 7.58 | 150 | 15 | 257 | 24 | NA | 600 | 0.5 | 22.3 | 1100000
2020-12-10 | 7429 | 7.429 | 7.19 | 7.43 | 142 | 17 | 267 | 23 | NA | 500 | 0.5 | 21.6 | 1400000
2020-12-11 | 7494 | 7.494 | 7.24 | 7.53 | 140 | 16 | 261 | 24 | NA | 700 | 0.5 | 22.5 | 1600000
2020-12-12 | 8862 | 8.862 | 7.16 | 7.38 | 145 | 15 | 272 | 23 | NA | 600 | 0.5 | 23.1 | 1400000
2020-12-13 | 8191 | 8.191 | 7.34 | 7.67 | 132 | 16 | 260 | 22 | NA | 500 | 0.5 | 22.4 | 1300000
2020-12-14 | 7971 | 7.971 | 7.29 | 7.54 | 142 | 15 | 266 | 21 | NA | 700 | 0.5 | 23.9 | 1600000
2020-12-15 | 8295 | 8.295 | 7.21 | 7.65 | 135 | 17 | 254 | 22 | NA | 600 | 0.4 | 21.2 | 1200000
2020-12-16 | 9903 | 9.903 | 7.27 | 7.74 | 130 | 16 | 264 | 24 | NA | 500 | 0.5 | 22.6 | 1400000
2020-12-17 | 7972 | 7.972 | 7.16 | 7.46 | 132 | 15 | 271 | 25 | NA | 400 | 0.4 | 23.3 | 1300000
2020-12-18 | 7601 | 7.601 | 7.26 | 7.53 | 128 | 17 | 258 | 23 | NA | 600 | 0.5 | 21.5 | 1200000
2020-12-19 | 8006 | 8.006 | 7.31 | 7.63 | 135 | 16 | 265 | 21 | NA | 500 | 0.4 | 22.7 | 1400000
2020-12-20 | 8096 | 8.096 | 7.23 | 7.59 | 142 | 15 | 271 | 24 | NA | 600 | 0.5 | 23.3 | 1300000
2020-12-21 | 7163 | 7.163 | 7.36 | 7.62 | 138 | 16 | 252 | 25 | NA | 700 | 0.5 | 22.3 | 1600000
2020-12-22 | 7095 | 7.095 | 7.18 | 7.44 | 145 | 17 | 261 | 22 | NA | 500 | 0.4 | 23.6 | 1400000
2020-12-23 | 7924 | 7.924 | 7.27 | 7.56 | 150 | 16 | 274 | 23 | NA | 400 | 0.5 | 21.8 | 1100000
2020-12-24 | 7958 | 7.958 | 7.32 | 7.65 | 140 | 15 | 258 | 21 | NA | 600 | 0.5 | 22.5 | 1300000
2020-12-25 | 8271 | 8.271 | 7.18 | 7.49 | 146 | 14 | 261 | 17 | NA | 500 | 0.5 | 23.1 | 1200000
2020-12-26 | 8071 | 8.071 | 7.27 | 7.59 | 138 | 15 | 255 | 21 | NA | 400 | 0.5 | 24.2 | 1100000
2020-12-27 | 8182 | 8.182 | 7.21 | 7.46 | 145 | 16 | 266 | 23 | NA | 600 | 0.4 | 22.6 | 1400000
2020-12-28 | 7537 | 7.537 | 7.34 | 7.7 | 140 | 14 | 252 | 22 | NA | 500 | 0.5 | 21.4 | 1200000
2020-12-29 | 7469 | 7.469 | 7.25 | 7.48 | 135 | 15 | 263 | 24 | NA | 400 | 0.3 | 23.2 | 1400000
2020-12-30 | 7809 | 7.809 | 7.1 | 7.34 | 142 | 14 | 256 | 21 | NA | 600 | 0.2 | 22.3 | 1600000
2020-12-31 | 7795 | 7.795 | 7.22 | 7.53 | 135 | 15 | 268 | 23 | NA | 500 | 0.4 | 21.5 | 1200000
Average | 7900.7419 | 7.9007 | 7.2523 | 7.5677 | 139.2258 | 15.7097 | 263.0968 | 22.6774 | NA | 553.2258 | 0.46452 | 22.5742 | 1351612.9032
Sum | 244923 | 244.923 | 224.82 | 234.6 | 4316 | 487 | 8156 | 703 | NA | 17150 | 14.4 | 699.8 | 41900000
Source: | Logbook of Labarotory at Sewage Treament Plant
Max |  | 9.903 | 7.37 | 7.75 | 150 | 17 | 276 | 25 | 0 | 700 | 0.5 | 24.2 | 1600000
Min |  | 7.095 | 7.1 | 7.34 | 128 | 14 | 252 | 17 | 0 | 400 | 0.2 | 21.2 | 1100000