## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-02-01 | 50950 | 50.95 | 7.12 | 7.84 | 140 | 12 | 266 | 24 | NA | 600 | 0.6 | 24.9 | 1300000
2021-02-02 | 62200 | 62.2 | 7.14 | 7.89 | 130 | 14 | 238 | 26 | NA | 700 | 0.4 | 20.1 | 1300000
2021-02-03 | 58020 | 58.02 | 7.19 | 7.83 | 155 | 12 | 276 | 28 | NA | 600 | 0.6 | 22.1 | 1200000
2021-02-04 | 56270 | 56.27 | 7.17 | 7.84 | 150 | 14 | 240 | 26 | NA | 400 | 0.4 | 22.5 | 1700000
2021-02-05 | 61790 | 61.79 | 7.11 | 7.67 | 140 | 16 | 260 | 20 | NA | 700 | 0.6 | 21.73 | 1400000
2021-02-06 | 59990 | 59.99 | 7.21 | 7.79 | 155 | 11 | 296 | 24 | NA | 600 | 0.4 | 24.04 | 1200000
2021-02-07 | 59750 | 59.75 | 7.19 | 7.68 | 130 | 14 | 276 | 22 | NA | 700 | 0.6 | 22.5 | 1300000
2021-02-08 | 58950 | 58.95 | 7.09 | 7.64 | 145 | 16 | 254 | 26 | NA | 500 | 0.4 | 22.51 | 1700000
2021-02-09 | 60240 | 60.24 | 7.11 | 7.67 | 150 | 13 | 236 | 24 | NA | 700 | 0.6 | 25.7 | 1400000
2021-02-10 | 62330 | 62.33 | 7.16 | 7.84 | 140 | 16 | 240 | 26 | NA | 600 | 0.4 | 22.7 | 1200000
2021-02-11 | 59900 | 59.9 | 7.14 | 7.79 | 135 | 15 | 270 | 24 | NA | 700 | 0.6 | 21.5 | 1400000
2021-02-12 | 59130 | 59.13 | 7.24 | 7.89 | 145 | 17 | 260 | 22 | NA | 500 | 0.4 | 22.8 | 1700000
2021-02-13 | 58840 | 58.84 | 7.16 | 7.84 | 150 | 14 | 220 | 26 | NA | 700 | 0.6 | 24.4 | 1300000
2021-02-14 | 57340 | 57.34 | 7.36 | 7.77 | 145 | 16 | 278 | 24 | NA | 600 | 0.4 | 26.29 | 1200000
2021-02-15 | 57220 | 57.22 | 7.24 | 7.84 | 150 | 15 | 240 | 28 | NA | 500 | 0.4 | 24.04 | 1400000 | Plant availability is less as retaining wall at Ghagharnalla was broken for nearby nalla from 10:00 AM to 02:00 PM.
2021-02-16 | 59720 | 59.72 | 7.26 | 7.77 | 155 | 18 | 250 | 26 | NA | 500 | 0.4 | 21.38 | 1200000
2021-02-17 | 62450 | 62.45 | 7.28 | 7.59 | 150 | 16 | 254 | 28 | NA | 600 | 0.6 | 22.1 | 1300000
2021-02-18 | 63080 | 63.08 | 7.19 | 7.84 | 135 | 18 | 278 | 26 | NA | 500 | 0.4 | 22.46 | 1400000
2021-02-19 | 65940 | 65.94 | 7.21 | 7.89 | 150 | 16 | 290 | 28 | NA | 400 | 0.6 | 22.61 | 1700000
2021-02-20 | 63840 | 63.84 | 7.26 | 7.75 | 140 | 14 | 260 | 24 | NA | 600 | 0.4 | 25.43 | 1200000
2021-02-21 | 62130 | 62.13 | 7.2 | 7.81 | 130 | 18 | 270 | 26 | NA | 500 | 0.5 | 25.42 | 1300000
2021-02-22 | 59760 | 59.76 | 7.21 | 7.87 | 135 | 13 | 276 | 20 | NA | 400 | 0.4 | 22.7 | 1400000
2021-02-23 | 61920 | 61.92 | 7.19 | 7.64 | 150 | 16 | 298 | 22 | NA | 700 | 0.4 | 21.45 | 1700000
2021-02-24 | 62540 | 62.54 | 7.36 | 7.89 | 130 | 18 | 260 | 28 | NA | 600 | 0.5 | 25.4 | 1200000
2021-02-25 | 62940 | 62.94 | 7.2 | 7.72 | 155 | 14 | 196 | 26 | NA | 500 | 0.4 | 24.4 | 1300000
2021-02-26 | 61640 | 61.64 | 7.18 | 7.62 | 135 | 16 | 302 | 18 | NA | 400 | 0.4 | 24 | 1700000
2021-02-27 | 61800 | 61.8 | 7.31 | 7.64 | 130 | 17 | 242 | 28 | NA | 500 | 0.5 | 22.5 | 1400000
2021-02-28 | 61660 | 61.66 | 7.27 | 7.8 | 140 | 16 | 240 | 26 | NA | 600 | 0.4 | 21.73 | 1200000
Average | 60440.7143 | 60.4407 | 7.2054 | 7.7732 | 142.6786 | 15.1786 | 259.5 | 24.8571 | NA | 567.8571 | 0.475 | 23.1925 | 1382142.8571
1692.34
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 65940 | 65.94 | 7.36 | 7.89 | 155 | 18 | 302 | 28 |  | 700 | 0.6 | 26.29 | 1700000
Min | 50950 | 50.95 | 7.09 | 7.59 | 130 | 11 | 196 | 18 |  | 400 | 0.4 | 20.1 | 1200000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-02-01 | 37390 | 37.39 | 7.28 | 7.52 | 153 | 20 | 310 | 38 | NA | 500 | 0.5 | 25.9 | 1400000
2021-02-02 | 37850 | 37.85 | 7.35 | 7.58 | 155 | 22 | 314 | 40 | NA | 600 | 0.4 | 23.8 | 1300000
2021-02-03 | 37460 | 37.46 | 7.25 | 7.48 | 159 | 21 | 317 | 36 | NA | 700 | 0.3 | 24.5 | 1100000
2021-02-04 | 37490 | 37.49 | 7.39 | 7.6 | 153 | 23 | 322 | 37 | NA | 400 | 0.4 | 20.5 | 1700000
2021-02-05 | 39860 | 39.86 | 7.45 | 7.65 | 157 | 25 | 318 | 35 | NA | 500 | 0.5 | 23.1 | 1400000
2021-02-06 | 36470 | 36.47 | 7.51 | 7.67 | 160 | 22 | 310 | 39 | NA | 600 | 0.4 | 25.4 | 1300000
2021-02-07 | 37390 | 37.39 | 7.52 | 7.61 | 163 | 20 | 315 | 41 | NA | 700 | 0.3 | 26.9 | 1100000
2021-02-08 | 37560 | 37.56 | 7.48 | 7.58 | 159 | 18 | 311 | 36 | NA | 400 | 0.4 | 27.1 | 1400000
2021-02-09 | 37050 | 37.05 | 7.45 | 7.63 | 166 | 20 | 304 | 38 | NA | 500 | 0.5 | 25.3 | 1700000
2021-02-10 | 36580 | 36.58 | 7.52 | 7.65 | 163 | 22 | 299 | 40 | NA | 700 | 0.3 | 23.4 | 1300000
2021-02-11 | 36010 | 36.01 | 7.49 | 7.62 | 159 | 24 | 303 | 37 | NA | 600 | 0.4 | 22.4 | 1100000
2021-02-12 | 37510 | 37.51 | 7.47 | 7.58 | 156 | 25 | 308 | 39 | NA | 500 | 0.5 | 21.9 | 1400000
2021-02-13 | 37070 | 37.07 | 7.53 | 7.65 | 153 | 23 | 314 | 41 | NA | 700 | 0.3 | 22.8 | 1700000
2021-02-14 | 37650 | 37.65 | 7.55 | 7.67 | 157 | 21 | 322 | 35 | NA | 400 | 0.4 | 24.1 | 1300000
2021-02-15 | 37920 | 37.92 | 7.46 | 7.55 | 160 | 19 | 324 | 36 | NA | 500 | 0.5 | 22.7 | 1100000
2021-02-16 | 38530 | 38.53 | 7.38 | 7.58 | 153 | 22 | 327 | 38 | NA | 700 | 0.3 | 27.7 | 1400000
2021-02-17 | 37970 | 37.97 | 7.54 | 7.61 | 156 | 20 | 323 | 40 | NA | 600 | 0.4 | 24.9 | 1700000
2021-02-18 | 38270 | 38.27 | 7.45 | 7.52 | 159 | 23 | 318 | 42 | NA | 500 | 0.5 | 21.9 | 1300000
2021-02-19 | 37730 | 37.73 | 7.52 | 7.65 | 163 | 21 | 316 | 39 | NA | 400 | 0.4 | 25.9 | 1100000
2021-02-20 | 37460 | 37.46 | 7.54 | 7.68 | 166 | 24 | 312 | 41 | NA | 500 | 0.5 | 22.2 | 1300000
2021-02-21 | 37000 | 37 | 7.56 | 7.71 | 160 | 22 | 308 | 37 | NA | 700 | 0.3 | 23.3 | 1400000
2021-02-22 | 38470 | 38.47 | 7.52 | 7.65 | 156 | 20 | 312 | 36 | NA | 500 | 0.5 | 24.1 | 1700000
2021-02-23 | 38810 | 38.81 | 7.48 | 7.72 | 153 | 18 | 309 | 38 | NA | 600 | 0.4 | 27.6 | 1100000
2021-02-24 | 36330 | 36.33 | 7.55 | 7.67 | 157 | 21 | 305 | 40 | NA | 500 | 0.5 | 28.7 | 1400000
2021-02-25 | 39360 | 39.36 | 7.58 | 7.75 | 159 | 23 | 307 | 42 | NA | 400 | 0.3 | 25.1 | 1300000
2021-02-26 | 37430 | 37.43 | 7.45 | 7.68 | 156 | 25 | 301 | 39 | NA | 600 | 0.4 | 24.5 | 1400000
2021-02-27 | 35900 | 35.9 | 7.42 | 7.65 | 160 | 24 | 308 | 41 | NA | 700 | 0.3 | 23.2 | 1700000
2021-02-28 | 36910 | 36.91 | 7.51 | 7.71 | 156 | 22 | 314 | 38 | NA | 500 | 0.5 | 24.6 | 1100000
Average | 37551.0714 | 37.5511 | 7.4714 | 7.6293 | 158.1071 | 21.7857 | 312.5357 | 38.5357 | NA | 553.5714 | 0.40714 | 24.4107 | 1364285.7143
1051.43
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 39860 | 39.86 | 7.58 | 7.75 | 166 | 25 | 327 | 42 |  | 700 | 0.5 | 28.7 | 1700000
Min | 35900 | 35.9 | 7.25 | 7.48 | 153 | 18 | 299 | 35 |  | 400 | 0.3 | 20.5 | 1100000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-02-01 | 22680 | 22.68 | 7.24 | 7.84 | 142 | 15 | 270 | 23 | NA | 400 | 0.5 | 21.81 | 1400000
2021-02-02 | 24000 | 24 | 7.1 | 7.55 | 154 | 17 | 300 | 19 | NA | 500 | 0.4 | 29.74 | 1100000
2021-02-03 | 25600 | 25.6 | 7.18 | 7.67 | 138 | 13 | 256 | 21 | NA | 400 | 0.5 | 25.13 | 1300000
2021-02-04 | 25360 | 25.36 | 7.25 | 7.69 | 162 | 14 | 296 | 25 | NA | 500 | 0.3 | 26.22 | 1700000
2021-02-05 | 24760 | 24.76 | 7.35 | 7.61 | 140 | 13 | 270 | 20 | NA | 400 | 0.4 | 26.82 | 1400000
2021-02-06 | 25660 | 25.66 | 7.32 | 7.59 | 146 | 14 | 304 | 23 | NA | 500 | 0.3 | 24.11 | 1200000
2021-02-07 | 24960 | 24.96 | 7.28 | 7.54 | 152 | 16 | 316 | 25 | NA | 400 | 0.5 | 27.8 | 1700000
2021-02-08 | 24650 | 24.65 | 7.1 | 7.49 | 138 | 13 | 290 | 21 | NA | 700 | 0.3 | 26.56 | 1300000
2021-02-09 | 25160 | 25.16 | 7.14 | 7.7 | 140 | 14 | 283 | 24 | NA | 500 | 0.4 | 24.6 | 1400000
2021-02-10 | 26190 | 26.19 | 7.03 | 7.64 | 132 | 13 | 260 | 19 | NA | 600 | 0.3 | 26 | 1200000
2021-02-11 | 26720 | 26.72 | 7.15 | 7.6 | 152 | 15 | 266 | 24 | NA | 500 | 0.4 | 26.99 | 1700000
2021-02-12 | 27080 | 27.08 | 7.25 | 7.52 | 130 | 13 | 287 | 21 | NA | 400 | 0.4 | 27.45 | 1300000
2021-02-13 | 26160 | 26.16 | 7.11 | 7.72 | 132 | 15 | 260 | 20 | NA | 600 | 0.3 | 25.9 | 1400000
2021-02-14 | 26140 | 26.14 | 7.27 | 7.64 | 142 | 14 | 285 | 24 | NA | 500 | 0.4 | 24.29 | 1700000
2021-02-15 | 25520 | 25.52 | 7.18 | 7.54 | 144 | 15 | 260 | 18 | NA | 400 | 0.3 | 26.63 | 1400000
2021-02-16 | 24930 | 24.93 | 7.11 | 7.6 | 140 | 13 | 264 | 20 | NA | 500 | 0.4 | 23.74 | 1700000
2021-02-17 | 24900 | 24.9 | 7.15 | 7.49 | 132 | 14 | 278 | 19 | NA | 400 | 0.3 | 25.36 | 1300000
2021-02-18 | 25220 | 25.22 | 7.07 | 7.74 | 136 | 16 | 292 | 22 | NA | 600 | 0.4 | 25.28 | 1400000
2021-02-19 | 23670 | 23.67 | 7.21 | 7.42 | 130 | 15 | 262 | 21 | NA | 500 | 0.3 | 24.3 | 1600000
2021-02-20 | 24260 | 24.26 | 7.1 | 7.6 | 135 | 13 | 274 | 18 | NA | 400 | 0.4 | 24.32 | 1300000
2021-02-21 | 27590 | 27.59 | 7.06 | 7.45 | 154 | 14 | 265 | 19 | NA | 600 | 0.5 | 25.92 | 1700000
2021-02-22 | 25220 | 25.22 | 7.18 | 7.69 | 142 | 16 | 290 | 22 | NA | 500 | 0.4 | 24.53 | 1400000
2021-02-23 | 25040 | 25.04 | 7.23 | 7.81 | 136 | 14 | 285 | 18 | NA | 600 | 0.3 | 25.26 | 1200000
2021-02-24 | 24940 | 24.94 | 7.23 | 7.61 | 132 | 15 | 294 | 24 | NA | 500 | 0.2 | 23.79 | 1400000
2021-02-25 | 23910 | 23.91 | 7.15 | 7.87 | 138 | 13 | 263 | 21 | NA | 600 | 0.3 | 23.98 | 1700000
2021-02-26 | 25720 | 25.72 | 7.24 | 7.8 | 130 | 14 | 286 | 20 | NA | 500 | 0.4 | 25.03 | 1300000
2021-02-27 | 23700 | 23.7 | 7.15 | 7.63 | 142 | 15 | 276 | 18 | NA | 400 | 0.3 | 26.78 | 1700000
2021-02-28 | 24820 | 24.82 | 7.23 | 7.8 | 156 | 15 | 287 | 23 | NA | 500 | 0.3 | 27.15 | 1200000
Average | 25162.8571 | 25.1629 | 7.1807 | 7.6375 | 140.9643 | 14.3214 | 279.25 | 21.1429 | NA | 496.4286 | 0.36429 | 25.5532 | 1432142.8571
704.56
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 27590 | 27.59 | 7.35 | 7.87 | 162 | 17 | 316 | 25 |  | 700 | 0.5 | 29.74 | 1700000
Min | 22680 | 22.68 | 7.03 | 7.42 | 130 | 13 | 256 | 18 |  | 400 | 0.2 | 21.81 | 1100000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-02-01 | 7423 | 7.423 | 7.19 | 7.33 | 148 | 15 | 255 | 18 | NA | 400 | 0.3 | 21.34 | 1200000
2021-02-02 | 7725 | 7.725 | 7.13 | 7.27 | 142 | 14 | 265 | 21 | NA | 500 | 0.4 | 22.19 | 1400000
2021-02-03 | 7821 | 7.821 | 7.24 | 7.39 | 140 | 15 | 259 | 19 | NA | 600 | 0.2 | 20.28 | 1300000
2021-02-04 | 7520 | 7.52 | 7.16 | 7.32 | 135 | 16 | 262 | 22 | NA | 400 | 0.3 | 23.61 | 1600000
2021-02-05 | 7765 | 7.765 | 7.24 | 7.59 | 142 | 15 | 271 | 24 | NA | 500 | 0.4 | 22.29 | 1400000
2021-02-06 | 8322 | 8.322 | 7.13 | 7.48 | 145 | 15 | 277 | 22 | NA | 450 | 0.3 | 20.39 | 1300000
2021-02-07 | 8191 | 8.191 | 7.26 | 7.53 | 150 | 14 | 264 | 18 | NA | 400 | 0.2 | 22.28 | 1200000
2021-02-08 | 7777 | 7.777 | 7.32 | 7.64 | 140 | 15 | 256 | 20 | NA | 500 | 0.4 | 21.69 | 1400000
2021-02-09 | 7522 | 7.522 | 7.21 | 7.57 | 135 | 14 | 249 | 22 | NA | 500 | 0.3 | 22.34 | 1600000
2021-02-10 | 8208 | 8.208 | 7.11 | 7.46 | 142 | 16 | 261 | 20 | NA | 400 | 0.4 | 21.47 | 1400000
2021-02-11 | 8571 | 8.571 | 7.13 | 7.41 | 136 | 15 | 273 | 23 | NA | 500 | 0.5 | 20.19 | 1200000
2021-02-12 | 9688 | 9.688 | 7.29 | 7.55 | 140 | 16 | 279 | 21 | NA | 400 | 0.3 | 21.83 | 1400000
2021-02-13 | 8290 | 8.29 | 7.14 | 7.43 | 135 | 15 | 261 | 23 | NA | 500 | 0.4 | 23.12 | 1300000
2021-02-14 | 8717 | 8.717 | 7.22 | 7.62 | 142 | 14 | 257 | 21 | NA | 400 | 0.3 | 21.52 | 1100000
2021-02-15 | 8036 | 8.036 | 7.27 | 7.36 | 150 | 15 | 265 | 19 | NA | 500 | 0.2 | 20.39 | 1400000
2021-02-16 | 7445 | 7.445 | 7.13 | 7.26 | 130 | 16 | 251 | 22 | NA | 400 | 0.4 | 22.45 | 1200000
2021-02-17 | 7695 | 7.695 | 7.32 | 7.49 | 135 | 14 | 267 | 20 | NA | 600 | 0.2 | 21.62 | 1700000
2021-02-18 | 7818 | 7.818 | 7.24 | 7.37 | 140 | 15 | 256 | 23 | NA | 500 | 0.3 | 23.31 | 1600000
2021-02-19 | 8092 | 8.092 | 7.14 | 7.31 | 145 | 13 | 271 | 18 | NA | 400 | 0.3 | 23.21 | 1400000
2021-02-20 | 9021 | 9.021 | 7.19 | 7.52 | 135 | 13 | 269 | 23 | NA | 450 | 0.2 | 22.16 | 1700000
2021-02-21 | 7969 | 7.969 | 7.24 | 7.62 | 140 | 15 | 258 | 20 | NA | 600 | 0.4 | 21.76 | 1300000
2021-02-22 | 7393 | 7.393 | 7.17 | 7.39 | 145 | 16 | 265 | 22 | NA | 500 | 0.2 | 22.36 | 1400000
2021-02-23 | 7489 | 7.489 | 7.29 | 7.46 | 135 | 14 | 252 | 19 | NA | 400 | 0.3 | 21.46 | 1600000
2021-02-24 | 7560 | 7.56 | 7.22 | 7.36 | 142 | 16 | 260 | 23 | NA | 500 | 0.2 | 23.12 | 1400000
2021-02-25 | 7333 | 7.333 | 7.13 | 7.26 | 132 | 13 | 241 | 18 | NA | 450 | 0.4 | 20.81 | 1300000
2021-02-26 | 7753 | 7.753 | 7.23 | 7.44 | 137 | 15 | 259 | 22 | NA | 500 | 0.3 | 21.31 | 1400000
2021-02-27 | 7422 | 7.422 | 7.17 | 7.36 | 130 | 14 | 247 | 24 | NA | 400 | 0.2 | 22.61 | 1200000
2021-02-28 | 7653 | 7.653 | 7.11 | 7.52 | 135 | 15 | 256 | 20 | NA | 500 | 0.4 | 20.67 | 1300000
Average | 7936.3929 | 7.9364 | 7.2007 | 7.4396 | 139.3929 | 14.75 | 260.9286 | 20.9643 | NA | 469.6429 | 0.31071 | 21.8493 | 1382142.8571
222.219
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 9688 | 9.688 | 7.32 | 7.64 | 150 | 16 | 279 | 24 |  | 600 | 0.5 | 23.61 | 1700000
Min | 7333 | 7.333 | 7.11 | 7.26 | 130 | 13 | 241 | 18 |  | 400 | 0.2 | 20.19 | 1100000