## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-01-01 | 58960 | 58.96 | 7.17 | 7.94 | 130 | 18 | 300 | 24 | NA | 700 | 0.6 | 21.43 | 1700000 | Aeration tank no. 2 is under maintenance due to problem in diffusers.
2021-01-02 | 57130 | 57.13 | 7.19 | 7.74 | 145 | 15 | 284 | 22 | NA | 400 | 0.5 | 22.7 | 1200000 | Aeration tank no. 2 is under maintenance due to problem in diffusers.
2021-01-03 | 47740 | 47.74 | 7.24 | 7.57 | 140 | 12 | 276 | 28 | NA | 500 | 0.4 | 25.4 | 1400000 | Maintenace for Aeration tank no. 2 is completed & it is taken into operation.
2021-01-04 | 55830 | 55.83 | 7.2 | 7.67 | 130 | 14 | 296 | 26 | NA | 700 | 0.5 | 24.4 | 1300000
2021-01-05 | 54560 | 54.56 | 7.14 | 7.64 | 150 | 18 | 260 | 22 | NA | 600 | 0.4 | 21.5 | 1400000
2021-01-06 | 60400 | 60.4 | 7.31 | 7.97 | 135 | 14 | 266 | 24 | NA | 400 | 0.5 | 22.7 | 1200000
2021-01-07 | 57010 | 57.01 | 7.14 | 7.69 | 130 | 12 | 240 | 22 | NA | 700 | 0.6 | 21.1 | 1400000
2021-01-08 | 53600 | 53.6 | 7.17 | 7.74 | 140 | 14 | 290 | 18 | NA | 600 | 0.4 | 21.5 | 1700000
2021-01-09 | 54940 | 54.94 | 7.16 | 7.59 | 130 | 14 | 240 | 28 | NA | 500 | 0.5 | 22.5 | 1400000
2021-01-10 | 55740 | 55.74 | 7.19 | 7.77 | 135 | 12 | 276 | 22 | NA | 700 | 0.4 | 24.04 | 1400000
2021-01-11 | 51400 | 51.4 | 7.24 | 7.62 | 150 | 14 | 238 | 24 | NA | 600 | 0.5 | 20.1 | 1200000
2021-01-12 | 54360 | 54.36 | 7.19 | 7.54 | 140 | 12 | 240 | 22 | NA | 700 | 0.6 | 22.1 | 1700000
2021-01-13 | 55480 | 55.48 | 7.22 | 7.64 | 155 | 14 | 256 | 26 | NA | 600 | 0.4 | 21.96 | 1200000
2021-01-14 | 47300 | 47.3 | 7.27 | 7.79 | 145 | 15 | 260 | 22 | NA | 500 | 0.6 | 21.43 | 1400000
2021-01-15 | 52620 | 52.62 | 7.21 | 7.97 | 140 | 14 | 208 | 26 | NA | 700 | 0.4 | 23.5 | 1400000
2021-01-16 | 51660 | 51.66 | 7.14 | 7.69 | 135 | 17 | 276 | 20 | NA | 600 | 0.6 | 21.5 | 1200000
2021-01-17 | 59878 | 59.878 | 7.24 | 7.72 | 145 | 15 | 220 | 26 | NA | 500 | 0.4 | 24.4 | 1400000
2021-01-18 | 51695 | 51.695 | 7.27 | 7.84 | 130 | 13 | 268 | 22 | NA | 600 | 0.5 | 21.18 | 1200000
2021-01-19 | 55250 | 55.25 | 7.24 | 7.86 | 155 | 14 | 260 | 24 | NA | 700 | 0.4 | 21.4 | 1600000
2021-01-20 | 50820 | 50.82 | 7.26 | 7.94 | 130 | 12 | 240 | 22 | NA | 800 | 0.6 | 22.7 | 1400000
2021-01-21 | 47350 | 47.35 | 7.34 | 7.41 | 150 | 13 | 270 | 24 | NA | 600 | 0.4 | 23.7 | 1700000
2021-01-22 | 43820 | 43.82 | 7.38 | 7.4 | 135 | 15 | 260 | 22 | NA | 500 | 0.5 | 21.7 | 1400000
2021-01-23 | 46950 | 46.95 | 7.17 | 7.89 | 140 | 13 | 256 | 26 | NA | 700 | 0.4 | 22.7 | 1300000
2021-01-24 | 62970 | 62.97 | 7.19 | 7.94 | 130 | 17 | 220 | 24 | NA | 600 | 0.6 | 24.9 | 1200000
2021-01-25 | 62040 | 62.04 | 7.24 | 7.68 | 145 | 16 | 276 | 28 | NA | 500 | 0.5 | 22.1 | 1400000
2021-01-26 | 60730 | 60.73 | 7.18 | 7.6 | 140 | 15 | 220 | 22 | NA | 700 | 0.4 | 20.1 | 1300000
2021-01-27 | 60300 | 60.3 | 7.29 | 7.67 | 135 | 13 | 208 | 26 | NA | 800 | 0.6 | 21.43 | 1400000
2021-01-28 | 61440 | 61.44 | 7.24 | 7.78 | 130 | 15 | 256 | 20 | NA | 600 | 0.4 | 25.05 | 1200000
2021-01-29 | 61070 | 61.07 | 7.21 | 7.6 | 140 | 13 | 248 | 23 | NA | 500 | 0.4 | 24.3 | 1300000
2021-01-30 | 60680 | 60.68 | 7.3 | 7.59 | 135 | 15 | 263 | 25 | NA | 700 | 0.3 | 23.4 | 1400000
2021-01-31 | 61100 | 61.1 | 7.16 | 7.34 | 145 | 14 | 273 | 22 | NA | 500 | 0.2 | 21.62 | 1400000
Average | 55316.871 | 55.3169 | 7.2223 | 7.7042 | 139.1935 | 14.2581 | 256.2581 | 23.6129 | NA | 606.4516 | 0.46774 | 22.5335 | 1380645.1613
Sum | 1714823 | 1714.823 | 223.89 | 238.83 | 4315 | 442 | 7944 | 732 | NA | 18800 | 14.5 | 698.54 | 42800000
Source: | Logbook of Laboratory at Sewage Treament Plant
Max |  | 62.97 | 7.38 | 7.97 | 155 | 18 | 300 | 28 | 0 | 800 | 0.6 | 25.4 | 1700000
Min |  | 43.82 | 7.14 | 7.34 | 130 | 12 | 208 | 18 | 0 | 400 | 0.2 | 20.1 | 1200000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-01-01 | 36570 | 36.57 | 7.37 | 7.46 | 160 | 19 | 320 | 20 | NA | 500 | 0.5 | 22.6 | 1400000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate.
2021-01-02 | 36140 | 36.14 | 7.31 | 7.43 | 153 | 22 | 316 | 18 | NA | 600 | 0.4 | 24.1 | 1300000
2021-01-03 | 36220 | 36.22 | 7.28 | 7.45 | 156 | 20 | 305 | 21 | NA | 700 | 0.3 | 27.5 | 1100000
2021-01-04 | 34710 | 34.71 | 7.22 | 7.41 | 153 | 24 | 312 | 19 | NA | 500 | 0.4 | 22.4 | 1400000
2021-01-05 | 32300 | 32.3 | 7.28 | 7.38 | 159 | 22 | 299 | 22 | NA | 600 | 0.3 | 20.2 | 1100000
2021-01-06 | 34290 | 34.29 | 7.21 | 7.39 | 157 | 25 | 305 | 24 | NA | 700 | 0.5 | 24.3 | 1700000
2021-01-07 | 32200 | 32.2 | 7.19 | 7.51 | 150 | 23 | 313 | 20 | NA | 400 | 0.3 | 27.2 | 1400000
2021-01-08 | 34980 | 34.98 | 7.25 | 7.42 | 153 | 24 | 316 | 18 | NA | 600 | 0.4 | 21.8 | 1300000
2021-01-09 | 32670 | 32.67 | 7.31 | 7.55 | 160 | 22 | 308 | 20 | NA | 500 | 0.5 | 23.2 | 1400000
2021-01-10 | 36130 | 36.13 | 7.27 | 7.52 | 156 | 23 | 302 | 24 | NA | 600 | 0.4 | 20.5 | 1700000
2021-01-11 | 33320 | 33.32 | 7.19 | 7.38 | 159 | 25 | 312 | 26 | NA | 700 | 0.3 | 22.7 | 1300000
2021-01-12 | 33200 | 33.2 | 7.24 | 7.41 | 157 | 26 | 318 | 25 | NA | 500 | 0.5 | 21.2 | 1100000
2021-01-13 | 34660 | 34.66 | 7.21 | 7.48 | 153 | 24 | 322 | 27 | NA | 600 | 0.4 | 23.4 | 1400000
2021-01-14 | 33640 | 33.64 | 7.22 | 7.51 | 150 | 22 | 314 | 26 | NA | 500 | 0.5 | 25.5 | 1700000
2021-01-15 | 32160 | 32.16 | 7.18 | 7.35 | 153 | 25 | 306 | 28 | NA | 700 | 0.3 | 24.2 | 1300000
2021-01-16 | 34040 | 34.04 | 7.25 | 7.39 | 156 | 23 | 302 | 25 | NA | 600 | 0.4 | 23.4 | 1400000
2021-01-17 | 32930 | 32.93 | 7.17 | 7.25 | 150 | 24 | 299 | 27 | NA | 400 | 0.5 | 21.2 | 1100000
2021-01-18 | 33560 | 33.56 | 7.28 | 7.33 | 157 | 22 | 306 | 24 | NA | 700 | 0.3 | 25.2 | 1700000
2021-01-19 | 36160 | 36.16 | 7.31 | 7.38 | 153 | 24 | 310 | 28 | NA | 400 | 0.4 | 24.3 | 1300000
2021-01-20 | 39540 | 39.54 | 7.25 | 7.41 | 156 | 26 | 314 | 32 | NA | 500 | 0.5 | 25.4 | 1100000
2021-01-21 | 39060 | 39.06 | 7.26 | 7.45 | 159 | 23 | 316 | 34 | NA | 600 | 0.4 | 26.1 | 1700000
2021-01-22 | 38100 | 38.1 | 7.19 | 7.37 | 163 | 24 | 318 | 36 | NA | 700 | 0.3 | 22.8 | 1300000
2021-01-23 | 37360 | 37.36 | 7.24 | 7.39 | 160 | 26 | 322 | 33 | NA | 500 | 0.5 | 25.1 | 1400000
2021-01-24 | 36930 | 36.93 | 7.28 | 7.34 | 166 | 25 | 317 | 35 | NA | 400 | 0.4 | 23.4 | 1100000
2021-01-25 | 36650 | 36.65 | 7.32 | 7.47 | 156 | 23 | 310 | 37 | NA | 700 | 0.3 | 27.6 | 1300000
2021-01-26 | 37110 | 37.11 | 7.38 | 7.52 | 159 | 24 | 304 | 34 | NA | 600 | 0.4 | 22.16 | 1400000
2021-01-27 | 36910 | 36.91 | 7.35 | 7.58 | 153 | 22 | 299 | 36 | NA | 500 | 0.5 | 23.6 | 1700000
2021-01-28 | 37040 | 37.04 | 7.32 | 7.61 | 157 | 20 | 305 | 38 | NA | 400 | 0.4 | 25.3 | 1100000 | 1) Sludge dewatering system is started on 27.01.2021.
2021-01-29 | 37900 | 37.9 | 7.29 | 7.57 | 160 | 22 | 308 | 35 | NA | 700 | 0.3 | 24.4 | 1300000
2021-01-30 | 38060 | 38.06 | 7.25 | 7.55 | 163 | 25 | 312 | 37 | NA | 500 | 0.5 | 27.2 | 1400000
2021-01-31 | 39040 | 39.04 | 7.31 | 7.58 | 156 | 23 | 318 | 34 | NA | 600 | 0.4 | 23.1 | 1300000
Average | 35599.3548 | 35.5994 | 7.2639 | 7.4465 | 156.5484 | 23.2903 | 310.5806 | 27.8387 | NA | 564.5161 | 0.40323 | 23.9052 | 1361290.3226
Sum | 1103580 | 1103.58 | 225.18 | 230.84 | 4853 | 722 | 9628 | 863 | NA | 17500 | 12.5 | 741.06 | 42200000
Source: | Logbook of Laboratory at Sewage Treament Plant
Max |  | 39.54 | 7.38 | 7.61 | 166 | 26 | 322 | 38 | 0 | 700 | 0.5 | 27.6 | 1700000
Min |  | 32.16 | 7.17 | 7.25 | 150 | 19 | 299 | 18 | 0 | 400 | 0.3 | 20.2 | 1100000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-01-01 | 25060 | 25.06 | 7.23 | 7.53 | 140 | 17 | 263 | 25 | NA | 500 | 0.5 | 23.76 | 1100000 | Plant availability is 100%
2021-01-02 | 24110 | 24.11 | 7.13 | 7.63 | 135 | 15 | 279 | 27 | NA | 700 | 0.3 | 26.05 | 1400000 | Plant availability is 100%
2021-01-03 | 24420 | 24.42 | 7.25 | 7.8 | 142 | 16 | 269 | 19 | NA | 600 | 0.5 | 26.98 | 1200000 | Plant availability is 100%
2021-01-04 | 24800 | 24.8 | 7.17 | 7.64 | 134 | 17 | 273 | 22 | NA | 700 | 0.4 | 24.36 | 1600000 | Plant availability is 100%
2021-01-05 | 24940 | 24.94 | 7.29 | 7.57 | 130 | 14 | 258 | 24 | NA | 500 | 0.3 | 23.05 | 1400000 | Plant availability is 100%
2021-01-06 | 25930 | 25.93 | 7.33 | 7.69 | 138 | 13 | 276 | 25 | NA | 400 | 0.5 | 25.6 | 1300000 | Plant availability is 100%
2021-01-07 | 25010 | 25.01 | 7.23 | 7.59 | 145 | 16 | 293 | 20 | NA | 500 | 0.4 | 23.22 | 1200000 | Plant availability is 100%
2021-01-08 | 24550 | 24.55 | 7.11 | 7.49 | 136 | 14 | 315 | 25 | NA | 400 | 0.5 | 22.23 | 1400000 | Plant availability is 100%
2021-01-09 | 23500 | 23.5 | 7.28 | 7.82 | 146 | 15 | 300 | 27 | NA | 500 | 0.5 | 24.05 | 1300000 | Plant availability is 100%
2021-01-10 | 26300 | 26.3 | 7.35 | 7.79 | 142 | 16 | 288 | 24 | NA | 400 | 0.5 | 23.31 | 1300000 | Plant availability is 100%
2021-01-11 | 24090 | 24.09 | 7.28 | 7.82 | 136 | 15 | 310 | 20 | NA | 600 | 0.3 | 23.13 | 1700000 | Plant availability is 100%
2021-01-12 | 23380 | 23.38 | 7.14 | 7.78 | 150 | 16 | 284 | 23 | NA | 350 | 0.6 | 27.05 | 1400000 | Plant availability is 100%
2021-01-13 | 23880 | 23.88 | 7.23 | 7.91 | 146 | 13 | 306 | 19 | NA | 500 | 0.5 | 25.52 | 1700000 | Plant availability is 100%
2021-01-14 | 23420 | 23.42 | 7.24 | 7.73 | 140 | 15 | 278 | 21 | NA | 400 | 0.5 | 24.65 | 1400000 | Plant availability is 100%
2021-01-15 | 22510 | 22.51 | 7.3 | 7.72 | 150 | 16 | 296 | 20 | NA | 600 | 0.4 | 23.48 | 1300000 | Plant availability is 100%
2021-01-16 | 22200 | 22.2 | 7.25 | 7.64 | 145 | 14 | 290 | 24 | NA | 500 | 0.4 | 27.78 | 1700000 | Plant availability is 100%
2021-01-17 | 24250 | 24.25 | 7.18 | 7.48 | 136 | 17 | 278 | 18 | NA | 600 | 0.3 | 26.4 | 1300000 | Plant availability is 100%
2021-01-18 | 25380 | 25.38 | 7.23 | 7.8 | 140 | 14 | 283 | 23 | NA | 300 | 0.6 | 24.86 | 1100000 | Plant availability is 100%
2021-01-19 | 23920 | 23.92 | 7.28 | 7.78 | 148 | 12 | 256 | 20 | NA | 400 | 0.4 | 23.4 | 1400000 | Plant availability is 100%
2021-01-20 | 25330 | 25.33 | 7.21 | 7.69 | 136 | 15 | 286 | 25 | NA | 500 | 0.5 | 23.15 | 1700000 | Plant availability is 100%
2021-01-21 | 23070 | 23.07 | 7.34 | 7.54 | 132 | 13 | 295 | 26 | NA | 500 | 0.4 | 26.54 | 1300000 | Plant availability is 100%
2021-01-22 | 23010 | 23.01 | 7.12 | 7.49 | 140 | 15 | 286 | 22 | NA | 600 | 0.3 | 24.25 | 1600000 | Plant availability is 100%
2021-01-23 | 25330 | 25.33 | 7.18 | 7.64 | 145 | 16 | 303 | 18 | NA | 500 | 0.5 | 25.64 | 1400000 | Plant availability is 100%
2021-01-24 | 26590 | 26.59 | 7.23 | 7.64 | 134 | 14 | 270 | 21 | NA | 400 | 0.4 | 22.2 | 1300000 | Plant availability is 100%
2021-01-25 | 23070 | 23.07 | 7.12 | 7.8 | 148 | 17 | 298 | 25 | NA | 400 | 0.5 | 25.22 | 1200000 | Plant availability is 100%
2021-01-26 | 24780 | 24.78 | 7.3 | 7.69 | 138 | 13 | 260 | 22 | NA | 600 | 0.5 | 25.14 | 1400000 | Plant availability is 100%
2021-01-27 | 24160 | 24.16 | 7.12 | 7.7 | 130 | 15 | 288 | 24 | NA | 500 | 0.3 | 23.3 | 1100000 | Plant availability is 100%
2021-01-28 | 22770 | 22.77 | 7.2 | 7.72 | 134 | 12 | 263 | 20 | NA | 400 | 0.4 | 26.07 | 1400000 | Plant availability is 100%
2021-01-29 | 23530 | 23.53 | 7.13 | 7.65 | 150 | 14 | 291 | 23 | NA | 600 | 0.3 | 22.54 | 1700000 | Plant availability is 100%
2021-01-30 | 23970 | 23.97 | 7.24 | 7.69 | 154 | 16 | 310 | 26 | NA | 400 | 0.4 | 25.1 | 1300000 | Plant availability is 100%
2021-01-31 | 26330 | 26.33 | 7.3 | 7.72 | 135 | 13 | 290 | 20 | NA | 600 | 0.5 | 23.23 | 1700000 | Plant availability is 100%
Average | 24309.3548 | 24.3094 | 7.2255 | 7.6832 | 140.4839 | 14.7742 | 285 | 22.5161 | NA | 498.3871 | 0.43226 | 24.5568 | 1396774.1935
Sum | 753590 | 753.59 | 223.99 | 238.18 | 4355 | 458 | 8835 | 698 | NA | 15450 | 13.4 | 761.26 | 43300000
Source: | Logbook of Laboratory at Sewage Treament Plant
Max |  | 26.59 | 7.35 | 7.91 | 154 | 17 | 315 | 27 | 0 | 700 | 0.6 | 27.78 | 1700000
Min |  | 22.2 | 7.11 | 7.48 | 130 | 12 | 256 | 18 | 0 | 300 | 0.3 | 22.2 | 1100000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-01-01 | 8091 | 8.091 | 7.37 | 7.62 | 130 | 14 | 271 | 25 | NA | 400 | 0.5 | 22.7 | 1400000 | Plant availability is 100%
2021-01-02 | 7415 | 7.415 | 7.25 | 7.59 | 135 | 13 | 264 | 22 | NA | 500 | 0.4 | 21.4 | 1200000 | Plant availability is 100%
2021-01-03 | 7721 | 7.721 | 7.17 | 7.46 | 142 | 14 | 254 | 20 | NA | 400 | 0.2 | 22.5 | 1100000 | Plant availability is 100%
2021-01-04 | 7766 | 7.766 | 7.22 | 7.68 | 150 | 13 | 269 | 18 | NA | 500 | 0.4 | 21.2 | 1400000 | Plant availability is 100%
2021-01-05 | 7254 | 7.254 | 7.11 | 7.48 | 140 | 14 | 251 | 20 | NA | 400 | 0.5 | 22.6 | 1200000 | Plant availability is 100%
2021-01-06 | 7396 | 7.396 | 7.23 | 7.57 | 145 | 13 | 263 | 19 | NA | 600 | 0.5 | 23.5 | 1400000 | Plant availability is 100%
2021-01-07 | 7993 | 7.993 | 7.29 | 7.51 | 138 | 14 | 275 | 22 | NA | 500 | 0.3 | 21.3 | 1200000 | Plant availability is 100%
2021-01-08 | 8320 | 8.32 | 7.36 | 7.72 | 135 | 13 | 258 | 20 | NA | 400 | 0.5 | 22.24 | 1100000 | Plant availability is 100%
2021-01-09 | 8459 | 8.459 | 7.19 | 7.58 | 148 | 14 | 267 | 18 | NA | 500 | 0.2 | 21.71 | 1300000 | Plant availability is 100%
2021-01-10 | 8661 | 8.661 | 7.28 | 7.63 | 140 | 15 | 251 | 20 | NA | 400 | 0.3 | 22.19 | 1100000 | Plant availability is 100%
2021-01-11 | 8251 | 8.251 | 7.16 | 7.5 | 145 | 14 | 262 | 17 | NA | 450 | 0.2 | 21.23 | 1300000 | Plant availability is 100%
2021-01-12 | 7397 | 7.397 | 7.24 | 7.41 | 150 | 13 | 269 | 19 | NA | 500 | 0.3 | 21.61 | 1600000 | Plant availability is 100%
2021-01-13 | 7778 | 7.778 | 7.38 | 7.62 | 155 | 14 | 276 | 20 | NA | 400 | 0.2 | 22.32 | 1400000 | Plant availability is 100%
2021-01-14 | 8023 | 8.023 | 7.13 | 7.37 | 145 | 15 | 279 | 17 | NA | 500 | 0.2 | 20.19 | 1600000 | Plant availability is 100%
2021-01-15 | 7378 | 7.378 | 7.23 | 7.49 | 135 | 13 | 266 | 19 | NA | 400 | 0.3 | 21.29 | 1700000 | Plant availability is 100%
2021-01-16 | 8709 | 8.709 | 7.38 | 7.59 | 140 | 14 | 271 | 17 | NA | 450 | 0.2 | 20.09 | 1200000 | Plant availability is 100%
2021-01-17 | 10603 | 10.603 | 7.18 | 7.64 | 132 | 13 | 280 | 20 | NA | 600 | 0.3 | 22.11 | 1400000 | Plant availability is 100%
2021-01-18 | 9467 | 9.467 | 7.29 | 7.42 | 142 | 14 | 263 | 18 | NA | 500 | 0.2 | 21.65 | 1300000 | Plant availability is 100%
2021-01-19 | 9546 | 9.546 | 7.17 | 7.34 | 145 | 13 | 270 | 21 | NA | 400 | 0.3 | 20.26 | 1100000 | Plant availability is 100%
2021-01-20 | 7984 | 7.984 | 7.24 | 7.74 | 140 | 14 | 276 | 19 | NA | 450 | 0.2 | 22.49 | 1300000 | Plant availability is 100%
2021-01-21 | 7657 | 7.657 | 7.33 | 7.69 | 135 | 13 | 267 | 17 | NA | 500 | 0.3 | 21.45 | 1600000 | Plant availability is 100%
2021-01-22 | 7428 | 7.428 | 7.18 | 7.45 | 130 | 15 | 258 | 19 | NA | 400 | 0.2 | 22.61 | 1400000 | Plant availability is 100%
2021-01-23 | 8669 | 8.669 | 7.37 | 7.71 | 140 | 14 | 278 | 21 | NA | 500 | 0.3 | 20.39 | 1200000 | Plant availability is 100%
2021-01-24 | 8039 | 8.039 | 7.19 | 7.32 | 145 | 13 | 262 | 18 | NA | 400 | 0.2 | 21.55 | 1300000 | Plant availability is 100%
2021-01-25 | 8516 | 8.516 | 7.29 | 7.44 | 140 | 15 | 273 | 20 | NA | 500 | 0.3 | 20.29 | 1400000 | Plant availability is 100%
2021-01-26 | 7993 | 7.993 | 7.11 | 7.39 | 135 | 14 | 258 | 17 | NA | 450 | 0.2 | 22.16 | 1200000 | Plant availability is 100%
2021-01-27 | 7716 | 7.716 | 7.22 | 7.33 | 130 | 13 | 269 | 21 | NA | 500 | 0.3 | 21.39 | 1300000 | Plant availability is 100%
2021-01-28 | 6380 | 6.38 | 7.15 | 7.28 | 136 | 15 | 247 | 20 | NA | 400 | 0.2 | 20.64 | 1100000 | Plant availability is 100%
2021-01-29 | 7812 | 7.812 | 7.2 | 7.23 | 145 | 14 | 256 | 18 | NA | 500 | 0.3 | 22.11 | 1200000 | Plant availability is 100%
2021-01-30 | 7503 | 7.503 | 7.13 | 7.27 | 138 | 15 | 265 | 22 | NA | 400 | 0.2 | 21.32 | 1100000 | Plant availability is 100%
2020-12-31 | 7911 | 7.911 | 7.26 | 7.39 | 145 | 16 | 272 | 20 | NA | 500 | 0.3 | 20.41 | 1300000 | Plant availability is 100%
Average | 8059.2258 | 8.0592 | 7.2355 | 7.4987 | 140.3548 | 13.9032 | 265.8065 | 19.4839 | NA | 461.2903 | 0.29032 | 21.5774 | 1303225.8065
Sum | 249836 | 249.836 | 224.3 | 232.46 | 4351 | 431 | 8240 | 604 | NA | 14300 | 9 | 668.9 | 40400000
Source: | Logbook of Laboratory at Sewage Treament Plant
Max |  | 10.603 | 7.38 | 7.74 | 155 | 16 | 280 | 25 | 0 | 600 | 0.5 | 23.5 | 1700000
Min |  | 6.38 | 7.11 | 7.23 | 130 | 13 | 247 | 17 | 0 | 400 | 0.2 | 20.09 | 1100000