## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-07-01 | 40000 | 40 | 7.28 | 7.84 | 145 | 13 | 296 | 40 | 264 | 20 | NA | 700 | 0.3 | 23.3 | 1200000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-07-02 | 40680 | 40.68 | 7.2 | 7.41 | 135 | 14 | 336 | 40 | 228 | 24 | NA | 500 | 0.3 | 24.55 | 1400000
2021-07-03 | 42640 | 42.64 | 7.14 | 7.82 | 140 | 16 | 316 | 36 | 260 | 26 | NA | 700 | 0.2 | 21.5 | 1300000
2021-07-04 | 46350 | 46.35 | 7.21 | 7.61 | 145 | 13 | 344 | 36 | 282 | 28 | NA | 600 | 0.2 | 23.35 | 1400000
2021-07-05 | 44800 | 44.8 | 7.24 | 7.64 | 130 | 16 | 312 | 40 | 274 | 28 | NA | 500 | 0.2 | 21.09 | 1300000
2021-07-06 | 42600 | 42.6 | 7.23 | 7.56 | 150 | 14 | 328 | 44 | 278 | 24 | NA | 700 | 0.3 | 21.62 | 1400000
2021-07-07 | 39370 | 39.37 | 7.26 | 7.49 | 140 | 15 | 300 | 40 | 256 | 28 | NA | 600 | 0.2 | 23.16 | 1300000
2021-07-08 | 45510 | 45.51 | 7.21 | 7.67 | 135 | 12 | 288 | 36 | 268 | 28 | NA | 500 | 0.3 | 24.4 | 1300000
2021-07-09 | 45600 | 45.6 | 7.18 | 7.72 | 140 | 17 | 308 | 40 | 252 | 24 | NA | 700 | 0.2 | 23.67 | 1400000
2021-07-10 | 45110 | 45.11 | 7.27 | 7.78 | 150 | 14 | 328 | 40 | 276 | 18 | NA | 500 | 0.2 | 24.1 | 1200000
2021-07-11 | 39100 | 39.1 | 7.28 | 7.84 | 145 | 18 | 312 | 36 | 232 | 28 | NA | 700 | 0.2 | 22.78 | 1400000
2021-07-12 | 45940 | 45.94 | 7.19 | 7.67 | 150 | 15 | 320 | 40 | 240 | 24 | NA | 600 | 0.2 | 22.27 | 1200000
2021-07-13 | 47500 | 47.5 | 7.22 | 7.64 | 140 | 12 | 308 | 40 | 256 | 26 | NA | 500 | 0.2 | 23.26 | 1300000
2021-07-14 | 47330 | 47.33 | 7.18 | 7.84 | 140 | 16 | 280 | 40 | 276 | 26 | NA | 700 | 0.3 | 23.59 | 1200000
2021-07-15 | 47990 | 47.99 | 7.24 | 7.74 | 135 | 14 | 296 | 44 | 240 | 24 | NA | 500 | 0.2 | 23.12 | 1300000
2021-07-16 | 45810 | 45.81 | 7.29 | 7.64 | 150 | 16 | 328 | 40 | 228 | 28 | NA | 700 | 0.3 | 22.99 | 1400000
2021-07-17 | 45300 | 45.3 | 7.17 | 7.82 | 140 | 12 | 316 | 44 | 242 | 26 | NA | 500 | 0.2 | 23.79 | 1300000
2021-07-18 | 50140 | 50.14 | 7.16 | 7.62 | 145 | 15 | 324 | 40 | 248 | 24 | NA | 600 | 0.2 | 23.53 | 1200000
2021-07-19 | 47900 | 47.9 | 7.28 | 7.89 | 140 | 16 | 320 | 36 | 256 | 22 | NA | 600 | 0.2 | 24.1 | 1400000
2021-07-20 | 42500 | 42.5 | 7.18 | 7.8 | 135 | 14 | 280 | 40 | 264 | 26 | NA | 500 | 0.2 | 22.26 | 1300000
2021-07-21 | 42130 | 42.13 | 7.24 | 7.64 | 130 | 12 | 304 | 36 | 256 | 24 | NA | 700 | 0.3 | 23.35 | 1400000
2021-07-22 | 47300 | 47.3 | 7.32 | 7.64 | 140 | 12 | 316 | 40 | 272 | 24 | NA | 600 | 0.2 | 22.89 | 1200000
2021-07-23 | 43400 | 43.4 | 7.18 | 7.72 | 150 | 13 | 328 | 36 | 242 | 26 | NA | 500 | 0.3 | 22.35 | 1300000
2021-07-24 | 47910 | 47.91 | 7.16 | 7.84 | 130 | 12 | 336 | 40 | 248 | 28 | NA | 600 | 0.3 | 24.04 | 1200000
2021-07-25 | 49660 | 49.66 | 7.24 | 7.64 | 140 | 14 | 312 | 44 | 296 | 26 | NA | 700 | 0.2 | 23.1 | 1300000
2021-07-26 | 51120 | 51.12 | 7.15 | 7.61 | 130 | 16 | 328 | 36 | 228 | 24 | NA | 600 | 0.2 | 22.35 | 1300000
2021-07-27 | 52100 | 52.1 | 7.27 | 7.54 | 150 | 17 | 280 | 40 | 246 | 26 | NA | 500 | 0.3 | 23.52 | 1300000
2021-07-28 | 63110 | 63.11 | 7.19 | 7.71 | 140 | 12 | 316 | 44 | 252 | 28 | NA | 600 | 0.2 | 22.53 | 1200000
2021-07-29 | 57230 | 57.23 | 7.22 | 7.64 | 135 | 13 | 332 | 36 | 240 | 22 | NA | 700 | 0.3 | 23.3 | 1400000
2021-07-30 | 56250 | 56.25 | 7.16 | 7.74 | 145 | 16 | 328 | 40 | 224 | 24 | NA | 400 | 0.2 | 22.99 | 1700000
2021-07-31 | 55160 | 55.16 | 7.22 | 7.85 | 150 | 17 | 316 | 44 | 256 | 26 | NA | 500 | 0.3 | 23.67 | 1200000
Average | 47017.4194 | 47.0174 | 7.2181 | 7.6971 | 140.9677 | 14.3871 | 314.0645 | 39.6129 | 254.1935 | 25.1613 | NA | 590.3226 | 0.23871 | 23.1135 | 1312903.2258
1457.54
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 39100 | 39.1 | 7.14 | 7.41 | 130 | 12 | 280 | 36 | 224 | 18 |  | 400 | 0.2 | 21.09 | 1200000
Max | 63110 | 63.11 | 7.32 | 7.89 | 150 | 18 | 344 | 44 | 296 | 28 |  | 700 | 0.3 | 24.55 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-07-01 | 37830 | 37.83 | 7.49 | 7.39 | 163 | 24 | 356 | 44 | 318 | 33 | NA | 800 | 0.3 | 24.1 | 1700000 | Plant availability is 100%
2021-07-02 | 40340 | 40.34 | 7.56 | 7.45 | 156 | 20 | 368 | 40 | 311 | 38 | NA | 600 | 0.2 | 22.5 | 1400000 | Plant availability is 100%
2021-07-03 | 36700 | 36.7 | 7.51 | 7.48 | 162 | 25 | 360 | 36 | 304 | 35 | NA | 700 | 0.2 | 23.2 | 1200000 | Plant availability is 100%
2021-07-04 | 34680 | 34.68 | 7.57 | 7.46 | 154 | 22 | 356 | 32 | 312 | 31 | NA | 500 | 0.3 | 25.3 | 1300000 | Plant availability is 100%
2021-07-05 | 32880 | 32.88 | 7.48 | 7.41 | 148 | 19 | 352 | 40 | 319 | 34 | NA | 600 | 0.2 | 21.8 | 1200000 | Plant availability is 100%
2021-07-06 | 33070 | 33.07 | 7.54 | 7.49 | 153 | 17 | 356 | 36 | 315 | 38 | NA | 700 | 0.3 | 22.7 | 1100000 | Plant availability is 100%
2021-07-07 | 34760 | 34.76 | 7.59 | 7.37 | 159 | 23 | 364 | 44 | 321 | 36 | NA | 800 | 0.2 | 23.6 | 1300000 | Plant availability is 100%
2021-07-08 | 33910 | 33.91 | 7.56 | 7.45 | 157 | 24 | 352 | 40 | 308 | 38 | NA | 500 | 0.3 | 23.1 | 1700000 | Plant availability is 100%
2021-07-09 | 41380 | 41.38 | 7.54 | 7.36 | 153 | 22 | 356 | 36 | 323 | 33 | NA | 700 | 0.2 | 22.4 | 1400000 | Plant availability is 100%
2021-07-10 | 37100 | 37.1 | 7.47 | 7.42 | 156 | 25 | 360 | 32 | 320 | 35 | NA | 600 | 0.2 | 24.8 | 1300000 | Plant availability is 100%
2021-07-11 | 37650 | 37.65 | 7.53 | 7.39 | 147 | 21 | 364 | 44 | 318 | 34 | NA | 700 | 0.2 | 25.1 | 1700000 | Plant availability is 100%
2021-07-12 | 40700 | 40.7 | 7.49 | 7.43 | 158 | 24 | 356 | 40 | 322 | 31 | NA | 800 | 0.3 | 22.5 | 1200000 | Plant availability is 100%
2021-07-13 | 40570 | 40.57 | 7.55 | 7.4 | 163 | 23 | 352 | 36 | 315 | 36 | NA | 600 | 0.2 | 24.9 | 1100000 | Plant availability is 100%
2021-07-14 | 45100 | 45.1 | 7.47 | 7.38 | 156 | 20 | 360 | 44 | 306 | 39 | NA | 500 | 0.2 | 25.6 | 1400000 | Plant availability is 100%
2021-07-15 | 38030 | 38.03 | 7.59 | 7.37 | 160 | 25 | 368 | 40 | 311 | 38 | NA | 700 | 0.3 | 23.8 | 1700000 | Plant availability is 100%
2021-07-16 | 41050 | 41.05 | 7.54 | 7.44 | 157 | 23 | 364 | 32 | 302 | 41 | NA | 500 | 0.2 | 26.1 | 1300000 | Plant availability is 100%
2021-07-17 | 42760 | 42.76 | 7.48 | 7.49 | 153 | 22 | 356 | 36 | 310 | 37 | NA | 800 | 0.2 | 24.7 | 1400000 | Plant availability is 100%
2021-07-18 | 39760 | 39.76 | 7.52 | 7.42 | 146 | 20 | 360 | 40 | 309 | 35 | NA | 600 | 0.2 | 25.4 | 1200000 | Plant availability is 100%
2021-07-19 | 40820 | 40.82 | 7.57 | 7.38 | 154 | 21 | 368 | 44 | 322 | 32 | NA | 700 | 0.3 | 24.8 | 1700000 | Plant availability is 100%
2021-07-20 | 36100 | 36.1 | 7.54 | 7.43 | 147 | 24 | 364 | 36 | 315 | 36 | NA | 500 | 0.2 | 23.6 | 1100000 | Plant availability is 100%
2021-07-21 | 40080 | 40.08 | 7.62 | 7.46 | 149 | 22 | 372 | 44 | 326 | 39 | NA | 600 | 0.3 | 25.1 | 1300000 | Plant availability is 100%
2021-07-22 | 40140 | 40.14 | 7.56 | 7.39 | 156 | 23 | 356 | 48 | 323 | 38 | NA | 800 | 0.2 | 22.9 | 1200000 | Plant availability is 100%
2021-07-23 | 39290 | 39.29 | 7.59 | 7.35 | 160 | 26 | 360 | 40 | 318 | 31 | NA | 500 | 0.2 | 24.6 | 1400000 | Plant availability is 100%
2021-07-24 | 45010 | 45.01 | 7.48 | 7.41 | 146 | 22 | 352 | 36 | 309 | 34 | NA | 700 | 0.3 | 23.2 | 1100000 | Plant availability is 100%
2021-07-25 | 43390 | 43.39 | 7.58 | 7.45 | 151 | 25 | 356 | 32 | 314 | 38 | NA | 800 | 0.2 | 26.3 | 1700000 | Plant availability is 100%
2021-07-26 | 41640 | 41.64 | 7.64 | 7.42 | 155 | 23 | 352 | 40 | 310 | 35 | NA | 600 | 0.2 | 24.1 | 1400000 | Plant availability is 100%
2021-07-27 | 41620 | 41.62 | 7.49 | 7.46 | 149 | 24 | 360 | 44 | 326 | 40 | NA | 700 | 0.2 | 25.4 | 1200000 | Plant availability is 100%
2021-07-28 | 41570 | 41.57 | 7.52 | 7.4 | 152 | 22 | 356 | 36 | 318 | 37 | NA | 500 | 0.3 | 23.8 | 1300000 | Plant availability is 100%
2021-07-29 | 38690 | 38.69 | 7.48 | 7.37 | 154 | 24 | 352 | 32 | 321 | 34 | NA | 600 | 0.3 | 24.7 | 1700000 | Plant availability is 100%
2021-07-30 | 44690 | 44.69 | 7.45 | 7.41 | 148 | 25 | 356 | 40 | 316 | 36 | NA | 800 | 0.2 | 22.6 | 1100000 | Plant availability is 100%
2021-07-31 | 38360 | 38.36 | 7.49 | 7.37 | 149 | 26 | 352 | 36 | 305 | 31 | NA | 600 | 0.2 | 25.2 | 1400000 | Plant availability is 100%
Average | 39344.1935 | 39.3442 | 7.5319 | 7.4161 | 153.9032 | 22.7742 | 358.5806 | 38.7097 | 315.0645 | 35.5806 | NA | 648.3871 | 0.23548 | 24.1258 | 1361290.3226
1219.67
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 32880 | 32.88 | 7.45 | 7.35 | 146 | 17 | 352 | 32 | 302 | 31 |  | 500 | 0.2 | 21.8 | 1100000
Max | 45100 | 45.1 | 7.64 | 7.49 | 163 | 26 | 372 | 48 | 326 | 41 |  | 800 | 0.3 | 26.3 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-07-01 | 21250 | 21.25 | 7.33 | 7.46 | 135 | 13 | 356 | 40 | 292 | 20 | NA | 700 | 0.2 | 25 | 1300000 | Retaining wall for nearby drain is broken.
2021-07-02 | 24100 | 24.1 | 7.41 | 7.52 | 130 | 14 | 344 | 44 | 288 | 19 | NA | 600 | 0.3 | 24.4 | 1200000
2021-07-03 | 20680 | 20.68 | 7.53 | 7.66 | 140 | 12 | 360 | 36 | 296 | 21 | NA | 800 | 0.3 | 24.3 | 1500000
2021-07-04 | 21560 | 21.56 | 7.44 | 7.53 | 144 | 13 | 336 | 40 | 282 | 20 | NA | 600 | 0.2 | 24.5 | 1300000
2021-07-05 | 20190 | 20.19 | 7.53 | 7.66 | 140 | 14 | 348 | 32 | 292 | 22 | NA | 700 | 0.3 | 24.2 | 1600000
2021-07-06 | 19700 | 19.7 | 7.55 | 7.68 | 145 | 12 | 356 | 44 | 302 | 23 | NA | 500 | 0.2 | 24.4 | 1200000
2021-07-07 | 18940 | 18.94 | 7.44 | 7.59 | 130 | 11 | 332 | 36 | 296 | 20 | NA | 600 | 0.3 | 24.3 | 1300000
2021-07-08 | 18780 | 18.78 | 7.44 | 7.66 | 135 | 13 | 344 | 40 | 284 | 19 | NA | 700 | 0.2 | 24.5 | 1400000
2021-07-09 | 18360 | 18.36 | 7.53 | 7.52 | 130 | 12 | 336 | 36 | 294 | 20 | NA | 600 | 0.3 | 24.3 | 1500000
2021-07-10 | 18770 | 18.77 | 7.46 | 7.58 | 133 | 14 | 332 | 40 | 302 | 22 | NA | 500 | 0.2 | 24.6 | 1200000
2021-07-11 | 24890 | 24.89 | 7.51 | 7.64 | 135 | 11 | 348 | 32 | 288 | 19 | NA | 400 | 0.3 | 24.1 | 1400000
2021-07-12 | 22150 | 22.15 | 7.49 | 7.66 | 140 | 13 | 356 | 36 | 303 | 21 | NA | 700 | 0.2 | 24.3 | 1600000
2021-07-13 | 17890 | 17.89 | 7.44 | 7.53 | 130 | 11 | 340 | 44 | 308 | 23 | NA | 500 | 0.3 | 24.7 | 1300000
2021-07-14 | 18350 | 18.35 | 7.46 | 7.58 | 140 | 12 | 348 | 32 | 294 | 20 | NA | 600 | 0.2 | 24.2 | 1500000
2021-07-15 | 17580 | 17.58 | 7.52 | 7.61 | 135 | 14 | 356 | 40 | 292 | 22 | NA | 700 | 0.3 | 24.4 | 1200000
2021-07-16 | 18050 | 18.05 | 7.43 | 7.54 | 145 | 11 | 360 | 44 | 306 | 23 | NA | 800 | 0.2 | 24.3 | 1400000
2021-07-17 | 17820 | 17.82 | 7.51 | 7.64 | 130 | 13 | 344 | 36 | 302 | 20 | NA | 600 | 0.3 | 24.5 | 1500000
2021-07-18 | 15740 | 15.74 | 7.56 | 7.69 | 140 | 11 | 352 | 32 | 298 | 23 | NA | 400 | 0.2 | 24.1 | 1300000
2021-07-19 | 17870 | 17.87 | 7.44 | 7.55 | 148 | 13 | 340 | 40 | 292 | 22 | NA | 400 | 0.2 | 24.3 | 1400000
2021-07-20 | 16560 | 16.56 | 7.28 | 7.44 | 125 | 12 | 332 | 36 | 288 | 19 | NA | 700 | 0.3 | 24.4 | 1200000
2021-07-21 | 16210 | 16.21 | 7.33 | 7.49 | 135 | 15 | 348 | 44 | 276 | 23 | NA | 500 | 0.2 | 24.2 | 1400000
2021-07-22 | 15980 | 15.98 | 7.44 | 7.56 | 133 | 13 | 352 | 36 | 280 | 21 | NA | 400 | 0.3 | 24 | 1300000
2021-07-23 | 18920 | 18.92 | 7.51 | 7.67 | 129 | 11 | 332 | 32 | 301 | 20 | NA | 700 | 0.2 | 23.9 | 1600000
2021-07-24 | 21410 | 21.41 | 7.35 | 7.58 | 133 | 14 | 352 | 36 | 288 | 18 | NA | 600 | 0.3 | 24.4 | 1400000
2021-07-25 | 21780 | 21.78 | 7.44 | 7.59 | 136 | 13 | 356 | 40 | 306 | 23 | NA | 200 | 0.2 | 24.5 | 1500000
2021-07-26 | 20900 | 20.9 | 7.52 | 7.66 | 135 | 11 | 348 | 44 | 296 | 20 | NA | 500 | 0.3 | 26 | 1600000
2021-07-27 | 21100 | 21.1 | 7.48 | 7.53 | 129 | 13 | 340 | 40 | 288 | 19 | NA | 700 | 0.2 | 25.9 | 1300000
2021-07-28 | 27690 | 27.69 | 7.53 | 7.66 | 133 | 14 | 332 | 36 | 292 | 21 | NA | 600 | 0.3 | 24.4 | 1500000
2021-07-29 | 28110 | 28.11 | 7.44 | 7.55 | 140 | 12 | 336 | 32 | 284 | 19 | NA | 500 | 0.2 | 25.8 | 1200000
2021-07-30 | 26360 | 26.36 | 7.56 | 7.68 | 129 | 13 | 344 | 44 | 298 | 22 | NA | 600 | 0.3 | 25.3 | 1400000
2021-07-31 | 26130 | 26.13 | 7.36 | 7.55 | 135 | 15 | 336 | 36 | 307 | 23 | NA | 500 | 0.3 | 24.4 | 1500000
Average | 20445.8065 | 20.4458 | 7.46 | 7.589 | 135.3871 | 12.6774 | 345.0323 | 38.0645 | 294.0323 | 20.871 | NA | 577.4194 | 0.25161 | 24.5355 | 1387096.7742
633.82
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 15740 | 15.74 | 7.28 | 7.44 | 125 | 11 | 332 | 32 | 276 | 18 |  | 200 | 0.2 | 23.9 | 1200000
Max | 28110 | 28.11 | 7.56 | 7.69 | 148 | 15 | 360 | 44 | 308 | 23 |  | 800 | 0.3 | 26 | 1600000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-07-01 | 7220 | 7.22 | 7.2 | 7.48 | 135 | 14 | 296 | 32 | 256 | 21 | NA | 500 | 0.3 | 21.33 | 1400000 | Plant availability is 100%
2021-07-02 | 7980 | 7.98 | 7.34 | 7.59 | 140 | 16 | 312 | 40 | 267 | 23 | NA | 400 | 0.2 | 22.14 | 1600000 | Plant availability is 100%
2021-07-03 | 7960 | 7.96 | 7.15 | 7.39 | 145 | 15 | 320 | 36 | 274 | 20 | NA | 600 | 0.3 | 23.21 | 1700000 | Plant availability is 100%
2021-07-04 | 7910 | 7.91 | 7.23 | 7.61 | 138 | 14 | 308 | 44 | 263 | 24 | NA | 450 | 0.2 | 20.49 | 1400000 | Plant availability is 100%
2021-07-05 | 7940 | 7.94 | 7.19 | 7.56 | 142 | 16 | 316 | 40 | 255 | 22 | NA | 500 | 0.2 | 21.13 | 1300000 | Plant availability is 100%
2021-07-06 | 7920 | 7.92 | 7.11 | 7.33 | 136 | 15 | 304 | 44 | 246 | 23 | NA | 600 | 0.3 | 22.31 | 1600000 | Plant availability is 100%
2021-07-07 | 7910 | 7.91 | 7.22 | 7.42 | 140 | 14 | 312 | 36 | 259 | 21 | NA | 400 | 0.2 | 20.64 | 1400000 | Plant availability is 100%
2021-07-08 | 7920 | 7.92 | 7.31 | 7.67 | 135 | 16 | 300 | 40 | 270 | 24 | NA | 500 | 0.3 | 21.19 | 1700000 | Plant availability is 100%
2021-07-09 | 7930 | 7.93 | 7.14 | 7.54 | 130 | 15 | 308 | 44 | 250 | 22 | NA | 400 | 0.2 | 20.82 | 1300000 | Plant availability is 100%
2021-07-10 | 7890 | 7.89 | 7.24 | 7.61 | 138 | 16 | 320 | 40 | 276 | 23 | NA | 500 | 0.2 | 22.15 | 1600000 | Plant availability is 100%
2021-07-11 | 7650 | 7.65 | 7.29 | 7.58 | 140 | 14 | 316 | 36 | 265 | 20 | NA | 400 | 0.3 | 23.36 | 1400000 | Plant availability is 100%
2021-07-12 | 7930 | 7.93 | 7.18 | 7.49 | 136 | 15 | 304 | 40 | 252 | 22 | NA | 500 | 0.2 | 22.24 | 1300000 | Plant availability is 100%
2021-07-13 | 7680 | 7.68 | 7.23 | 7.44 | 142 | 14 | 312 | 36 | 264 | 19 | NA | 600 | 0.2 | 21.3 | 1600000 | Plant availability is 100%
2021-07-14 | 7760 | 7.76 | 7.33 | 7.51 | 135 | 15 | 300 | 40 | 260 | 21 | NA | 500 | 0.3 | 22.16 | 1400000 | Plant availability is 100%
2021-07-15 | 7920 | 7.92 | 7.16 | 7.38 | 140 | 14 | 308 | 36 | 256 | 23 | NA | 400 | 0.2 | 21.4 | 1300000 | Plant availability is 100%
2021-07-16 | 7980 | 7.98 | 7.22 | 7.64 | 132 | 16 | 296 | 40 | 266 | 22 | NA | 450 | 0.2 | 23.22 | 1700000 | Plant availability is 100%
2021-07-17 | 7910 | 7.91 | 7.13 | 7.41 | 138 | 14 | 316 | 36 | 248 | 20 | NA | 600 | 0.2 | 22.58 | 1600000 | Plant availability is 100%
2021-07-18 | 7790 | 7.79 | 7.28 | 7.55 | 135 | 15 | 304 | 44 | 264 | 24 | NA | 500 | 0.3 | 21.46 | 1400000 | Plant availability is 100%
2021-07-19 | 7950 | 7.95 | 7.34 | 7.67 | 140 | 16 | 312 | 40 | 251 | 22 | NA | 400 | 0.2 | 20.86 | 1300000 | Plant availability is 100%
2021-07-20 | 7990 | 7.99 | 7.17 | 7.43 | 136 | 14 | 308 | 36 | 258 | 21 | NA | 500 | 0.2 | 21.32 | 1600000 | Plant availability is 100%
2021-07-21 | 7970 | 7.97 | 7.24 | 7.44 | 145 | 15 | 320 | 40 | 271 | 23 | NA | 600 | 0.3 | 23.25 | 1400000 | Plant availability is 100%
2021-07-22 | 7980 | 7.98 | 7.19 | 7.53 | 142 | 16 | 312 | 44 | 262 | 22 | NA | 500 | 0.3 | 20.72 | 1300000 | Plant availability is 100%
2021-07-23 | 7960 | 7.96 | 7.26 | 7.62 | 138 | 14 | 300 | 36 | 252 | 24 | NA | 400 | 0.2 | 21.44 | 1600000 | Plant availability is 100%
2021-07-24 | 7980 | 7.98 | 7.23 | 7.69 | 140 | 15 | 316 | 40 | 265 | 21 | NA | 500 | 0.3 | 20.68 | 1400000 | Plant availability is 100%
2021-07-25 | 7930 | 7.93 | 7.27 | 7.73 | 135 | 14 | 308 | 36 | 242 | 23 | NA | 700 | 0.2 | 22.49 | 1700000 | Plant availability is 100%
2021-07-26 | 7950 | 7.95 | 7.14 | 7.36 | 130 | 15 | 296 | 44 | 255 | 22 | NA | 600 | 0.3 | 23.12 | 1600000 | Plant availability is 100%
2021-07-27 | 7500 | 7.5 | 7.27 | 7.51 | 136 | 13 | 304 | 36 | 266 | 24 | NA | 400 | 0.2 | 22.39 | 1300000 | Plant availability is 100%
2021-07-28 | 7990 | 7.99 | 7.36 | 7.76 | 140 | 15 | 320 | 40 | 275 | 21 | NA | 500 | 0.2 | 23.78 | 1400000 | Plant availability is 100%
2021-07-29 | 7700 | 7.7 | 7.18 | 7.39 | 138 | 14 | 312 | 36 | 249 | 20 | NA | 600 | 0.3 | 21.69 | 1600000 | Plant availability is 100%
2021-07-30 | 7970 | 7.97 | 7.29 | 7.56 | 145 | 16 | 324 | 40 | 270 | 23 | NA | 400 | 0.2 | 22.58 | 1200000 | Plant availability is 100%
2021-07-31 | 7800 | 7.8 | 7.15 | 7.63 | 142 | 14 | 316 | 36 | 257 | 21 | NA | 500 | 0.2 | 21.46 | 1300000 | Plant availability is 100%
Average | 7866.7742 | 7.8668 | 7.2271 | 7.5329 | 138.1935 | 14.8065 | 309.6774 | 38.9677 | 260.129 | 21.9677 | NA | 496.7742 | 0.23871 | 21.9003 | 1464516.129
243.87
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 7220 | 7.22 | 7.11 | 7.33 | 130 | 13 | 296 | 32 | 242 | 19 |  | 400 | 0.2 | 20.49 | 1200000
Max | 7990 | 7.99 | 7.36 | 7.76 | 145 | 16 | 324 | 44 | 276 | 24 |  | 700 | 0.3 | 23.78 | 1700000