## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-06-01 | 58890 | 58.89 | 7.18 | 7.69 | 130 | 18 | 296 | 28 | NA | 700 | 0.2 | 23.11 | 1400000
2021-06-02 | 56890 | 56.89 | 7.22 | 7.83 | 150 | 14 | 260 | 24 | NA | 500 | 0.3 | 23.14 | 1200000
2021-06-03 | 60750 | 60.75 | 7.09 | 7.54 | 140 | 16 | 264 | 28 | NA | 700 | 0.2 | 23.42 | 1300000
2021-06-04 | 58210 | 58.21 | 7.21 | 7.64 | 145 | 17 | 272 | 26 | NA | 400 | 0.3 | 22.52 | 1400000
2021-06-05 | 59210 | 59.21 | 7.18 | 7.72 | 150 | 15 | 292 | 28 | NA | 700 | 0.2 | 24.75 | 1700000
2021-06-06 | 57120 | 57.12 | 7.26 | 7.64 | 135 | 18 | 224 | 26 | NA | 500 | 0.3 | 23.62 | 1200000
2021-06-07 | 56220 | 56.22 | 7.16 | 7.72 | 130 | 14 | 270 | 28 | NA | 400 | 0.2 | 23.95 | 1400000
2021-06-08 | 60230 | 60.23 | 7.22 | 7.64 | 150 | 18 | 228 | 24 | NA | 500 | 0.3 | 23.32 | 1200000
2021-06-09 | 59210 | 59.21 | 7.24 | 7.84 | 140 | 16 | 264 | 28 | NA | 700 | 0.3 | 24.17 | 1300000
2021-06-10 | 55680 | 55.68 | 7.2 | 7.62 | 140 | 14 | 250 | 26 | NA | 500 | 0.2 | 24.1 | 1400000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-06-11 | 51660 | 51.66 | 7.32 | 7.54 | 150 | 16 | 272 | 24 | NA | 700 | 0.3 | 21.79 | 1200000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is repaired.
2021-06-12 | 56220 | 56.22 | 7.26 | 7.71 | 144 | 16 | 268 | 22 | NA | 600 | 0.2 | 22.5 | 1300000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain.
2021-06-13 | 56400 | 56.4 | 7.21 | 7.46 | 130 | 18 | 264 | 24 | NA | 400 | 0.3 | 23.41 | 1400000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain.
2021-06-14 | 56590 | 56.59 | 7.24 | 7.64 | 132 | 16 | 232 | 24 | NA | 500 | 0.2 | 23.62 | 1200000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-06-15 | 51050 | 51.05 | 7.21 | 7.65 | 128 | 14 | 256 | 28 | NA | 400 | 0.3 | 23.4 | 1300000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-06-16 | 56050 | 56.05 | 7.32 | 7.59 | 120 | 16 | 248 | 22 | NA | 600 | 0.2 | 24.32 | 1200000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is repaired.
2021-06-17 | 55210 | 55.21 | 7.26 | 7.63 | 126 | 14 | 244 | 24 | NA | 500 | 0.3 | 23.8 | 1300000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain.
2021-06-18 | 52240 | 52.24 | 7.42 | 7.72 | 130 | 14 | 221 | 22 | NA | 700 | 0.2 | 23.32 | 1400000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-06-19 | 43270 | 43.27 | 7.42 | 7.58 | 135 | 16 | 230 | 24 | NA | 600 | 0.3 | 21.79 | 1200000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-06-20 | 28150 | 28.15 | 7.56 | 7.65 | 140 | 14 | 237 | 22 | NA | 400 | 0.2 | 23.62 | 1300000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-06-21 | 24250 | 24.25 | 7.48 | 7.58 | 150 | 16 | 226 | 20 | NA | 400 | 0.2 | 23.5 | 1200000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-06-22 | 48200 | 48.2 | 7.63 | 7.63 | 140 | 16 | 219 | 23 | NA | 600 | 0.3 | 23.65 | 1300000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-06-23 | 45900 | 45.9 | 7.6 | 7.83 | 150 | 15 | 272 | 24 | NA | 700 | 0.2 | 21.79 | 1200000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-06-24 | 44500 | 44.5 | 7.48 | 7.84 | 145 | 14 | 264 | 22 | NA | 700 | 0.3 | 23.4 | 1300000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-06-25 | 46500 | 46.5 | 7.15 | 7.46 | 140 | 12 | 232 | 24 | NA | 400 | 0.3 | 21.61 | 1400000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-06-26 | 49450 | 49.45 | 7.19 | 7.64 | 135 | 16 | 268 | 28 | NA | 600 | 0.2 | 22.52 | 1200000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-06-27 | 50820 | 50.82 | 7.24 | 7.84 | 140 | 13 | 240 | 24 | NA | 400 | 0.3 | 22.51 | 1300000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-06-28 | 48930 | 48.93 | 7.18 | 7.74 | 145 | 14 | 228 | 22 | NA | 700 | 0.3 | 23.4 | 1400000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-06-29 | 32100 | 32.1 | 7.21 | 7.64 | 135 | 16 | 248 | 26 | NA | 600 | 0.2 | 24.07 | 1200000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-06-30 | 35420 | 35.42 | 7.19 | 7.86 | 150 | 12 | 240 | 24 | NA | 400 | 0.3 | 22.42 | 1300000 | 1. Retaining wall for nalla at Sasur Kadheri SPS is damaged due to heavy rain. 2. Retaining wall for nalla at Ghagharnalla MPS is damaged due to heavy rain.
Average | 50510.6667 | 50.5107 | 7.2843 | 7.6703 | 139.1667 | 15.2667 | 250.9667 | 24.6333 | NA | 550 | 0.25333 | 23.218 | 1303333.3333
1515.32
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 60750 | 60.75 | 7.63 | 7.86 | 150 | 18 | 296 | 28 |  | 700 | 0.3 | 24.75 | 1700000
Min | 24250 | 24.25 | 7.09 | 7.46 | 120 | 12 | 219 | 20 |  | 400 | 0.2 | 21.61 | 1200000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-06-01 | 27710 | 27.71 | 7.45 | 7.58 | 159 | 17 | 322 | 34 | NA | 700 | 0.2 | 23.8 | 1300000
2021-06-02 | 26250 | 26.25 | 7.48 | 7.68 | 153 | 19 | 332 | 38 | NA | 800 | 0.2 | 22.1 | 1400000
2021-06-03 | 25020 | 25.02 | 7.36 | 7.52 | 156 | 21 | 325 | 40 | NA | 700 | 0.2 | 21.3 | 1100000
2021-06-04 | 27110 | 27.11 | 7.32 | 7.63 | 163 | 23 | 312 | 42 | NA | 800 | 0.2 | 24.5 | 1700000
2021-06-05 | 29050 | 29.05 | 7.46 | 7.55 | 149 | 20 | 308 | 38 | NA | 600 | 0.3 | 23.8 | 1400000
2021-06-06 | 33790 | 33.79 | 7.51 | 7.41 | 153 | 22 | 314 | 36 | NA | 700 | 0.2 | 24.6 | 1300000
2021-06-07 | 29020 | 29.02 | 7.48 | 7.62 | 156 | 23 | 319 | 34 | NA | 800 | 0.2 | 23.9 | 1100000
2021-06-08 | 33560 | 33.56 | 7.53 | 7.44 | 159 | 21 | 324 | 35 | NA | 600 | 0.3 | 24.8 | 1400000
2021-06-09 | 31570 | 31.57 | 7.55 | 7.42 | 163 | 24 | 332 | 33 | NA | 700 | 0.2 | 26.3 | 1700000
2021-06-10 | 35840 | 35.84 | 7.57 | 7.38 | 156 | 22 | 328 | 35 | NA | 800 | 0.2 | 25.3 | 1300000
2021-06-11 | 33700 | 33.7 | 7.48 | 7.44 | 153 | 20 | 335 | 34 | NA | 600 | 0.3 | 24.3 | 1400000
2021-06-12 | 35240 | 35.24 | 7.56 | 7.49 | 149 | 18 | 329 | 36 | NA | 800 | 0.2 | 23.1 | 1100000
2021-06-13 | 35380 | 35.38 | 7.45 | 7.37 | 156 | 21 | 318 | 38 | NA | 700 | 0.2 | 25.8 | 1700000
2021-06-14 | 35620 | 35.62 | 7.53 | 7.45 | 153 | 17 | 310 | 40 | NA | 600 | 0.2 | 22.1 | 1100000
2021-06-15 | 31700 | 31.7 | 7.56 | 7.42 | 146 | 19 | 305 | 34 | NA | 500 | 0.3 | 23.8 | 1200000
2021-06-16 | 33760 | 33.76 | 7.48 | 7.4 | 153 | 20 | 301 | 31 | NA | 700 | 0.2 | 24.9 | 1300000
2021-06-17 | 33430 | 33.43 | 7.55 | 7.46 | 149 | 22 | 308 | 35 | NA | 800 | 0.2 | 21.3 | 1700000
2021-06-18 | 35320 | 35.32 | 7.57 | 7.48 | 146 | 25 | 315 | 34 | NA | 600 | 0.3 | 22.7 | 1400000
2021-06-19 | 32310 | 32.31 | 7.45 | 7.52 | 153 | 23 | 322 | 36 | NA | 800 | 0.2 | 21.4 | 1100000
2021-06-20 | 36990 | 36.99 | 7.42 | 7.49 | 146 | 26 | 298 | 38 | NA | 700 | 0.2 | 22.3 | 1300000
2021-06-21 | 32990 | 32.99 | 7.55 | 7.45 | 153 | 24 | 305 | 35 | NA | 800 | 0.2 | 23.8 | 1200000
2021-06-22 | 34080 | 34.08 | 7.48 | 7.39 | 159 | 22 | 311 | 38 | NA | 500 | 0.3 | 22.1 | 1400000
2021-06-23 | 38170 | 38.17 | 7.54 | 7.35 | 156 | 20 | 317 | 36 | NA | 700 | 0.2 | 23.3 | 1300000
2021-06-24 | 42170 | 42.17 | 7.57 | 7.48 | 163 | 18 | 312 | 32 | NA | 500 | 0.3 | 21.6 | 1100000
2021-06-25 | 38360 | 38.36 | 7.52 | 7.42 | 160 | 22 | 322 | 31 | NA | 600 | 0.2 | 24.8 | 1200000
2021-06-26 | 40350 | 40.35 | 7.45 | 7.54 | 158 | 19 | 328 | 34 | NA | 700 | 0.2 | 22.3 | 1400000
2021-06-27 | 41230 | 41.23 | 7.48 | 7.59 | 162 | 21 | 320 | 36 | NA | 600 | 0.3 | 21.5 | 1300000
2021-06-28 | 39490 | 39.49 | 7.42 | 7.53 | 156 | 23 | 315 | 38 | NA | 800 | 0.2 | 22.7 | 1400000
2021-06-29 | 35590 | 35.59 | 7.55 | 7.48 | 154 | 20 | 310 | 40 | NA | 500 | 0.2 | 25.8 | 1100000
2021-06-30 | 37230 | 37.23 | 7.45 | 7.52 | 159 | 23 | 327 | 36 | NA | 600 | 0.2 | 23.7 | 1200000
Average | 34067.6667 | 34.0677 | 7.4923 | 7.4833 | 155.0333 | 21.1667 | 317.4667 | 35.9 | NA | 676.6667 | 0.22667 | 23.4567 | 1320000
1022.03
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 42170 | 42.17 | 7.57 | 7.68 | 163 | 26 | 335 | 42 |  | 800 | 0.3 | 26.3 | 1700000
Min | 25020 | 25.02 | 7.32 | 7.35 | 146 | 17 | 298 | 31 |  | 500 | 0.2 | 21.3 | 1100000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-06-01 | 20520 | 20.52 | 7.11 | 7.56 | 135 | 13 | 263 | 23 | NA | 600 | 0.2 | 25.1 | 1700000 | Retaining wall for nearby drain is broken.
2021-06-02 | 19830 | 19.83 | 7.18 | 7.79 | 140 | 14 | 280 | 22 | NA | 500 | 0.2 | 24.01 | 1600000 | Retaining wall for nearby drain is broken.
2021-06-03 | 19560 | 19.56 | 7.2 | 7.69 | 138 | 12 | 245 | 21 | NA | 600 | 0.3 | 25.28 | 1600000 | Retaining wall for nearby drain is broken.
2021-06-04 | 19680 | 19.68 | 7.13 | 7.71 | 133 | 14 | 264 | 20 | NA | 400 | 0.2 | 23.96 | 1400000 | Retaining wall for nearby drain is broken.
2021-06-05 | 19270 | 19.27 | 7.17 | 7.67 | 140 | 13 | 258 | 23 | NA | 700 | 0.2 | 24.67 | 1700000 | Retaining wall for nearby drain is broken.
2021-06-06 | 20720 | 20.72 | 7.1 | 7.54 | 139 | 11 | 316 | 25 | NA | 600 | 0.2 | 24.11 | 1500000 | Retaining wall for nearby drain is broken.
2021-06-07 | 19610 | 19.61 | 7.18 | 7.63 | 142 | 12 | 285 | 23 | NA | 800 | 0.2 |  |  | 1. Retaining wall for nearby drain is broken. 2. Sludge dewatering unit was not operated due to maintenance of thickener.
2021-06-08 | 19460 | 19.46 | 7.21 | 7.44 | 145 | 13 | 288 | 20 | NA | 700 | 0.2 | 24.4 | 1700000 | Retaining wall for nearby drain is broken.
2021-06-09 | 19500 | 19.5 | 7.33 | 7.56 | 140 | 12 | 280 | 22 | NA | 500 | 0.3 | 24.5 | 1400000 | Retaining wall for nearby drain is broken.
2021-06-10 | 21260 | 21.26 | 7.22 | 7.32 | 139 | 11 | 302 | 19 | NA | 600 | 0.2 | 24.3 | 1500000 | Retaining wall for nearby drain is broken.
2021-06-11 | 19770 | 19.77 | 7.25 | 7.44 | 136 | 13 | 284 | 21 | NA | 800 | 0.2 | 24.4 | 1700000 | Retaining wall for nearby drain is broken.
2021-06-12 | 20250 | 20.25 | 7.15 | 7.62 | 142 | 15 | 290 | 20 | NA | 500 | 0.2 | 25.6 | 1600000 | Retaining wall for nearby drain is broken.
2021-06-13 | 22980 | 22.98 | 7.2 | 7.8 | 135 | 12 | 285 | 23 | NA | 700 | 0.2 | 24.73 | 1400000 | Retaining wall for nearby drain is broken.
2021-06-14 | 26930 | 26.93 | 7.25 | 7.63 | 140 | 13 | 290 | 22 | NA | 600 | 0.2 | 23.9 | 1300000 | Retaining wall for nearby drain is broken.
2021-06-15 | 20930 | 20.93 | 7.32 | 7.54 | 142 | 12 | 296 | 20 | NA | 700 | 0.3 | 24.1 | 1500000 | Retaining wall for nearby drain is broken.
2021-06-16 | 19830 | 19.83 | 7.56 | 7.66 | 136 | 14 | 288 | 22 | NA | 500 | 0.2 | 24.5 | 1200000 | Retaining wall for nearby drain is broken.
2021-06-17 | 26230 | 26.23 | 7.53 | 7.59 | 135 | 11 | 276 | 20 | NA | 600 | 0.3 | 24.4 | 1400000 | Retaining wall for nearby drain is broken.
2021-06-18 | 25190 | 25.19 | 7.52 | 7.64 | 139 | 13 | 268 | 21 | NA | 800 | 0.2 | 24.2 | 1600000 | Retaining wall for nearby drain is broken.
2021-06-19 | 27830 | 27.83 | 7.59 | 7.67 | 130 | 14 | 290 | 23 | NA | 600 | 0.2 | 24.9 | 1400000 | Retaining wall for nearby drain is broken.
2021-06-20 | 22530 | 22.53 | 7.34 | 7.63 | 138 | 11 | 285 | 20 | NA | 800 | 0.2 | 24.4 | 1500000 | Retaining wall for nearby drain is broken.
2021-06-21 | 21650 | 21.65 | 7.35 | 7.58 | 142 | 13 | 288 | 18 | NA | 700 | 0.2 | 24.2 | 1200000 | Retaining wall for nearby drain is broken.
2021-06-22 | 23420 | 23.42 | 7.36 | 7.49 | 138 | 12 | 294 | 21 | NA | 600 | 0.3 | 24.5 | 1400000 | Retaining wall for nearby drain is broken.
2021-06-23 | 22140 | 22.14 | 7.49 | 7.56 | 135 | 14 | 288 | 19 | NA | 500 | 0.2 | 24.2 | 1200000 | Retaining wall for nearby drain is broken.
2021-06-24 | 25960 | 25.96 | 7.33 | 7.44 | 133 | 13 | 276 | 22 | NA | 600 | 0.3 | 24 | 1500000 | Retaining wall for nearby drain is broken.
2021-06-25 | 20810 | 20.81 | 7.38 | 7.65 | 130 | 15 | 256 | 21 | NA | 700 | 0.3 | 24.09 | 1400000 | Retaining wall for nearby drain is broken.
2021-06-26 | 23030 | 23.03 | 7.21 | 7.73 | 135 | 12 | 247 | 20 | NA | 600 | 0.2 | 24.3 | 1300000 | Retaining wall for nearby drain is broken.
2021-06-27 | 23590 | 23.59 | 7.36 | 7.49 | 140 | 11 | 266 | 22 | NA | 500 | 0.3 | 24.5 | 1500000 | Retaining wall for nearby drain is broken.
2021-06-28 | 20380 | 20.38 | 7.44 | 7.56 | 143 | 13 | 278 | 20 | NA | 700 | 0.2 | 24.3 | 1200000 | Retaining wall for nearby drain is broken.
2021-06-29 | 19610 | 19.61 | 7.52 | 7.66 | 145 | 14 | 288 | 23 | NA | 800 | 0.3 | 24.4 | 1400000 | Retaining wall for nearby drain is broken.
2021-06-30 | 22970 | 22.97 | 7.44 | 7.59 | 135 | 12 | 292 | 21 | NA | 500 | 0.2 | 24.5 | 1500000 | Retaining wall for nearby drain is broken.
Average | 21848 | 21.848 | 7.314 | 7.596 | 138 | 12.7333 | 280.2 | 21.2333 | NA | 626.6667 | 0.23 | 24.4293 | 1458620.6897
655.44
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 27830 | 27.83 | 7.59 | 7.8 | 145 | 15 | 316 | 25 |  | 800 | 0.3 | 25.6 | 1700000
Min | 19270 | 19.27 | 7.1 | 7.32 | 130 | 11 | 245 | 18 |  | 400 | 0.2 | 23.9 | 1200000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-06-01 | 7390 | 7.39 | 7.16 | 7.39 | 130 | 13 | 248 | 22 | NA | 500 | 0.2 | 22.19 | 1400000
2021-06-02 | 7470 | 7.47 | 7.29 | 7.56 | 140 | 15 | 265 | 24 | NA | 400 | 0.3 | 21.64 | 1600000
2021-06-03 | 7580 | 7.58 | 7.18 | 7.43 | 135 | 14 | 256 | 21 | NA | 600 | 0.2 | 23.11 | 1300000
2021-06-04 | 7970 | 7.97 | 7.24 | 7.61 | 142 | 13 | 270 | 23 | NA | 500 | 0.2 | 22.44 | 1400000
2021-06-05 | 7950 | 7.95 | 7.14 | 7.33 | 145 | 15 | 259 | 20 | NA | 400 | 0.3 | 21.31 | 1700000
2021-06-06 | 7920 | 7.92 | 7.29 | 7.7 | 150 | 14 | 273 | 22 | NA | 500 | 0.3 | 23.54 | 1600000
2021-06-07 | 7830 | 7.83 | 7.15 | 7.44 | 140 | 16 | 251 | 21 | NA | 600 | 0.2 | 22.26 | 1400000
2021-06-08 | 7530 | 7.53 | 7.27 | 7.59 | 146 | 13 | 264 | 23 | NA | 400 | 0.3 | 24.17 | 1300000
2021-06-09 | 7450 | 7.45 | 7.12 | 7.37 | 138 | 15 | 250 | 20 | NA | 500 | 0.2 | 23.39 | 1600000
2021-06-10 | 7230 | 7.23 | 7.24 | 7.66 | 135 | 14 | 242 | 22 | NA | 450 | 0.2 | 21.22 | 1400000
2021-06-11 | 7180 | 7.18 | 7.11 | 7.49 | 132 | 13 | 256 | 24 | NA | 600 | 0.3 | 22.12 | 1700000
2021-06-12 | 7570 | 7.57 | 7.17 | 7.38 | 142 | 15 | 266 | 21 | NA | 400 | 0.2 | 23.33 | 1300000
2021-06-13 | 7970 | 7.97 | 7.21 | 7.45 | 146 | 14 | 276 | 23 | NA | 500 | 0.2 | 20.82 | 1400000
2021-06-14 | 7800 | 7.8 | 7.13 | 7.31 | 140 | 13 | 253 | 20 | NA | 450 | 0.3 | 21.71 | 1600000
2021-06-15 | 7100 | 7.1 | 7.25 | 7.51 | 132 | 15 | 260 | 22 | NA | 600 | 0.2 | 22.66 | 1700000
2021-06-16 | 7610 | 7.61 | 7.33 | 7.69 | 130 | 14 | 247 | 24 | NA | 500 | 0.2 | 23.41 | 1400000
2021-06-17 | 7380 | 7.38 | 7.22 | 7.54 | 135 | 15 | 258 | 21 | NA | 400 | 0.3 | 22.18 | 1300000
2021-06-18 | 7460 | 7.46 | 7.14 | 7.34 | 140 | 13 | 265 | 23 | NA | 500 | 0.2 | 21.13 | 1400000
2021-06-19 | 7230 | 7.23 | 7.26 | 7.61 | 132 | 15 | 243 | 22 | NA | 600 | 0.3 | 22.4 | 1200000
2021-06-20 | 7260 | 7.26 | 7.3 | 7.63 | 136 | 14 | 256 | 24 | NA | 400 | 0.2 | 20.96 | 1300000
2021-06-21 | 7490 | 7.49 | 7.19 | 7.46 | 140 | 15 | 262 | 21 | NA | 500 | 0.3 | 21.85 | 1600000
2021-06-22 | 7050 | 7.05 | 7.12 | 7.32 | 145 | 13 | 249 | 23 | NA | 450 | 0.3 | 23.31 | 1400000
2021-06-23 | 7310 | 7.31 | 7.21 | 7.44 | 142 | 14 | 263 | 22 | NA | 600 | 0.2 | 22.46 | 1300000
2021-06-24 | 7730 | 7.73 | 7.15 | 7.52 | 137 | 15 | 271 | 20 | NA | 500 | 0.2 | 21.73 | 1600000
2021-06-25 | 7690 | 7.69 | 7.29 | 7.64 | 140 | 14 | 259 | 23 | NA | 400 | 0.3 | 20.78 | 1400000
2021-06-26 | 7250 | 7.25 | 7.18 | 7.49 | 135 | 16 | 246 | 21 | NA | 500 | 0.3 | 23.24 | 1300000
2021-06-27 | 7320 | 7.32 | 7.24 | 7.55 | 130 | 13 | 255 | 24 | NA | 400 | 0.2 | 22.32 | 1200000
2021-06-28 | 7410 | 7.41 | 7.1 | 7.37 | 132 | 15 | 241 | 22 | NA | 500 | 0.3 | 21.64 | 1400000
2021-06-29 | 7460 | 7.46 | 7.21 | 7.45 | 140 | 14 | 257 | 20 | NA | 600 | 0.2 | 23.16 | 1300000
2021-06-30 | 7590 | 7.59 | 7.31 | 7.54 | 138 | 15 | 262 | 23 | NA | 450 | 0.2 | 20.84 | 1600000
Average | 7506 | 7.506 | 7.2067 | 7.4937 | 138.1667 | 14.2333 | 257.4333 | 22.0333 | NA | 490 | 0.24333 | 22.244 | 1436666.6667
225.18
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 7970 | 7.97 | 7.33 | 7.7 | 150 | 16 | 276 | 24 |  | 600 | 0.3 | 24.17 | 1700000
Min | 7050 | 7.05 | 7.1 | 7.31 | 130 | 13 | 241 | 20 |  | 400 | 0.2 | 20.78 | 1200000