## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-03-01 | 55870 | 55.87 | 7.32 | 7.88 | 150 | 17 | 270 | 22 | NA | 800 | 0.4 | 22.7 | 1700000
2021-03-02 | 54370 | 54.37 | 7.24 | 7.82 | 130 | 19 | 260 | 24 | NA | 500 | 0.6 | 21.54 | 1400000
2021-03-03 | 51840 | 51.84 | 7.2 | 7.63 | 140 | 14 | 256 | 26 | NA | 600 | 0.4 | 26.93 | 1200000
2021-03-04 | 62950 | 62.95 | 7.39 | 7.84 | 135 | 12 | 218 | 20 | NA | 500 | 0.5 | 22.17 | 1400000
2021-03-05 | 64160 | 64.16 | 7.18 | 7.67 | 145 | 14 | 240 | 24 | NA | 400 | 0.6 | 24.04 | 1300000
2021-03-06 | 62520 | 62.52 | 7.21 | 7.87 | 140 | 17 | 270 | 20 | NA | 700 | 0.4 | 20.1 | 1400000
2021-03-07 | 60870 | 60.87 | 7.24 | 7.8 | 145 | 18 | 280 | 28 | NA | 600 | 0.5 | 21.43 | 1200000
2021-03-08 | 63440 | 63.44 | 7.26 | 7.89 | 130 | 17 | 236 | 26 | NA | 700 | 0.4 | 22.8 | 1400000
2021-03-09 | 64200 | 64.2 | 7.29 | 7.74 | 135 | 15 | 232 | 20 | NA | 500 | 0.4 | 26.29 | 1200000
2021-03-10 | 61120 | 61.12 | 7.32 | 7.72 | 140 | 12 | 240 | 26 | NA | 400 | 0.5 | 22.8 | 1300000
2021-03-11 | 60580 | 60.58 | 7.19 | 7.64 | 145 | 16 | 224 | 28 | NA | 500 | 0.4 | 20.03 | 1400000
2021-03-12 | 60350 | 60.35 | 7.24 | 7.59 | 160 | 14 | 296 | 24 | NA | 600 | 0.4 | 20.03 | 1300000
2021-03-13 | 61720 | 61.72 | 7.27 | 7.72 | 130 | 12 | 230 | 28 | NA | 500 | 0.4 | 22.5 | 1400000
2021-03-14 | 65460 | 65.46 | 7.34 | 7.68 | 155 | 17 | 260 | 22 | NA | 700 | 0.5 | 25.4 | 1200000
2021-03-15 | 63150 | 63.15 | 7.31 | 7.62 | 140 | 13 | 288 | 26 | NA | 400 | 0.4 | 24.13 | 1200000
2021-03-16 | 63950 | 63.95 | 7.28 | 7.7 | 150 | 17 | 256 | 22 | NA | 500 | 0.4 | 22.69 | 1400000
2021-03-17 | 64460 | 64.46 | 7.16 | 7.69 | 145 | 14 | 224 | 24 | NA | 700 | 0.4 | 22.8 | 1300000
2021-03-18 | 57880 | 57.88 | 7.17 | 7.64 | 130 | 18 | 270 | 24 | NA | 600 | 0.4 | 24.4 | 1400000
2021-03-19 | 63830 | 63.83 | 7.25 | 7.78 | 135 | 14 | 290 | 28 | NA | 500 | 0.5 | 26.47 | 1400000
2021-03-20 | 62470 | 62.47 | 7.24 | 7.78 | 140 | 19 | 280 | 26 | NA | 500 | 0.4 | 20.05 | 1200000
2021-03-21 | 61790 | 61.79 | 7.22 | 7.84 | 130 | 13 | 250 | 20 | NA | 700 | 0.4 | 24.88 | 1700000
2021-03-22 | 61730 | 61.73 | 7.14 | 7.69 | 140 | 15 | 256 | 26 | NA | 600 | 0.4 | 22.17 | 1400000
2021-03-23 | 60760 | 60.76 | 7.19 | 7.84 | 150 | 16 | 224 | 28 | NA | 500 | 0.5 | 26.4 | 1200000
2021-03-24 | 61340 | 61.34 | 7.21 | 7.89 | 145 | 16 | 270 | 24 | NA | 600 | 0.5 | 24.4 | 1200000
2021-03-25 | 62310 | 62.31 | 7.31 | 7.64 | 130 | 15 | 228 | 24 | NA | 500 | 0.4 | 20.77 | 1400000
2021-03-26 | 64330 | 64.33 | 7.22 | 7.72 | 135 | 12 | 250 | 22 | NA | 500 | 0.4 | 21.38 | 1400000
2021-03-27 | 62800 | 62.8 | 7.16 | 7.84 | 140 | 14 | 252 | 24 | NA | 600 | 0.4 | 22.17 | 1200000
2021-03-28 | 66000 | 66 | 7.17 | 7.75 | 130 | 16 | 224 | 22 | NA | 500 | 0.4 | 24.4 | 1400000
2021-03-29 | 73000 | 73 | 7.14 | 7.56 | 145 | 15 | 256 | 20 | NA | 600 | 0.5 | 22.4 | 1400000
2021-03-30 | 63680 | 63.68 | 7.22 | 7.84 | 135 | 16 | 236 | 24 | NA | 700 | 0.4 | 22.8 | 1300000
2021-03-31 | 63160 | 63.16 | 7.29 | 7.8 | 140 | 18 | 232 | 22 | NA | 500 | 0.4 | 22.69 | 1700000
Average | 62131.9355 | 62.1319 | 7.2377 | 7.7455 | 140 | 15.3226 | 251.5484 | 24 | NA | 564.5161 | 0.43871 | 23.0245 | 1354838.7097
1926.09
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 73000 | 73 | 7.39 | 7.89 | 160 | 19 | 296 | 28 |  | 800 | 0.6 | 26.93 | 1700000
Min | 51840 | 51.84 | 7.14 | 7.56 | 130 | 12 | 218 | 20 |  | 400 | 0.4 | 20.03 | 1200000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-03-01 | 38930 | 38.93 | 7.55 | 7.72 | 159 | 21 | 306 | 36 | NA | 600 | 0.4 | 25.5 | 1300000
2021-03-02 | 39710 | 39.71 | 7.45 | 7.68 | 153 | 23 | 312 | 38 | NA | 500 | 0.5 | 27.5 | 1400000
2021-03-03 | 39010 | 39.01 | 7.48 | 7.58 | 156 | 24 | 316 | 40 | NA | 600 | 0.4 | 25.9 | 1100000
2021-03-04 | 39680 | 39.68 | 7.52 | 7.71 | 160 | 22 | 318 | 39 | NA | 700 | 0.3 | 22.1 | 1400000
2021-03-05 | 37860 | 37.86 | 7.53 | 7.65 | 163 | 25 | 315 | 41 | NA | 500 | 0.5 | 23.1 | 1300000
2021-03-06 | 34450 | 34.45 | 7.55 | 7.72 | 166 | 23 | 308 | 38 | NA | 700 | 0.3 | 24.4 | 1700000
2021-03-07 | 38730 | 38.73 | 7.46 | 7.59 | 159 | 20 | 303 | 36 | NA | 600 | 0.4 | 23.8 | 1400000
2021-03-08 | 39320 | 39.32 | 7.48 | 7.62 | 156 | 22 | 307 | 35 | NA | 500 | 0.5 | 22.2 | 1100000
2021-03-09 | 37520 | 37.52 | 7.51 | 7.58 | 159 | 21 | 314 | 37 | NA | 600 | 0.4 | 25.7 | 1300000
2021-03-10 | 35730 | 35.73 | 7.45 | 7.55 | 163 | 19 | 312 | 39 | NA | 700 | 0.3 | 24.3 | 1400000
2021-03-11 | 35390 | 35.39 | 7.47 | 7.61 | 163 | 21 | 315 | 41 | NA | 600 | 0.4 | 26.9 | 1700000
2021-03-12 | 32380 | 32.38 | 7.42 | 7.68 | 160 | 23 | 311 | 42 | NA | 500 | 0.5 | 25.7 | 1100000
2021-03-13 | 33310 | 33.31 | 7.38 | 7.65 | 156 | 22 | 316 | 40 | NA | 600 | 0.4 | 24.6 | 1700000
2021-03-14 | 39780 | 39.78 | 7.45 | 7.56 | 153 | 20 | 322 | 38 | NA | 500 | 0.5 | 28.4 | 1400000
2021-03-15 | 37890 | 37.89 | 7.49 | 7.55 | 159 | 22 | 318 | 41 | NA | 700 | 0.3 | 26.2 | 1300000
2021-03-16 | 37150 | 37.15 | 7.51 | 7.62 | 156 | 24 | 315 | 39 | NA | 600 | 0.4 | 24.9 | 1100000
2021-03-17 | 35100 | 35.1 | 7.55 | 7.71 | 153 | 21 | 311 | 37 | NA | 400 | 0.5 | 27.3 | 1300000
2021-03-18 | 33640 | 33.64 | 7.47 | 7.65 | 159 | 23 | 309 | 35 | NA | 600 | 0.4 | 25.2 | 1700000
2021-03-19 | 33380 | 33.38 | 7.45 | 7.72 | 163 | 25 | 305 | 38 | NA | 700 | 0.3 | 24.9 | 1400000
2021-03-20 | 36390 | 36.39 | 7.38 | 7.55 | 166 | 22 | 302 | 35 | NA | 600 | 0.4 | 22.2 | 1700000
2021-03-21 | 35320 | 35.32 | 7.35 | 7.48 | 160 | 20 | 312 | 33 | NA | 500 | 0.5 | 23.8 | 1100000
2021-03-22 | 33010 | 33.01 | 7.41 | 7.51 | 156 | 21 | 316 | 36 | NA | 600 | 0.4 | 24.3 | 1300000
2021-03-23 | 34640 | 34.64 | 7.38 | 7.56 | 159 | 19 | 311 | 38 | NA | 700 | 0.3 | 22.1 | 1400000
2021-03-24 | 31760 | 31.76 | 7.45 | 7.62 | 156 | 22 | 318 | 40 | NA | 500 | 0.5 | 21.9 | 1100000
2021-03-25 | 31490 | 31.49 | 7.41 | 7.65 | 153 | 24 | 322 | 42 | NA | 600 | 0.4 | 24.6 | 1700000
2021-03-26 | 31940 | 31.94 | 7.35 | 7.61 | 159 | 25 | 328 | 39 | NA | 500 | 0.5 | 21.8 | 1100000
2021-03-27 | 36600 | 36.6 | 7.39 | 7.55 | 163 | 23 | 319 | 41 | NA | 700 | 0.3 | 23.8 | 1300000
2021-03-28 | 37920 | 37.92 | 7.42 | 7.52 | 159 | 24 | 311 | 38 | NA | 600 | 0.4 | 24.5 | 1400000
2021-03-29 | 42760 | 42.76 | 7.36 | 7.63 | 156 | 26 | 307 | 40 | NA | 500 | 0.5 | 22.2 | 1100000
2021-03-30 | 42950 | 42.95 | 7.35 | 7.56 | 163 | 27 | 312 | 42 | NA | 700 | 0.3 | 24.1 | 1700000
2021-03-31 | 38180 | 38.18 | 7.41 | 7.59 | 166 | 24 | 314 | 39 | NA | 600 | 0.4 | 25.9 | 1300000
Average | 36513.5484 | 36.5135 | 7.4461 | 7.6123 | 159.0968 | 22.5161 | 313.0645 | 38.4839 | NA | 590.3226 | 0.40645 | 24.5097 | 1364516.129
1131.92
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 42950 | 42.95 | 7.55 | 7.72 | 166 | 27 | 328 | 42 |  | 700 | 0.5 | 28.4 | 1700000
Min | 31490 | 31.49 | 7.35 | 7.48 | 153 | 19 | 302 | 33 |  | 400 | 0.3 | 21.8 | 1100000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-03-01 | 24810 | 24.81 | 7.15 | 7.7 | 148 | 14 | 260 | 22 | NA | 700 | 0.3 | 22.93 | 1700000
2021-03-02 | 24660 | 24.66 | 7.18 | 7.55 | 138 | 13 | 277 | 20 | NA | 500 | 0.4 | 23.82 | 1400000
2021-03-03 | 25570 | 25.57 | 7.1 | 7.6 | 140 | 15 | 270 | 23 | NA | 600 | 0.3 | 25.04 | 1300000
2021-03-04 | 23800 | 23.8 | 7.25 | 7.7 | 132 | 13 | 256 | 19 | NA | 500 | 0.3 | 24.48 | 1400000
2021-03-05 | 25180 | 25.18 | 7.3 | 7.84 | 142 | 14 | 269 | 22 | NA | 400 | 0.3 | 25.14 | 1700000
2021-03-06 | 25030 | 25.03 | 7.25 | 7.7 | 130 | 15 | 272 | 20 | NA | 600 | 0.4 | 26.24 | 1200000
2021-03-07 | 26390 | 26.39 | 7.11 | 7.84 | 136 | 16 | 260 | 21 | NA | 500 | 0.3 | 23.97 | 1300000
2021-03-08 | 24810 | 24.81 | 7.18 | 7.64 | 145 | 13 | 280 | 24 | NA | 700 | 0.2 | 21.5 | 1700000
2021-03-09 | 25050 | 25.05 | 7.12 | 7.59 | 148 | 15 | 263 | 20 | NA | 500 | 0.4 | 22.7 | 1400000
2021-03-10 | 25050 | 25.05 | 7.24 | 7.64 | 130 | 12 | 250 | 25 | NA | 400 | 0.3 | 24.67 | 1700000
2021-03-11 | 25710 | 25.71 | 7.12 | 7.52 | 135 | 14 | 273 | 20 | NA | 700 | 0.4 | 23.32 | 1400000
2021-03-12 | 24910 | 24.91 | 7.17 | 7.88 | 132 | 15 | 260 | 22 | NA | 500 | 0.3 | 25.58 | 1300000
2021-03-13 | 24710 | 24.71 | 7.15 | 7.54 | 140 | 14 | 283 | 18 | NA | 600 | 0.3 | 26.01 | 1700000
2021-03-14 | 26360 | 26.36 | 7.08 | 7.74 | 130 | 13 | 258 | 23 | NA | 500 | 0.3 | 26.82 | 1400000
2021-03-15 | 26090 | 26.09 | 7.22 | 7.7 | 152 | 16 | 270 | 20 | NA | 600 | 0.4 | 22.59 | 1200000
2021-03-16 | 25700 | 25.7 | 7.37 | 7.89 | 138 | 13 | 250 | 24 | NA | 400 | 0.5 | 25.69 | 1700000
2021-03-17 | 24180 | 24.18 | 7.14 | 7.73 | 130 | 14 | 270 | 19 | NA | 500 | 0.3 | 25.58 | 1300000
2021-03-18 | 24020 | 24.02 | 7.15 | 7.8 | 135 | 16 | 265 | 21 | NA | 700 | 0.3 | 24.64 | 1700000
2021-03-19 | 25480 | 25.48 | 7.1 | 7.59 | 145 | 14 | 250 | 20 | NA | 400 | 0.4 | 24.44 | 1300000
2021-03-20 | 24190 | 24.19 | 7.05 | 7.82 | 136 | 15 | 278 | 23 | NA | 600 | 0.3 | 24.25 | 1700000
2021-03-21 | 25570 | 25.57 | 7.18 | 7.54 | 138 | 13 | 253 | 19 | NA | 500 | 0.5 | 25.15 | 1400000
2021-03-22 | 24660 | 24.66 | 7.24 | 7.64 | 140 | 16 | 264 | 21 | NA | 700 | 0.3 | 24.18 | 1600000
2021-03-23 | 25280 | 25.28 | 7.14 | 7.49 | 138 | 14 | 274 | 23 | NA | 400 | 0.5 | 23.58 | 1300000
2021-03-24 | 22900 | 22.9 | 7.25 | 7.54 | 130 | 13 | 273 | 24 | NA | 600 | 0.4 | 24.48 | 1500000
2021-03-25 | 25700 | 25.7 | 7.13 | 7.61 | 135 | 15 | 286 | 21 | NA | 500 | 0.3 | 26.56 | 1400000
2021-03-26 | 23800 | 23.8 | 7.08 | 7.54 | 140 | 14 | 284 | 20 | NA | 700 | 0.4 | 26.03 | 1700000
2021-03-27 | 24560 | 24.56 | 7.11 | 7.63 | 135 | 16 | 278 | 22 | NA | 600 | 0.5 | 25.73 | 1200000
2021-03-28 | 26310 | 26.31 | 7.15 | 7.71 | 142 | 13 | 277 | 19 | NA | 500 | 0.4 | 24.56 | 1300000
2021-03-29 | 28560 | 28.56 | 7.04 | 7.54 | 145 | 15 | 283 | 21 | NA | 400 | 0.4 | 24.25 | 1700000
2021-03-30 | 26230 | 26.23 | 7.25 | 7.64 | 138 | 13 | 260 | 20 | NA | 500 | 0.5 | 23.58 | 1400000
2021-03-31 | 26160 | 26.16 | 7.13 | 7.61 | 135 | 12 | 274 | 23 | NA | 400 | 0.5 | 25.14 | 1700000
Average | 25207.4194 | 25.2074 | 7.1655 | 7.6613 | 138 | 14.129 | 268.3871 | 21.2581 | NA | 538.7097 | 0.36774 | 24.6016 | 1474193.5484
781.43
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 28560 | 28.56 | 7.37 | 7.89 | 152 | 16 | 286 | 25 |  | 700 | 0.5 | 26.82 | 1700000
Min | 22900 | 22.9 | 7.04 | 7.49 | 130 | 12 | 250 | 18 |  | 400 | 0.2 | 21.5 | 1200000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-03-01 | 7444 | 7.444 | 7.12 | 7.32 | 130 | 14 | 266 | 22 | NA | 400 | 0.2 | 22.42 | 1200000
2021-03-02 | 7685 | 7.685 | 7.19 | 7.48 | 135 | 15 | 273 | 20 | NA | 500 | 0.4 | 21.67 | 1400000
2021-03-03 | 7949 | 7.949 | 7.26 | 7.54 | 132 | 14 | 276 | 23 | NA | 450 | 0.2 | 23.21 | 1700000
2021-03-04 | 7625 | 7.625 | 6.98 | 7.67 | 130 | 16 | 259 | 21 | NA | 600 | 0.3 | 22.49 | 1300000
2021-03-05 | 7881 | 7.881 | 7.14 | 7.49 | 135 | 13 | 264 | 24 | NA | 400 | 0.5 | 20.92 | 1400000
2021-03-06 | 7615 | 7.615 | 7.22 | 7.32 | 140 | 15 | 256 | 22 | NA | 500 | 0.2 | 21.44 | 1300000
2021-03-07 | 7386 | 7.386 | 7.15 | 7.43 | 128 | 14 | 249 | 20 | NA | 400 | 0.4 | 22.25 | 1200000
2021-03-08 | 7637 | 7.637 | 7.26 | 7.69 | 135 | 16 | 261 | 23 | NA | 500 | 0.3 | 20.74 | 1100000
2021-03-09 | 6904 | 6.904 | 7.16 | 7.54 | 132 | 14 | 246 | 21 | NA | 450 | 0.2 | 23.12 | 1400000
2021-03-10 | 7473 | 7.473 | 7.34 | 7.63 | 136 | 15 | 258 | 24 | NA | 500 | 0.5 | 21.49 | 1200000
2021-03-11 | 7550 | 7.55 | 7.16 | 7.47 | 140 | 16 | 264 | 22 | NA | 400 | 0.3 | 22.27 | 1600000
2021-03-12 | 7359 | 7.359 | 7.22 | 7.52 | 132 | 14 | 255 | 20 | NA | 500 | 0.4 | 20.92 | 1300000
2021-03-13 | 7818 | 7.818 | 7.31 | 7.69 | 140 | 15 | 270 | 23 | NA | 400 | 0.3 | 21.63 | 1400000
2021-03-14 | 7923 | 7.923 | 7.27 | 7.78 | 135 | 14 | 262 | 21 | NA | 500 | 0.4 | 22.42 | 1600000
2021-03-15 | 7230 | 7.23 | 7.18 | 7.59 | 142 | 16 | 257 | 24 | NA | 450 | 0.2 | 21.12 | 1200000
2021-03-16 | 7922 | 7.922 | 7.33 | 7.54 | 137 | 14 | 261 | 22 | NA | 400 | 0.3 | 23.41 | 1400000
2021-03-17 | 7759 | 7.759 | 7.29 | 7.61 | 130 | 16 | 268 | 20 | NA | 500 | 0.5 | 22.18 | 1600000
2021-03-18 | 7318 | 7.318 | 7.17 | 7.46 | 135 | 14 | 259 | 23 | NA | 450 | 0.5 | 23.16 | 1400000
2021-03-19 | 7949 | 7.949 | 7.26 | 7.66 | 140 | 13 | 272 | 21 | NA | 400 | 0.4 | 21.49 | 1600000
2021-03-20 | 6724 | 6.724 | 7.12 | 7.39 | 136 | 15 | 246 | 23 | NA | 500 | 0.5 | 22.28 | 1300000
2021-03-21 | 7922 | 7.922 | 7.29 | 7.49 | 142 | 14 | 258 | 22 | NA | 400 | 0.5 | 20.67 | 1200000
2021-03-22 | 7867 | 7.867 | 7.14 | 7.31 | 135 | 16 | 264 | 24 | NA | 500 | 0.5 | 21.51 | 1400000
2021-03-23 | 7796 | 7.796 | 7.22 | 7.42 | 140 | 14 | 248 | 23 | NA | 600 | 0.5 | 22.16 | 1600000
2021-03-24 | 7248 | 7.248 | 7.17 | 7.37 | 137 | 13 | 253 | 21 | NA | 400 | 0.5 | 23.38 | 1300000
2021-03-25 | 7916 | 7.916 | 7.21 | 7.56 | 145 | 15 | 267 | 22 | NA | 600 | 0.5 | 20.64 | 1400000
2021-03-26 | 7660 | 7.66 | 7.32 | 7.49 | 130 | 14 | 245 | 20 | NA | 450 | 0.5 | 21.33 | 1200000
2021-03-27 | 7755 | 7.755 | 7.28 | 7.46 | 135 | 16 | 252 | 22 | NA | 500 | 0.4 | 22.19 | 1300000
2021-03-28 | 7983 | 7.983 | 7.14 | 7.34 | 140 | 14 | 261 | 21 | NA | 400 | 0.5 | 23.41 | 1600000
2021-03-29 | 7761 | 7.761 | 7.26 | 7.51 | 137 | 15 | 268 | 24 | NA | 500 | 0.5 | 21.14 | 1400000
2021-03-30 | 7591 | 7.591 | 7.15 | 7.39 | 142 | 14 | 255 | 22 | NA | 400 | 0.4 | 22.24 | 1300000
2021-03-31 | 7633 | 7.633 | 7.24 | 7.44 | 145 | 16 | 270 | 20 | NA | 450 | 0.5 | 20.36 | 1400000
Average | 7622.0323 | 7.622 | 7.2113 | 7.5032 | 136.3871 | 14.6452 | 260.0968 | 21.9355 | NA | 464.5161 | 0.39677 | 21.9245 | 1377419.3548
236.283
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 7983 | 7.983 | 7.34 | 7.78 | 145 | 16 | 276 | 24 |  | 600 | 0.5 | 23.41 | 1700000
Min | 6724 | 6.724 | 6.98 | 7.31 | 128 | 13 | 245 | 20 |  | 400 | 0.2 | 20.36 | 1100000