## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-05-01 | 60770 | 60.77 | 7.18 | 7.68 | 140 | 15 | 264 | 24 | NA | 600 | 0.2 | 21.94 | 1400000
2021-05-02 | 60660 | 60.66 | 7.26 | 7.78 | 150 | 18 | 248 | 28 | NA | 500 | 0.3 | 23.14 | 1200000
2021-05-03 | 48800 | 48.8 | 7.16 | 7.86 | 130 | 16 | 256 | 26 | NA | 700 | 0.2 | 24.8 | 1300000 | Manual screen at Ghagharnalla damaged due to which overflow occurred at MPS.
2021-05-04 | 56080 | 56.08 | 7.32 | 7.84 | 145 | 14 | 240 | 28 | NA | 600 | 0.3 | 24.01 | 1200000
2021-05-05 | 62930 | 62.93 | 7.16 | 7.69 | 150 | 13 | 270 | 26 | NA | 500 | 0.2 | 20.97 | 1400000
2021-05-06 | 58080 | 58.08 | 7.22 | 7.74 | 140 | 15 | 250 | 28 | NA | 700 | 0.3 | 25.4 | 1300000
2021-05-07 | 58950 | 58.95 | 7.27 | 7.67 | 130 | 16 | 272 | 24 | NA | 600 | 0.2 | 21.61 | 1400000
2021-05-08 | 56810 | 56.81 | 7.15 | 7.84 | 150 | 15 | 246 | 28 | NA | 700 | 0.2 | 23.48 | 1300000
2021-05-09 | 54490 | 54.49 | 7.16 | 7.68 | 135 | 16 | 216 | 28 | NA | 500 | 0.3 | 23.21 | 1400000
2021-05-10 | 54250 | 54.25 | 7.14 | 7.72 | 150 | 18 | 280 | 26 | NA | 600 | 0.3 | 23.86 | 1200000
2021-05-11 | 51500 | 51.5 | 7.18 | 7.84 | 130 | 14 | 260 | 24 | NA | 500 | 0.2 | 23.22 | 1700000
2021-05-12 | 56230 | 56.23 | 7.22 | 7.6 | 140 | 16 | 266 | 24 | NA | 600 | 0.3 | 24.87 | 1400000
2021-05-13 | 62210 | 62.21 | 7.2 | 7.81 | 150 | 14 | 268 | 22 | NA | 500 | 0.3 | 22.61 | 1400000
2021-05-14 | 60840 | 60.84 | 7.14 | 7.62 | 145 | 18 | 248 | 28 | NA | 700 | 0.2 | 22.66 | 1300000
2021-05-15 | 63400 | 63.4 | 7.19 | 7.74 | 130 | 14 | 250 | 26 | NA | 500 | 0.3 | 23.12 | 1700000
2021-05-16 | 57190 | 57.19 | 7.22 | 7.89 | 140 | 16 | 264 | 28 | NA | 700 | 0.3 | 24.11 | 1400000
2021-05-17 | 57080 | 57.08 | 7.26 | 7.64 | 150 | 17 | 280 | 24 | NA | 500 | 0.2 | 23.62 | 1200000
2021-05-18 | 56830 | 56.83 | 7.17 | 7.52 | 140 | 14 | 276 | 22 | NA | 600 | 0.3 | 22.67 | 1400000
2021-05-19 | 64120 | 64.12 | 7.18 | 7.64 | 145 | 16 | 252 | 24 | NA | 700 | 0.2 | 22.6 | 1700000
2021-05-20 | 41873 | 41.873 | 7.32 | 7.64 | 135 | 16 | 260 | 24 | NA | 500 | 0.2 | 22.65 | 1400000 | Retaining wall for the Nalla at Ghagharnalla MPS is damaged at 16:00 due to heavy rain.
2021-05-21 | 36500 | 36.5 | 7.18 | 7.56 | 150 | 18 | 228 | 26 | NA | 700 | 0.2 | 21.67 | 1400000 | Retaining wall for the Nalla at Ghagharnalla MPS is damaged due to heavy rain.
2021-05-22 | 9940 | 9.94 | 7.25 | 7.64 | 135 | 15 | 264 | 28 | NA | 600 | 0.3 | 22.69 | 1200000 | Shutdown of Ghagharnalla MPS was taken for repairing of NRV and rectification of leakage from ARVs in rising main from Ghagharnalla MPS to Numayadahi STP.
2021-05-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 20.4 | 0
2021-05-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 22.55 | 0
2021-05-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 22.6 | 0
2021-05-26 | 15361 | 15.361 | 7.17 | 7.64 | 145 | 15 | 266 | 28 | NA | 600 | 0.3 | 23.12 | 1400000 | Repairing of retaining wall for the Nalla at Ghagharnalla MPS is completed.
2021-05-27 | 54580 | 54.58 | 7.21 | 7.84 | 150 | 14 | 252 | 24 | NA | 500 | 0.2 | 22.73 | 1400000
2021-05-28 | 60000 | 60 | 7.28 | 7.94 | 135 | 16 | 238 | 26 | NA | 700 | 0.2 | 23.25 | 1200000
2021-05-29 | 59800 | 59.8 | 7.27 | 7.84 | 140 | 15 | 296 | 28 | NA | 500 | 0.3 | 22.08 | 1300000
2021-05-30 | 58741 | 58.741 | 7.34 | 7.72 | 130 | 17 | 264 | 24 | NA | 600 | 0.2 | 22.65 | 1400000
2021-05-31 | 59480 | 59.48 | 7.22 | 7.8 | 145 | 14 | 252 | 26 | NA | 500 | 0.3 | 23.62 | 1200000
Average | 53481.9643 | 53.482 | 7.215 | 7.7293 | 141.25 | 15.5357 | 258.0714 | 25.7857 | NA | 589.2857 | 0.25 | 22.9648 | 1364285.7143
SUM | 1497495 | 1497.495 | 202.02 | 216.42 | 3955 | 435 | 7226 | 722 |  | 16500 | 7 | 711.91 | 38200000
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 64120 | 64.12 | 7.34 | 7.94 | 150 | 18 | 296 | 28 |  | 700 | 0.3 | 25.4 | 1700000
Min | 9940 | 9.94 | 7.14 | 7.52 | 130 | 13 | 216 | 22 |  | 500 | 0.2 | 20.4 | 1200000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-05-01 | 27180 | 27.18 | 7.37 | 7.52 | 156 | 18 | 315 | 36 | NA | 700 | 0.2 | 25.4 | 1400000
2021-05-02 | 31130 | 31.13 | 7.42 | 7.55 | 153 | 20 | 311 | 38 | NA | 800 | 0.2 | 26.9 | 1300000
2021-05-03 | 31830 | 31.83 | 7.35 | 7.63 | 163 | 22 | 302 | 35 | NA | 700 | 0.2 | 23.1 | 1100000
2021-05-04 | 30340 | 30.34 | 7.28 | 7.68 | 169 | 20 | 310 | 37 | NA | 800 | 0.2 | 22.8 | 1700000
2021-05-05 | 29760 | 29.76 | 7.4 | 7.57 | 159 | 21 | 318 | 39 | NA | 600 | 0.2 | 23.3 | 1600000
2021-05-06 | 28780 | 28.78 | 7.44 | 7.65 | 156 | 23 | 325 | 36 | NA | 700 | 0.2 | 24.5 | 1300000
2021-05-07 | 26830 | 26.83 | 7.38 | 7.62 | 163 | 24 | 316 | 38 | NA | 800 | 0.2 | 22.2 | 1400000
2021-05-08 | 27290 | 27.29 | 7.28 | 7.57 | 169 | 22 | 308 | 40 | NA | 700 | 0.2 | 25.9 | 1100000
2021-05-09 | 33610 | 33.61 | 7.33 | 7.54 | 159 | 21 | 299 | 38 | NA | 600 | 0.2 | 23.8 | 1300000
2021-05-10 | 26470 | 26.47 | 7.26 | 7.44 | 153 | 18 | 306 | 36 | NA | 700 | 0.2 | 26.9 | 1700000
2021-05-11 | 27170 | 27.17 | 7.35 | 7.52 | 159 | 16 | 309 | 38 | NA | 800 | 0.2 | 23.7 | 1400000
2021-05-12 | 26670 | 26.67 | 7.44 | 7.49 | 156 | 18 | 314 | 34 | NA | 700 | 0.2 | 24.4 | 1300000
2021-05-13 | 24940 | 24.94 | 7.47 | 7.58 | 163 | 20 | 325 | 35 | NA | 500 | 0.3 | 25.7 | 1100000
2021-05-14 | 26500 | 26.5 | 7.41 | 7.65 | 153 | 22 | 318 | 33 | NA | 800 | 0.2 | 23.8 | 1700000
2021-05-15 | 26640 | 26.64 | 7.38 | 7.55 | 159 | 19 | 312 | 35 | NA | 700 | 0.2 | 21.2 | 1300000
2021-05-16 | 25240 | 25.24 | 7.48 | 7.62 | 156 | 16 | 305 | 37 | NA | 600 | 0.3 | 23.1 | 1400000
2021-05-17 | 24140 | 24.14 | 7.35 | 7.71 | 163 | 18 | 309 | 39 | NA | 700 | 0.2 | 21.8 | 1100000
2021-05-18 | 30720 | 30.72 | 7.39 | 7.68 | 169 | 20 | 314 | 36 | NA | 800 | 0.2 | 23.3 | 1700000
2021-05-19 | 32140 | 32.14 | 7.32 | 7.53 | 173 | 17 | 319 | 35 | NA | 600 | 0.2 | 25.1 | 1300000
2021-05-20 | 25020 | 25.02 | 7.38 | 7.44 | 166 | 16 | 316 | 37 | NA | 500 | 0.2 | 24.6 | 1400000
2021-05-21 | 25380 | 25.38 | 7.34 | 7.51 | 163 | 18 | 308 | 35 | NA | 700 | 0.2 | 27.4 | 1300000
2021-05-22 | 23070 | 23.07 | 7.44 | 7.55 | 176 | 20 | 312 | 30 | NA | 800 | 0.2 | 25.8 | 1100000
2021-05-23 | 29430 | 29.43 | 7.29 | 7.62 | 169 | 19 | 325 | 34 | NA | 600 | 0.2 | 24.9 | 1600000
2021-05-24 | 30040 | 30.04 | 7.35 | 7.45 | 156 | 17 | 335 | 35 | NA | 800 | 0.2 | 22.2 | 1400000
2021-05-25 | 29660 | 29.66 | 7.44 | 7.56 | 153 | 20 | 322 | 37 | NA | 700 | 0.2 | 25.5 | 1300000
2021-05-26 | 30990 | 30.99 | 7.48 | 7.62 | 159 | 22 | 316 | 33 | NA | 500 | 0.3 | 26.9 | 1700000
2021-05-27 | 28530 | 28.53 | 7.36 | 7.52 | 163 | 20 | 310 | 35 | NA | 600 | 0.2 | 23.6 | 1400000
2021-05-28 | 30030 | 30.03 | 7.42 | 7.58 | 173 | 23 | 302 | 37 | NA | 800 | 0.2 | 22.1 | 1100000
2021-05-29 | 27380 | 27.38 | 7.38 | 7.45 | 166 | 21 | 315 | 30 | NA | 700 | 0.2 | 24.4 | 1300000
2021-05-30 | 27940 | 27.94 | 7.44 | 7.59 | 163 | 22 | 328 | 32 | NA | 600 | 0.2 | 23.5 | 1400000
2021-05-31 | 26830 | 26.83 | 7.48 | 7.65 | 153 | 20 | 335 | 35 | NA | 800 | 0.2 | 22.8 | 1700000
Average | 28118.7097 | 28.1187 | 7.3839 | 7.569 | 161.6452 | 19.7742 | 314.8065 | 35.6452 | NA | 690.3226 | 0.20968 | 24.2129 | 1383870.9677
SUM | 871680 | 871.68 | 228.9 | 234.64 | 5011 | 613 | 9759 | 1105 |  | 21400 | 6.5 | 750.6 | 42900000
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 33610 | 33.61 | 7.48 | 7.71 | 176 | 24 | 335 | 40 |  | 800 | 0.3 | 27.4 | 1700000
Min | 23070 | 23.07 | 7.26 | 7.44 | 153 | 16 | 299 | 30 |  | 500 | 0.2 | 21.2 | 1100000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-05-01 | 24850 | 24.85 | 7.3 | 7.69 | 145 | 13 | 278 | 18 | NA | 400 | 0.2 | 26.14 | 1200000
2021-05-02 | 25480 | 25.48 | 7.21 | 7.73 | 148 | 14 | 247 | 20 | NA | 600 | 0.2 | 24.18 | 1400000
2021-05-03 | 24970 | 24.97 | 7.34 | 7.64 | 152 | 15 | 268 | 23 | NA | 700 | 0.2 | 25.76 | 1300000
2021-05-04 | 25880 | 25.88 | 7.25 | 7.7 | 145 | 13 | 293 | 21 | NA | 500 | 0.2 | 27.24 | 1700000
2021-05-05 | 25270 | 25.27 | 7.18 | 7.78 | 130 | 14 | 278 | 24 | NA | 600 | 0.2 | 26.77 | 1400000
2021-05-06 | 24750 | 24.75 | 7.1 | 7.83 | 148 | 12 | 300 | 20 | NA | 700 | 0.3 | 25.41 | 1300000
2021-05-07 | 25380 | 25.38 | 7.3 | 7.69 | 156 | 14 | 288 | 22 | NA | 600 | 0.2 | 26.6 | 1700000
2021-05-08 | 25660 | 25.66 | 7.33 | 7.78 | 138 | 13 | 264 | 19 | NA | 500 | 0.2 | 24.09 | 1400000
2021-05-09 | 27870 | 27.87 | 7.17 | 7.64 | 142 | 15 | 273 | 21 | NA | 600 | 0.2 | 25.3 | 1300000
2021-05-10 | 25690 | 25.69 | 7.11 | 7.52 | 130 | 13 | 283 | 20 | NA | 700 | 0.2 | 26.1 | 1700000
2021-05-11 | 25730 | 25.73 | 7.15 | 7.6 | 154 | 14 | 275 | 23 | NA | 600 | 0.3 | 25.78 | 1400000
2021-05-12 | 26060 | 26.06 | 7.21 | 7.68 | 150 | 15 | 256 | 18 | NA | 500 | 0.2 | 24.48 | 1300000
2021-05-13 | 25860 | 25.86 | 7.34 | 7.55 | 145 | 13 | 263 | 22 | NA | 700 | 0.2 | 25.43 | 1600000
2021-05-14 | 25660 | 25.66 | 7.24 | 7.62 | 130 | 12 | 250 | 20 | NA | 600 | 0.2 | 26.04 | 1400000
2021-05-15 | 25420 | 25.42 | 7.16 | 7.6 | 148 | 14 | 245 | 22 | NA | 500 | 0.2 | 25.32 | 1300000
2021-05-16 | 26480 | 26.48 | 7.34 | 7.73 | 142 | 12 | 288 | 21 | NA | 600 | 0.2 | 25.76 | 1700000
2021-05-17 | 25990 | 25.99 | 7.21 | 7.62 | 138 | 13 | 278 | 23 | NA | 400 | 0.2 | 26.1 | 1200000
2021-05-18 | 30650 | 30.65 | 7.3 | 7.74 | 142 | 15 | 300 | 24 | NA | 500 | 0.3 | 24.09 | 1600000
2021-05-19 | 21910 | 21.91 | 7.22 | 7.7 | 140 | 16 | 270 | 20 | NA | 600 | 0.2 | 24.56 | 1400000 | Plant is receiving less flow as retaining wall for near-by nalla is broken.
2021-05-20 | 23050 | 23.05 | 7.1 | 7.82 | 136 | 13 | 275 | 22 | NA | 700 | 0.2 | 25.3 | 1600000
2021-05-21 | 19150 | 19.15 | 7.12 | 7.72 | 130 | 12 | 283 | 21 | NA | 500 | 0.3 | 26.24 | 1300000
2021-05-22 | 19250 | 19.25 | 7.25 | 7.68 | 142 | 14 | 280 | 23 | NA | 700 | 0.2 | 24.09 | 1400000
2021-05-23 | 20160 | 20.16 | 7.18 | 7.73 | 138 | 13 | 263 | 20 | NA | 600 | 0.2 | 26.77 | 1400000
2021-05-24 | 19390 | 19.39 | 7.11 | 7.63 | 140 | 12 | 278 | 22 | NA | 400 | 0.2 | 25.73 | 1200000
2021-05-25 | 19640 | 19.64 | 7.22 | 7.55 | 136 | 15 | 263 | 24 | NA | 500 | 0.3 | 24.18 | 1700000
2021-05-26 | 18870 | 18.87 | 7.18 | 7.64 | 138 | 13 | 280 | 21 | NA | 700 | 0.3 | 23.97 | 1600000
2021-05-27 | 20250 | 20.25 | 7.24 | 7.7 | 140 | 16 | 264 | 23 | NA | 600 | 0.2 | 25.76 | 1400000
2021-05-28 | 20680 | 20.68 | 7.21 | 7.64 | 138 | 14 | 282 | 20 | NA | 500 | 0.2 | 24.24 | 1600000
2021-05-29 | 19510 | 19.51 | 7.17 | 7.72 | 130 | 13 | 234 | 23 | NA | 400 | 0.2 | 25.62 | 1400000
2021-05-30 | 20430 | 20.43 | 7.28 | 7.7 | 135 | 15 | 285 | 21 | NA | 700 | 0.2 | 26.85 | 1700000
2021-05-31 | 19670 | 19.67 | 7.1 | 7.65 | 140 | 14 | 256 | 19 | NA | 400 | 0.2 | 24.56 | 1400000
Average | 23535.8065 | 23.5358 | 7.2135 | 7.6781 | 140.8387 | 13.6774 | 272.2581 | 21.2903 | NA | 567.7419 | 0.21935 | 25.4342 | 1451612.9032
SUM | 729610 | 729.61 | 223.62 | 238.02 | 4366 | 424 | 8440 | 660 |  | 17600 | 6.8 | 788.46 | 45000000
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 30650 | 30.65 | 7.34 | 7.83 | 156 | 16 | 300 | 24 |  | 700 | 0.3 | 27.24 | 1700000
Min | 18870 | 18.87 | 7.1 | 7.52 | 130 | 12 | 234 | 18 |  | 400 | 0.2 | 23.97 | 1200000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-05-01 | 7451 | 7.451 | 7.21 | 7.41 | 145 | 13 | 260 | 23 | NA | 400 | 0.2 | 22.41 | 1600000
2021-05-02 | 7280 | 7.28 | 7.17 | 7.32 | 136 | 15 | 246 | 20 | NA | 500 | 0.2 | 21.18 | 1400000
2021-05-03 | 7262 | 7.262 | 7.28 | 7.47 | 140 | 14 | 251 | 22 | NA | 600 | 0.2 | 23.34 | 1300000
2021-05-04 | 7161 | 7.161 | 7.15 | 7.38 | 135 | 16 | 243 | 24 | NA | 400 | 0.2 | 24.29 | 1400000
2021-05-05 | 7202 | 7.202 | 7.24 | 7.49 | 138 | 13 | 256 | 21 | NA | 500 | 0.2 | 22.51 | 1600000
2021-05-06 | 7134 | 7.134 | 7.13 | 7.29 | 132 | 15 | 248 | 23 | NA | 400 | 0.2 | 21.68 | 1300000
2021-05-07 | 7174 | 7.174 | 7.22 | 7.33 | 140 | 14 | 255 | 20 | NA | 500 | 0.2 | 23.59 | 1400000
2021-05-08 | 7237 | 7.237 | 7.19 | 7.44 | 142 | 16 | 264 | 22 | NA | 600 | 0.2 | 22.37 | 1600000
2021-05-09 | 7359 | 7.359 | 7.26 | 7.52 | 145 | 13 | 271 | 24 | NA | 400 | 0.2 | 24.13 | 1700000
2021-05-10 | 7195 | 7.195 | 7.3 | 7.62 | 140 | 15 | 261 | 21 | NA | 500 | 0.2 | 23.42 | 1400000
2021-05-11 | 7205 | 7.205 | 7.14 | 7.36 | 135 | 14 | 249 | 19 | NA | 450 | 0.2 | 22.63 | 1200000
2021-05-12 | 7216 | 7.216 | 7.23 | 7.48 | 146 | 13 | 258 | 22 | NA | 600 | 0.2 | 23.52 | 1400000
2021-05-13 | 7504 | 7.504 | 7.31 | 7.65 | 138 | 15 | 265 | 20 | NA | 500 | 0.2 | 21.46 | 1600000
2021-05-14 | 7665 | 7.665 | 7.11 | 7.31 | 142 | 13 | 274 | 22 | NA | 400 | 0.2 | 22.58 | 1700000
2021-05-15 | 7650 | 7.65 | 7.18 | 7.35 | 135 | 14 | 268 | 20 | NA | 500 | 0.2 | 21.97 | 1300000
2021-05-16 | 7980 | 7.98 | 7.27 | 7.49 | 140 | 13 | 252 | 23 | NA | 600 | 0.2 | 23.19 | 1400000
2021-05-17 | 7160 | 7.16 | 7.15 | 7.27 | 136 | 15 | 242 | 21 | NA | 400 | 0.2 | 22.14 | 1200000
2021-05-18 | 7110 | 7.11 | 7.24 | 7.41 | 142 | 16 | 266 | 24 | NA | 500 | 0.2 | 24.26 | 1300000
2021-05-19 | 7980 | 7.98 | 7.17 | 7.52 | 132 | 14 | 277 | 20 | NA | 450 | 0.2 | 23.32 | 1400000
2021-05-20 | 7560 | 7.56 | 7.12 | 7.33 | 128 | 15 | 244 | 22 | NA | 600 | 0.2 | 22.41 | 1600000
2021-05-21 | 7970 | 7.97 | 7.21 | 7.46 | 135 | 13 | 255 | 24 | NA | 500 | 0.2 | 21.62 | 1700000
2021-05-22 | 7730 | 7.73 | 7.33 | 7.77 | 130 | 15 | 248 | 21 | NA | 400 | 0.2 | 23.17 | 1400000
2021-05-23 | 7470 | 7.47 | 7.14 | 7.29 | 132 | 14 | 258 | 23 | NA | 500 | 0.2 | 22.11 | 1300000
2021-05-24 | 7800 | 7.8 | 7.26 | 7.55 | 136 | 15 | 265 | 22 | NA | 450 | 0.2 | 21.39 | 1600000
2021-05-25 | 7850 | 7.85 | 7.17 | 7.37 | 140 | 13 | 242 | 20 | NA | 500 | 0.2 | 22.16 | 1400000
2021-05-26 | 7980 | 7.98 | 7.12 | 7.44 | 145 | 14 | 256 | 24 | NA | 600 | 0.2 | 23.21 | 1300000
2021-05-27 | 7960 | 7.96 | 7.2 | 7.51 | 142 | 16 | 261 | 21 | NA | 400 | 0.2 | 24.13 | 1700000
2021-05-28 | 7920 | 7.92 | 7.25 | 7.63 | 138 | 15 | 240 | 23 | NA | 500 | 0.2 | 20.19 | 1600000
2021-05-29 | 7150 | 7.15 | 7.34 | 7.79 | 130 | 13 | 247 | 20 | NA | 400 | 0.2 | 22.34 | 1400000
2021-05-30 | 7610 | 7.61 | 7.13 | 7.36 | 135 | 14 | 259 | 22 | NA | 600 | 0.2 | 21.67 | 1300000
2021-05-31 | 7560 | 7.56 | 7.22 | 7.61 | 140 | 16 | 261 | 24 | NA | 450 | 0.2 | 23.49 | 1600000
Average | 7499.5161 | 7.4995 | 7.2077 | 7.4587 | 137.7419 | 14.3226 | 256.1935 | 21.8387 | NA | 487.0968 | 0.2 | 22.6413 | 1454838.7097
SUM | 232485 | 232.485 | 223.44 | 231.22 | 4270 | 444 | 7942 | 677 |  | 15100 | 6.2 | 701.88 | 45100000
Source: | Logbook of Labarotory at Sewage Treament Plant
Max | 7980 | 7.98 | 7.34 | 7.79 | 146 | 16 | 277 | 24 |  | 600 | 0.2 | 24.29 | 1700000
Min | 7110 | 7.11 | 7.11 | 7.27 | 128 | 13 | 240 | 19 |  | 400 | 0.2 | 20.19 | 1200000