## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-10-01 | 55120 | 55.12 | 7.21 | 7.64 | 145 | 14 | 320 | 36 | 248 | 24 | NA | 500 | 0.3 | 22.32 | 1200000 | Retaining wall of Nalla at Sasur Kadheri SPS is broken hence raw sewage is going directly into the river.
2021-10-02 | 50960 | 50.96 | 7.26 | 7.76 | 150 | 16 | 308 | 40 | 278 | 28 | NA | 600 | 0.2 | 24.21 | 1700000
2021-10-03 | 52240 | 52.24 | 7.28 | 7.64 | 150 | 12 | 328 | 40 | 290 | 26 | NA | 700 | 0.2 | 23.42 | 1300000
2021-10-04 | 51900 | 51.9 | 7.17 | 7.84 | 140 | 16 | 304 | 44 | 268 | 22 | NA | 600 | 0.3 | 23.52 | 1300000
2021-10-05 | 51780 | 51.78 | 7.14 | 7.5 | 135 | 15 | 320 | 40 | 278 | 26 | NA | 500 | 0.2 | 23.23 | 1200000
2021-10-06 | 44120 | 44.12 | 7.28 | 7.76 | 140 | 15 | 312 | 36 | 250 | 28 | NA | 400 | 0.2 | 20.99 | 1300000
2021-10-07 | 50880 | 50.88 | 7.18 | 7.8 | 150 | 18 | 324 | 40 | 236 | 26 | NA | 500 | 0.3 | 22.85 | 1200000
2021-10-08 | 49100 | 49.1 | 7.21 | 7.84 | 140 | 12 | 336 | 36 | 250 | 28 | NA | 700 | 0.2 | 22.31 | 1300000
2021-10-09 | 46750 | 46.75 | 7.24 | 7.64 | 145 | 14 | 324 | 40 | 260 | 26 | NA | 500 | 0.2 | 24.35 | 1400000
2021-10-10 | 50450 | 50.45 | 7.14 | 7.84 | 150 | 16 | 320 | 40 | 228 | 28 | NA | 700 | 0.3 | 23.96 | 1300000
2021-10-11 | 50650 | 50.65 | 7.18 | 7.91 | 140 | 14 | 332 | 36 | 254 | 28 | NA | 700 | 0.3 | 22.72 | 1300000
2021-10-12 | 49810 | 49.81 | 7.24 | 7.84 | 150 | 16 | 320 | 40 | 274 | 26 | NA | 500 | 0.2 | 24.03 | 1300000
2021-10-13 | 50800 | 50.8 | 7.26 | 7.88 | 135 | 14 | 304 | 36 | 236 | 22 | NA | 600 | 0.2 | 24.38 | 1700000
2021-10-14 | 48120 | 48.12 | 7.24 | 7.64 | 145 | 18 | 336 | 40 | 256 | 24 | NA | 700 | 0.3 | 21.65 | 1300000
2021-10-15 | 42950 | 42.95 | 7.18 | 7.74 | 140 | 15 | 320 | 36 | 236 | 24 | NA | 500 | 0.2 | 22.93 | 1300000
2021-10-16 | 47000 | 47 | 7.19 | 7.78 | 140 | 16 | 328 | 36 | 236 | 28 | NA | 500 | 0.3 | 22.21 | 1700000
2021-10-17 | 49140 | 49.14 | 7.22 | 7.68 | 150 | 18 | 324 | 40 | 256 | 28 | NA | 700 | 0.2 | 21.33 | 1200000
2021-10-18 | 45500 | 45.5 | 7.19 | 7.84 | 145 | 15 | 316 | 36 | 256 | 26 | NA | 500 | 0.2 | 22.24 | 1300000
2021-10-19 | 49500 | 49.5 | 7.2 | 7.81 | 140 | 13 | 280 | 40 | 210 | 28 | NA | 700 | 0.2 | 24.61 | 1200000
2021-10-20 | 44300 | 44.3 | 7.15 | 7.64 | 135 | 15 | 324 | 36 | 232 | 26 | NA | 700 | 0.3 | 24 | 1700000
2021-10-21 | 41900 | 41.9 | 7.19 | 7.84 | 145 | 16 | 316 | 40 | 256 | 24 | NA | 400 | 0.2 | 24.23 | 1400000
2021-10-22 | 51050 | 51.05 | 7.18 | 7.78 | 130 | 14 | 320 | 40 | 274 | 26 | NA | 500 | 0.2 | 24.03 | 1700000
2021-10-23 | 45910 | 45.91 | 7.24 | 7.84 | 140 | 18 | 328 | 40 | 216 | 28 | NA | 700 | 0.3 | 22.82 | 1200000
2021-10-24 | 51940 | 51.94 | 7.16 | 7.96 | 150 | 15 | 316 | 36 | 232 | 24 | NA | 500 | 0.2 | 22.21 | 1700000
2021-10-25 | 52360 | 52.36 | 7.18 | 7.84 | 140 | 14 | 320 | 40 | 244 | 28 | NA | 400 | 0.3 | 21.6 | 1400000
2021-10-26 | 50000 | 50 | 7.21 | 7.78 | 145 | 14 | 312 | 36 | 216 | 24 | NA | 500 | 0.3 | 24.45 | 1300000
2021-10-27 | 50840 | 50.84 | 7.28 | 7.84 | 140 | 15 | 336 | 40 | 244 | 28 | NA | 700 | 0.3 | 21.97 | 1200000
2021-10-28 | 50880 | 50.88 | 7.16 | 7.8 | 135 | 15 | 332 | 40 | 240 | 26 | NA | 500 | 0.2 | 25.43 | 1700000
2021-10-29 | 51800 | 51.8 | 7.24 | 7.94 | 135 | 11 | 328 | 36 | 258 | 28 | NA | 700 | 0.3 | 24.38 | 1400000
2021-10-30 | 49300 | 49.3 | 7.19 | 7.74 | 145 | 16 | 320 | 40 | 228 | 26 | NA | 500 | 0.3 | 22 | 1300000
2021-10-31 | 51160 | 51.16 | 7.22 | 7.82 | 135 | 13 | 284 | 36 | 250 | 28 | NA | 700 | 0.2 | 24.66 | 1200000
Average | 49297.0968 | 49.2971 | 7.2068 | 7.7806 | 142.0968 | 14.9355 | 319.0968 | 38.4516 | 248.0645 | 26.1935 | NA | 577.4194 | 0.24516 | 23.1948 | 1377419.3548
1528.21
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 41900 | 41.9 | 7.14 | 7.5 | 130 | 11 | 280 | 36 | 210 | 22 |  | 400 | 0.2 | 20.99 | 1200000
Max | 55120 | 55.12 | 7.28 | 7.96 | 150 | 18 | 336 | 44 | 290 | 28 |  | 700 | 0.3 | 25.43 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-10-01 | 34010 | 34.01 | 7.34 | 7.57 | 153 | 22 | 364 | 40 | 318 | 38 | NA | 400 | 0.3 | 23.9 | 1100000 | Plant availability is 100%
2021-10-02 | 34630 | 34.63 | 7.41 | 7.65 | 163 | 25 | 372 | 44 | 326 | 35 | NA | 800 | 0.2 | 24.2 | 1400000 | Plant availability is 100%
2021-10-03 | 34170 | 34.17 | 7.38 | 7.61 | 157 | 23 | 360 | 36 | 304 | 42 | NA | 500 | 0.2 | 23.6 | 1700000 | Plant availability is 100%
2021-10-04 | 31610 | 31.61 | 7.32 | 7.59 | 160 | 21 | 368 | 48 | 312 | 39 | NA | 700 | 0.3 | 25.7 | 1200000 | Plant availability is 100%
2021-10-05 | 32200 | 32.2 | 7.35 | 7.58 | 153 | 24 | 356 | 44 | 321 | 42 | NA | 600 | 0.2 | 24.5 | 1400000 | Plant availability is 100%
2021-10-06 | 31470 | 31.47 | 7.43 | 7.55 | 157 | 22 | 360 | 40 | 314 | 37 | NA | 400 | 0.2 | 23.7 | 1200000 | Plant availability is 100%
2021-10-07 | 31960 | 31.96 | 7.41 | 7.56 | 160 | 21 | 364 | 44 | 319 | 36 | NA | 700 | 0.3 | 24.1 | 1100000 | Plant availability is 100%
2021-10-08 | 31970 | 31.97 | 7.33 | 7.62 | 167 | 23 | 356 | 36 | 325 | 40 | NA | 500 | 0.2 | 24.8 | 1300000 | Plant availability is 100%
2021-10-09 | 32390 | 32.39 | 7.35 | 7.57 | 163 | 24 | 360 | 40 | 302 | 34 | NA | 800 | 0.2 | 25.2 | 1400000 | Plant availability is 100%
2021-10-10 | 32010 | 32.01 | 7.28 | 7.39 | 157 | 23 | 352 | 36 | 298 | 38 | NA | 600 | 0.2 | 24 | 1600000 | Plant availability is 100%
2021-10-11 | 34140 | 34.14 | 7.3 | 7.49 | 153 | 27 | 360 | 44 | 309 | 45 | NA | 500 | 0.3 | 23.8 | 1100000 | Plant availability is 100%
2021-10-12 | 35670 | 35.67 | 7.36 | 7.51 | 150 | 25 | 368 | 40 | 326 | 41 | NA | 700 | 0.2 | 24.4 | 1200000 | Plant availability is 100%
2021-10-13 | 35490 | 35.49 | 7.34 | 7.47 | 157 | 28 | 364 | 32 | 322 | 33 | NA | 800 | 0.2 | 24.7 | 1300000 | Plant availability is 100%
2021-10-14 | 36600 | 36.6 | 7.39 | 7.53 | 160 | 26 | 356 | 36 | 312 | 37 | NA | 400 | 0.3 | 26.3 | 1300000 | Plant availability is 100%
2021-10-15 | 35270 | 35.27 | 7.4 | 7.58 | 167 | 24 | 360 | 40 | 300 | 43 | NA | 600 | 0.2 | 26.7 | 1400000 | Plant availability is 100%
2021-10-16 | 37740 | 37.74 | 7.37 | 7.54 | 163 | 22 | 352 | 44 | 317 | 35 | NA | 500 | 0.2 | 25.7 | 1200000 | Plant availability is 100%
2021-10-17 | 37430 | 37.43 | 7.35 | 7.51 | 157 | 20 | 356 | 36 | 328 | 38 | NA | 700 | 0.3 | 26.2 | 1100000 | Plant availability is 100%
2021-10-18 | 36860 | 36.86 | 7.32 | 7.55 | 150 | 22 | 364 | 40 | 314 | 36 | NA | 500 | 0.2 | 25.9 | 1300000 | Plant availability is 100%
2021-10-19 | 35840 | 35.84 | 7.34 | 7.42 | 147 | 21 | 368 | 48 | 302 | 39 | NA | 800 | 0.2 | 25 | 1400000 | Plant availability is 100%
2021-10-20 | 37790 | 37.79 | 7.29 | 7.43 | 157 | 23 | 360 | 44 | 310 | 34 | NA | 600 | 0.2 | 24.8 | 1600000 | Plant availability is 100%
2021-10-21 | 38550 | 38.55 | 7.31 | 7.5 | 163 | 26 | 352 | 36 | 308 | 40 | NA | 700 | 0.3 | 24.4 | 1200000 | Plant availability is 100%
2021-10-22 | 38030 | 38.03 | 7.36 | 7.61 | 160 | 25 | 356 | 32 | 323 | 33 | NA | 400 | 0.3 | 23.9 | 1300000 | Plant availability is 100%
2021-10-23 | 40170 | 40.17 | 7.42 | 7.59 | 172 | 28 | 364 | 40 | 325 | 37 | NA | 500 | 0.2 | 24.3 | 1700000 | Plant availability is 100%
2021-10-24 | 36480 | 36.48 | 7.4 | 7.62 | 167 | 24 | 368 | 44 | 318 | 43 | NA | 600 | 0.2 | 23.6 | 1200000 | Plant availability is 100%
2021-10-25 | 35770 | 35.77 | 7.38 | 7.56 | 163 | 23 | 360 | 48 | 306 | 39 | NA | 500 | 0.2 | 23.1 | 1100000 | Plant availability is 100%
2021-10-26 | 38250 | 38.25 | 7.35 | 7.58 | 160 | 25 | 364 | 36 | 308 | 38 | NA | 800 | 0.3 | 23.8 | 1400000 | Plant availability is 100%
2021-10-27 | 38290 | 38.29 | 7.32 | 7.61 | 153 | 23 | 356 | 40 | 320 | 34 | NA | 700 | 0.2 | 24.2 | 1200000 | Plant availability is 100%
2021-10-28 | 37550 | 37.55 | 7.28 | 7.63 | 150 | 24 | 360 | 44 | 298 | 31 | NA | 500 | 0.3 | 24.5 | 1300000 | Plant availability is 100%
2021-10-29 | 31400 | 31.4 | 7.3 | 7.6 | 147 | 23 | 364 | 36 | 315 | 37 | NA | 600 | 0.3 | 24.9 | 1600000 | 1. Due to rise in river levet, tapping point at Amitabh Bachchan culvert was closed on 29.10.2021 at 15:50. 2. Raw sewage from Allahpur drain and local house connections is received at site.
2021-10-30 | 31660 | 31.66 | 7.34 | 7.57 | 157 | 27 | 368 | 44 | 322 | 41 | NA | 400 | 0.2 | 25.3 | 1700000
2021-10-31 | 31320 | 31.32 | 7.31 | 7.53 | 153 | 26 | 356 | 48 | 326 | 33 | NA | 800 | 0.2 | 25 | 1400000
Average | 35055.4839 | 35.0555 | 7.3494 | 7.5523 | 157.9355 | 23.871 | 360.9032 | 40.6452 | 314.4516 | 37.6774 | NA | 600 | 0.23548 | 24.6516 | 1335483.871
1086.72
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 31320 | 31.32 | 7.28 | 7.39 | 147 | 20 | 352 | 32 | 298 | 31 |  | 400 | 0.2 | 23.1 | 1100000
Max | 40170 | 40.17 | 7.43 | 7.65 | 172 | 28 | 372 | 48 | 328 | 45 |  | 800 | 0.3 | 26.7 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-10-01 | 30010 | 30.01 | 7.39 | 7.62 | 150 | 15 | 336 | 36 | 280 | 17 | NA | 600 | 0.2 | 24.6 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-10-02 | 31260 | 31.26 | 7.43 | 7.59 | 144 | 13 | 328 | 40 | 272 | 18 | NA | 700 | 0.3 | 24.1 | 1300000 | Retaining wall for tapping of nearby nalla is broken
2021-10-03 | 31930 | 31.93 | 7.35 | 7.52 | 147 | 14 | 324 | 44 | 268 | 16 | NA | 500 | 0.2 | 24.7 | 1200000 | Retaining wall for tapping of nearby nalla is broken
2021-10-04 | 30950 | 30.95 | 7.47 | 7.65 | 138 | 12 | 332 | 40 | 284 | 18 | NA | 700 | 0.2 | 24.3 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-10-05 | 31230 | 31.23 | 7.51 | 7.73 | 141 | 13 | 340 | 44 | 280 | 21 | NA | 600 | 0.3 | 23.2 | 1300000 | Retaining wall for tapping of nearby nalla is broken
2021-10-06 | 29890 | 29.89 | 7.42 | 7.63 | 135 | 12 | 324 | 36 | 272 | 19 | NA | 500 | 0.2 | 24.1 | 1200000 | Retaining wall for tapping of nearby nalla is broken
2021-10-07 | 26810 | 26.81 | 7.37 | 7.58 | 144 | 16 | 332 | 40 | 284 | 18 | NA | 700 | 0.3 | 24.4 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-10-08 | 26580 | 26.58 | 7.45 | 7.67 | 138 | 15 | 328 | 44 | 276 | 20 | NA | 600 | 0.2 | 24.7 | 1300000 | Retaining wall for tapping of nearby nalla is broken
2021-10-09 | 25360 | 25.36 | 7.41 | 7.59 | 135 | 13 | 320 | 40 | 270 | 17 | NA | 700 | 0.3 | 24.4 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-10-10 | 25090 | 25.09 | 7.39 | 7.65 | 141 | 14 | 336 | 44 | 274 | 19 | NA | 500 | 0.2 | 24.3 | 1300000 | Retaining wall for tapping of nearby nalla is broken
2021-10-11 | 25170 | 25.17 | 7.43 | 7.61 | 138 | 12 | 324 | 36 | 265 | 18 | NA | 600 | 0.3 | 24.6 | 1200000 | Retaining wall for tapping of nearby nalla is broken
2021-10-12 | 29020 | 29.02 | 7.34 | 7.57 | 144 | 15 | 332 | 40 | 271 | 16 | NA | 700 | 0.2 | 24.2 | 1300000 | Retaining wall for tapping of nearby nalla is broken
2021-10-13 | 26230 | 26.23 | 7.45 | 7.64 | 138 | 13 | 328 | 44 | 278 | 18 | NA | 600 | 0.2 | 24.5 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-10-14 | 23520 | 23.52 | 7.38 | 7.72 | 147 | 15 | 320 | 36 | 269 | 17 | NA | 500 | 0.3 | 23.9 | 1200000 | Retaining wall for tapping of nearby nalla is broken
2021-10-15 | 20960 | 20.96 | 7.41 | 7.66 | 141 | 14 | 336 | 40 | 277 | 16 | NA | 700 | 0.2 | 24.9 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-10-16 | 22930 | 22.93 | 7.37 | 7.58 | 135 | 12 | 328 | 48 | 282 | 22 | NA | 600 | 0.3 | 24.2 | 1200000 | Retaining wall for tapping of nearby nalla is broken
2021-10-17 | 23350 | 23.35 | 7.46 | 7.65 | 138 | 13 | 332 | 44 | 279 | 21 | NA | 500 | 0.2 | 24 | 1100000 | Retaining wall for tapping of nearby nalla is broken
2021-10-18 | 22810 | 22.81 | 7.54 | 7.74 | 144 | 14 | 324 | 40 | 273 | 20 | NA | 700 | 0.2 | 23.9 | 1300000 | Retaining wall for tapping of nearby nalla is broken
2021-10-19 | 24110 | 24.11 | 7.48 | 7.67 | 141 | 16 | 328 | 44 | 285 | 19 | NA | 600 | 0.3 | 23.5 | 1200000 | Retaining wall for tapping of nearby nalla is broken
2021-10-20 | 20900 | 20.9 | 7.51 | 7.78 | 135 | 15 | 316 | 36 | 274 | 20 | NA | 500 | 0.2 | 23.1 | 1100000 | Retaining wall for tapping of nearby nalla is broken
2021-10-21 | 18230 | 18.23 | 7.43 | 7.69 | 132 | 13 | 312 | 40 | 266 | 18 | NA | 400 | 0.3 | 23.4 | 1300000 | Retaining wall for tapping of nearby nalla is broken
2021-10-22 | 26910 | 26.91 | 7.39 | 7.58 | 129 | 15 | 296 | 44 | 259 | 21 | NA | 700 | 0.2 | 23.6 | 1200000 | Retaining wall for tapping of nearby nalla is broken
2021-10-23 | 33490 | 33.49 | 7.47 | 7.64 | 126 | 14 | 288 | 40 | 253 | 20 | NA | 600 | 0.3 | 23.7 | 1300000 | Retaining wall for tapping of nearby nalla is broken
2021-10-24 | 33400 | 33.4 | 7.41 | 7.73 | 120 | 13 | 280 | 44 | 264 | 19 | NA | 500 | 0.2 | 24.2 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-10-25 | 32210 | 32.21 | 7.54 | 7.69 | 128 | 12 | 284 | 48 | 260 | 21 | NA | 400 | 0.3 | 24.3 | 1300000 | Retaining wall for tapping of nearby nalla is broken
2021-10-26 | 30580 | 30.58 | 7.49 | 7.61 | 123 | 14 | 276 | 44 | 255 | 20 | NA | 600 | 0.2 | 23.7 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-10-27 | 32340 | 32.34 | 7.43 | 7.58 | 129 | 13 | 280 | 48 | 257 | 18 | NA | 500 | 0.3 | 23.5 | 1300000 | 1. Due to rise in river levet, inlet gate at tapping point of nearby nalla was closed on 27.10.2021 at 10:17 AM. 2. Raw sewage from Kalimandir SPS and Vivekanand park SPS is received in plant only. 3. Retaining wall for tapping of nearby nalla is broken
2021-10-28 | 31040 | 31.04 | 7.56 | 7.75 | 138 | 15 | 272 | 44 | 251 | 20 | NA | 400 | 0.2 | 24 | 1200000
2021-10-29 | 30920 | 30.92 | 7.51 | 7.63 | 132 | 12 | 276 | 40 | 259 | 19 | NA | 600 | 0.2 | 23.8 | 1400000
2021-10-30 | 31360 | 31.36 | 7.42 | 7.54 | 135 | 15 | 282 | 38 | 260 | 20 | NA | 500 | 0.2 | 24.3 | 1200000
2021-10-31 | 30720 | 30.72 | 7.49 | 7.65 | 141 | 14 | 288 | 44 | 250 | 18 | NA | 600 | 0.3 | 24.1 | 1300000
Average | 27719.6774 | 27.7197 | 7.4419 | 7.6432 | 137 | 13.7419 | 312.9677 | 41.6129 | 269.2581 | 18.8387 | NA | 577.4194 | 0.24194 | 24.071 | 1287096.7742
859.31
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 18230 | 18.23 | 7.34 | 7.52 | 120 | 12 | 272 | 36 | 250 | 16 |  | 400 | 0.2 | 23.1 | 1100000
Max | 33490 | 33.49 | 7.56 | 7.78 | 150 | 16 | 340 | 48 | 285 | 22 |  | 700 | 0.3 | 24.9 | 1400000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-10-01 | 7850 | 7.85 | 7.31 | 7.58 | 145 | 13 | 320 | 34 | 249 | 23 | NA | 600 | 0.3 | 21.33 | 1400000 | Plant availability is 100%
2021-10-02 | 7900 | 7.9 | 7.15 | 7.44 | 140 | 15 | 304 | 40 | 260 | 21 | NA | 500 | 0.2 | 22.16 | 1700000 | Plant availability is 100%
2021-10-03 | 7920 | 7.92 | 7.21 | 7.64 | 135 | 13 | 292 | 36 | 240 | 24 | NA | 700 | 0.2 | 20.41 | 1300000 | Plant availability is 100%
2021-10-04 | 7890 | 7.89 | 7.28 | 7.71 | 142 | 16 | 308 | 44 | 256 | 22 | NA | 400 | 0.3 | 21.12 | 1600000 | Plant availability is 100%
2021-10-05 | 7820 | 7.82 | 7.16 | 7.37 | 136 | 14 | 288 | 32 | 244 | 20 | NA | 500 | 0.2 | 21.52 | 1400000 | Plant availability is 100%
2021-10-06 | 7880 | 7.88 | 7.25 | 7.51 | 145 | 15 | 312 | 40 | 265 | 23 | NA | 600 | 0.3 | 23.14 | 1700000 | Plant availability is 100%
2021-10-07 | 7910 | 7.91 | 7.17 | 7.46 | 140 | 13 | 300 | 36 | 251 | 21 | NA | 400 | 0.2 | 22.26 | 1300000 | Plant availability is 100%
2021-10-08 | 7960 | 7.96 | 7.24 | 7.62 | 146 | 15 | 316 | 44 | 242 | 24 | NA | 500 | 0.2 | 21.77 | 1600000 | Plant availability is 100%
2021-10-09 | 7760 | 7.76 | 7.14 | 7.56 | 138 | 14 | 296 | 40 | 263 | 22 | NA | 700 | 0.3 | 20.48 | 1400000 | Plant availability is 100%
2021-10-10 | 7940 | 7.94 | 7.31 | 7.69 | 135 | 13 | 304 | 36 | 255 | 20 | NA | 600 | 0.2 | 22.56 | 1700000 | Plant availability is 100%
2021-10-11 | 8440 | 8.44 | 7.22 | 7.48 | 145 | 15 | 320 | 40 | 268 | 23 | NA | 400 | 0.3 | 23.31 | 1300000 | Plant availability is 100%
2021-10-12 | 8890 | 8.89 | 7.26 | 7.55 | 140 | 14 | 308 | 34 | 245 | 21 | NA | 500 | 0.2 | 21.29 | 1600000 | Plant availability is 100%
2021-10-13 | 8680 | 8.68 | 7.37 | 7.74 | 148 | 16 | 324 | 44 | 270 | 24 | NA | 700 | 0.2 | 22.42 | 1400000 | Plant availability is 100%
2021-10-14 | 8110 | 8.11 | 7.29 | 7.66 | 136 | 14 | 310 | 36 | 258 | 22 | NA | 500 | 0.3 | 20.84 | 1200000 | Plant availability is 100%
2021-10-15 | 7400 | 7.4 | 7.18 | 7.55 | 145 | 15 | 316 | 40 | 240 | 25 | NA | 600 | 0.3 | 21.36 | 1700000 | Plant availability is 100%
2021-10-16 | 7800 | 7.8 | 7.13 | 7.45 | 138 | 13 | 304 | 32 | 257 | 23 | NA | 400 | 0.2 | 22.19 | 1300000 | Plant availability is 100%
2021-10-17 | 6580 | 6.58 | 7.23 | 7.59 | 142 | 15 | 312 | 38 | 264 | 24 | NA | 500 | 0.2 | 20.59 | 1400000 | Plant was in shutdown from 12 PM to 6 PM for replacement of flowmeter in inlet line of STP.
2021-10-18 | 11341 | 11.341 | 7.11 | 7.32 | 135 | 17 | 296 | 44 | 278 | 22 | NA | 700 | 0.2 | 21.4 | 1600000 | Plant availability is 100%
2021-10-19 | 12686 | 12.686 | 7.3 | 7.64 | 140 | 14 | 308 | 36 | 269 | 20 | NA | 400 | 0.3 | 20.77 | 1300000 | Plant availability is 100%
2021-10-20 | 11054 | 11.054 | 7.24 | 7.77 | 145 | 16 | 324 | 40 | 273 | 23 | NA | 600 | 0.3 | 22.13 | 1700000 | Plant availability is 100%
2021-10-21 | 10120 | 10.12 | 7.32 | 7.51 | 136 | 13 | 300 | 32 | 252 | 21 | NA | 500 | 0.2 | 21.29 | 1600000 | Plant availability is 100%
2021-10-22 | 11010 | 11.01 | 7.21 | 7.47 | 142 | 15 | 316 | 44 | 265 | 24 | NA | 700 | 0.2 | 22.64 | 1400000 | Plant availability is 100%
2021-10-23 | 11170 | 11.17 | 7.34 | 7.69 | 132 | 14 | 304 | 36 | 276 | 22 | NA | 500 | 0.2 | 23.14 | 1700000 | Plant availability is 100%
2021-10-24 | 12210 | 12.21 | 7.15 | 7.54 | 140 | 15 | 320 | 40 | 267 | 25 | NA | 600 | 0.3 | 21.43 | 1300000 | Plant availability is 100%
2021-10-25 | 11510 | 11.51 | 7.27 | 7.78 | 135 | 17 | 308 | 44 | 255 | 23 | NA | 500 | 0.2 | 20.64 | 1400000 | Plant availability is 100%
2021-10-26 | 10850 | 10.85 | 7.22 | 7.68 | 130 | 15 | 292 | 38 | 241 | 26 | NA | 700 | 0.2 | 22.15 | 1600000 | Plant availability is 100%
2021-10-27 | 10310 | 10.31 | 7.14 | 7.56 | 138 | 16 | 310 | 42 | 260 | 24 | NA | 400 | 0.3 | 21.32 | 1300000 | Plant availability is 100%
2021-10-28 | 9950 | 9.95 | 7.29 | 7.48 | 132 | 18 | 300 | 46 | 258 | 21 | NA | 500 | 0.3 | 20.44 | 1200000 | Plant availability is 100%
2021-10-29 | 11390 | 11.39 | 7.16 | 7.52 | 140 | 15 | 316 | 40 | 268 | 23 | NA | 400 | 0.3 | 21.1 | 1400000 | Plant availability is 100%
2021-10-30 | 11490 | 11.49 | 7.25 | 7.63 | 150 | 13 | 324 | 36 | 275 | 20 | NA | 600 | 0.2 | 23.22 | 1600000 | Plant availability is 100%
2021-10-31 | 12010 | 12.01 | 7.31 | 7.41 | 145 | 16 | 318 | 44 | 285 | 25 | NA | 500 | 0.2 | 21.26 | 1700000 | Plant availability is 100%
Average | 9413.9032 | 9.4139 | 7.2326 | 7.5677 | 139.871 | 14.7419 | 308.7097 | 38.9677 | 259.6452 | 22.6129 | NA | 538.7097 | 0.24194 | 21.6671 | 1477419.3548
291.831
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 6580 | 6.58 | 7.11 | 7.32 | 130 | 13 | 288 | 32 | 240 | 20 |  | 400 | 0.2 | 20.41 | 1200000
Max | 12686 | 12.686 | 7.37 | 7.78 | 150 | 18 | 324 | 46 | 285 | 26 |  | 700 | 0.3 | 23.31 | 1700000