## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-09-01 | No testing was done as STP was in shutdown | [12 empty] | 22.56 | No testing was done as STP was in shutdown | 1) Plant is in shutdown for replacement of header line of HNC pumps in Ghagharnalla MPS.
2021-09-02 | [13 empty] | 24.2
2021-09-03 | [13 empty] | 24.4
2021-09-04 | [13 empty] | 22.15
2021-09-05 | [13 empty] | 23.14
2021-09-06 | 5900 | 5.9 | 7.16 | 7.78 | 150 | 19 | 344 | 48 | 262 | 28 | NA | 400 | 0.2 | 22.56 | 1300000 | 1) Ghagharnalla MPS was started at 4:50 PM on 06.09.2021 after completion of header line replacement works. At the same time Sasur Khaderi SPS was also started. 2) Subsequently, Numayadahi STP was also started.
2021-09-07 | 46680 | 46.68 | 7.17 | 7.69 | 140 | 19 | 320 | 44 | 276 | 26 | NA | 700 | 0.3 | 22.61 | 1200000 | 1) Retaining wall of Nalla at Ghagharnalla MPS is broken hence raw sewage is going directly into the river. 2) Retaining wall of Nalla at Sasur Kadheri SPS is broken hence raw sewage is going directly into the river.
2021-09-08 | 55990 | 55.99 | 7.16 | 7.79 | 155 | 16 | 320 | 40 | 236 | 28 | NA | 500 | 0.3 | 22.26 | 1400000
2021-09-09 | 50720 | 50.72 | 7.12 | 7.64 | 145 | 16 | 312 | 36 | 228 | 24 | NA | 600 | 0.2 | 22.27 | 1700000
2021-09-10 | 53550 | 53.55 | 7.24 | 7.68 | 150 | 15 | 328 | 40 | 296 | 28 | NA | 500 | 0.3 | 22.61 | 1300000
2021-09-11 | 49920 | 49.92 | 7.08 | 7.64 | 150 | 18 | 308 | 40 | 264 | 26 | NA | 500 | 0.3 | 22.45 | 1700000
2021-09-12 | 49390 | 49.39 | 7.15 | 7.54 | 145 | 13 | 328 | 36 | 240 | 24 | NA | 600 | 0.2 | 23.69 | 1300000
2021-09-13 | 48250 | 48.25 | 7.35 | 7.89 | 140 | 16 | 324 | 40 | 228 | 24 | NA | 700 | 0.2 | 21.63 | 1200000
2021-09-14 | 47140 | 47.14 | 7.23 | 7.94 | 135 | 14 | 312 | 44 | 228 | 28 | NA | 600 | 0.3 | 23.23 | 1300000
2021-09-15 | 47910 | 47.91 | 7.12 | 7.82 | 150 | 18 | 328 | 40 | 288 | 28 | NA | 500 | 0.2 | 22.61 | 1400000
2021-09-16 | 43200 | 43.2 | 7.14 | 7.84 | 140 | 14 | 320 | 48 | 280 | 26 | NA | 600 | 0.3 | 21.85 | 1700000
2021-09-17 | 41140 | 41.14 | 7.24 | 7.84 | 130 | 16 | 308 | 40 | 296 | 24 | NA | 700 | 0.3 | 23.63 | 1300000
2021-09-18 | 36780 | 36.78 | 7.18 | 7.49 | 150 | 14 | 304 | 36 | 286 | 28 | NA | 400 | 0.2 | 23.2 | 1700000
2021-09-19 | 38110 | 38.11 | 7.24 | 7.69 | 145 | 16 | 328 | 44 | 240 | 26 | NA | 600 | 0.2 | 23.63 | 1200000
2021-09-20 | 37380 | 37.38 | 7.26 | 7.66 | 130 | 14 | 336 | 40 | 246 | 28 | NA | 500 | 0.3 | 22.42 | 1300000
2021-09-21 | 46140 | 46.14 | 7.12 | 7.68 | 135 | 15 | 328 | 48 | 226 | 26 | NA | 500 | 0.3 | 22.24 | 1400000
2021-09-22 | 47890 | 47.89 | 7.14 | 7.84 | 135 | 13 | 336 | 40 | 264 | 24 | NA | 600 | 0.2 | 22.61 | 1200000
2021-09-23 | 47330 | 47.33 | 7.19 | 7.78 | 140 | 16 | 304 | 36 | 242 | 28 | NA | 500 | 0.3 | 22.42 | 1300000
2021-09-24 | 52250 | 52.25 | 7.17 | 7.58 | 135 | 13 | 344 | 40 | 248 | 24 | NA | 700 | 0.2 | 23.07 | 1400000
2021-09-25 | 52140 | 52.14 | 7.18 | 7.82 | 150 | 15 | 312 | 36 | 296 | 24 | NA | 700 | 0.2 | 22.74 | 1200000
2021-09-26 | 48160 | 48.16 | 7.16 | 7.78 | 140 | 12 | 328 | 44 | 278 | 24 | NA | 500 | 0.3 | 21.62 | 1300000
2021-09-27 | 43410 | 43.41 | 7.12 | 7.68 | 150 | 15 | 336 | 40 | 220 | 28 | NA | 500 | 0.2 | 22.24 | 1200000
2021-09-28 | 45110 | 45.11 | 7.18 | 7.74 | 135 | 14 | 304 | 36 | 246 | 24 | NA | 600 | 0.2 | 23.23 | 1700000
2021-09-29 | 50950 | 50.95 | 7.16 | 7.78 | 140 | 16 | 328 | 40 | 256 | 28 | NA | 500 | 0.2 | 22.4 | 1300000
2021-09-30 | 49430 | 49.43 | 7.19 | 7.89 | 145 | 12 | 320 | 40 | 280 | 26 | NA | 700 | 0.3 | 22.61 | 1400000
Average | 45394.8 | 45.3948 | 7.178 | 7.74 | 142.4 | 15.16 | 322.4 | 40.64 | 258 | 26.08 | NA | 568 | 0.248 | 22.7427 | 1376000
1134.87
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 5900 | 5.9 | 7.08 | 7.49 | 130 | 12 | 304 | 36 | 220 | 24 |  | 400 | 0.2 | 21.62 | 1200000
Max | 55990 | 55.99 | 7.35 | 7.94 | 155 | 19 | 344 | 48 | 296 | 28 |  | 700 | 0.3 | 24.4 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-09-01 | 42230 | 42.23 | 7.45 | 7.56 | 163 | 25 | 364 | 44 | 324 | 38 | NA | 800 | 0.3 | 23.9 | 1300000
2021-09-02 | 38170 | 38.17 | 7.36 | 7.49 | 157 | 22 | 360 | 40 | 318 | 42 | NA | 700 | 0.3 | 23.7 | 1400000
2021-09-03 | 37420 | 37.42 | 7.38 | 7.44 | 155 | 20 | 352 | 36 | 317 | 39 | NA | 500 | 0.2 | 24.1 | 1700000
2021-09-04 | 40770 | 40.77 | 7.41 | 7.53 | 158 | 24 | 360 | 44 | 325 | 43 | NA | 600 | 0.2 | 24.6 | 1200000
2021-09-05 | 43810 | 43.81 | 7.34 | 7.52 | 160 | 26 | 364 | 40 | 320 | 40 | NA | 500 | 0.2 | 25.16 | 1100000
2021-09-06 | 44340 | 44.34 | 7.4 | 7.54 | 158 | 25 | 352 | 36 | 334 | 42 | NA | 800 | 0.3 | 24.8 | 1200000
2021-09-07 | 41520 | 41.52 | 7.34 | 7.48 | 154 | 23 | 360 | 40 | 329 | 38 | NA | 700 | 0.2 | 25.4 | 1300000
2021-09-08 | 39490 | 39.49 | 7.37 | 7.55 | 158 | 28 | 356 | 32 | 332 | 46 | NA | 600 | 0.2 | 25.1 | 1400000
2021-09-09 | 41490 | 41.49 | 7.35 | 7.57 | 153 | 24 | 352 | 32 | 326 | 41 | NA | 800 | 0.3 | 24.7 | 1300000
2021-09-10 | 44770 | 44.77 | 7.39 | 7.51 | 149 | 22 | 360 | 36 | 328 | 44 | NA | 500 | 0.2 | 24.2 | 1700000
2021-09-11 | 41880 | 41.88 | 7.38 | 7.56 | 157 | 20 | 356 | 40 | 322 | 37 | NA | 700 | 0.2 | 23.9 | 1100000
2021-09-12 | 41340 | 41.34 | 7.33 | 7.58 | 153 | 23 | 352 | 36 | 310 | 40 | NA | 600 | 0.3 | 23.4 | 1200000
2021-09-13 | 34530 | 34.53 | 7.36 | 7.54 | 157 | 21 | 348 | 40 | 321 | 37 | NA | 800 | 0.2 | 25.5 | 1400000
2021-09-14 | 35520 | 35.52 | 7.37 | 7.52 | 146 | 22 | 356 | 44 | 309 | 33 | NA | 500 | 0.2 | 23.8 | 1200000
2021-09-15 | 34120 | 34.12 | 7.42 | 7.58 | 133 | 19 | 364 | 40 | 318 | 31 | NA | 700 | 0.3 | 23.2 | 1300000
2021-09-16 | 34650 | 34.65 | 7.35 | 7.57 | 126 | 17 | 360 | 36 | 306 | 35 | NA | 600 | 0.2 | 24.4 | 1400000
2021-09-17 | 34560 | 34.56 | 7.38 | 7.55 | 130 | 20 | 368 | 40 | 315 | 32 | NA | 700 | 0.2 | 23.9 | 1700000
2021-09-18 | 35110 | 35.11 | 7.36 | 7.53 | 147 | 23 | 364 | 44 | 322 | 38 | NA | 800 | 0.2 | 24.3 | 1400000
2021-09-19 | 41600 | 41.6 | 7.38 | 7.57 | 153 | 24 | 360 | 40 | 327 | 34 | NA | 500 | 0.3 | 24.7 | 1100000
2021-09-20 | 38930 | 38.93 | 7.41 | 7.54 | 157 | 27 | 368 | 48 | 308 | 36 | NA | 600 | 0.3 | 25 | 1600000
2021-09-21 | 40300 | 40.3 | 7.4 | 7.48 | 153 | 28 | 360 | 36 | 301 | 41 | NA | 700 | 0.2 | 26.4 | 1300000
2021-09-22 | 37860 | 37.86 | 7.44 | 7.55 | 160 | 25 | 356 | 32 | 319 | 43 | NA | 500 | 0.2 | 25.7 | 1200000
2021-09-23 | 41010 | 41.01 | 7.37 | 7.59 | 163 | 29 | 364 | 40 | 325 | 39 | NA | 800 | 0.3 | 24.6 | 1400000
2021-09-24 | 23250 | 23.25 | 7.39 | 7.51 | 157 | 26 | 368 | 44 | 319 | 34 | NA | 700 | 0.3 | 23.8 | 1100000 | Due to rise in river levet, tapping point at Amitabh Bachchan culvert was closed on 24.09.2021 at 10:15 AM.
2021-09-25 | 27430 | 27.43 | 7.35 | 7.47 | 153 | 24 | 360 | 36 | 324 | 40 | NA | 600 | 0.2 | 23.1 | 1200000 | Tapping point at Amitabh Bachchan culvert is closed.
2021-09-26 | 20160 | 20.16 | 7.33 | 7.51 | 154 | 21 | 356 | 40 | 310 | 37 | NA | 700 | 0.2 | 22.6 | 1400000
2021-09-27 | 21710 | 21.71 | 7.38 | 7.56 | 156 | 23 | 360 | 44 | 322 | 33 | NA | 500 | 0.3 | 24 | 1100000 | Due to fall in river levet, tapping point at Amitabh Bachchan culvert was opened on 27.09.2021 at 09:00 PM.
2021-09-28 | 33530 | 33.53 | 7.42 | 7.53 | 157 | 26 | 368 | 40 | 305 | 32 | NA | 800 | 0.2 | 26.2 | 1200000
2021-09-29 | 34370 | 34.37 | 7.43 | 7.6 | 151 | 25 | 360 | 36 | 320 | 42 | NA | 700 | 0.2 | 25.5 | 1700000
2021-09-30 | 32330 | 32.33 | 7.36 | 7.55 | 155 | 24 | 356 | 32 | 326 | 33 | NA | 600 | 0.2 | 24.4 | 1300000
Average | 36606.6667 | 36.6067 | 7.38 | 7.536 | 152.7667 | 23.5333 | 359.4667 | 38.9333 | 319.4 | 38 | NA | 653.3333 | 0.23667 | 24.4687 | 1330000
1098.2
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 20160 | 20.16 | 7.33 | 7.44 | 126 | 17 | 348 | 32 | 301 | 31 |  | 500 | 0.2 | 22.6 | 1100000
Max | 44770 | 44.77 | 7.45 | 7.6 | 163 | 29 | 368 | 48 | 334 | 46 |  | 800 | 0.3 | 26.4 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-09-01 | 26340 | 26.34 | 7.43 | 7.52 | 150 | 14 | 332 | 44 | 301 | 19 | NA | 500 | 0.2 | 24.9 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-09-02 | 25900 | 25.9 | 7.37 | 7.49 | 144 | 12 | 324 | 40 | 297 | 20 | NA | 600 | 0.2 | 24.3 | 1200000 | Retaining wall for tapping of nearby nalla is broken
2021-09-03 | 29010 | 29.01 | 7.47 | 7.59 | 147 | 13 | 328 | 36 | 288 | 18 | NA | 700 | 0.3 | 24.8 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-09-04 | 28520 | 28.52 | 7.39 | 7.57 | 141 | 12 | 312 | 40 | 272 | 24 | NA | 600 | 0.3 | 24.7 | 1300000 | Retaining wall for tapping of nearby nalla is broken
2021-09-05 | 29260 | 29.26 | 7.42 | 7.53 | 150 | 14 | 324 | 44 | 293 | 22 | NA | 700 | 0.2 | 24.5 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-09-06 | 26980 | 26.98 | 7.49 | 7.54 | 144 | 12 | 320 | 40 | 282 | 20 | NA | 500 | 0.2 | 24.2 | 1200000 | Retaining wall for tapping of nearby nalla is broken
2021-09-07 | 25610 | 25.61 | 7.31 | 7.51 | 141 | 13 | 328 | 36 | 274 | 21 | NA | 600 | 0.2 | 24.5 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-09-08 | 28220 | 28.22 | 7.38 | 7.47 | 147 | 15 | 336 | 40 | 289 | 22 | NA | 500 | 0.2 | 24.4 | 1300000 | Retaining wall for tapping of nearby nalla is broken
2021-09-09 | 28710 | 28.71 | 7.25 | 7.41 | 138 | 12 | 320 | 44 | 270 | 20 | NA | 700 | 0.3 | 24.3 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-09-10 | 29260 | 29.26 | 7.47 | 7.59 | 141 | 14 | 332 | 40 | 283 | 22 | NA | 500 | 0.2 | 23.7 | 1200000 | Retaining wall for tapping of nearby nalla is broken
2021-09-11 | 29110 | 29.11 | 7.33 | 7.47 | 147 | 13 | 336 | 44 | 281 | 20 | NA | 600 | 0.2 | 25.2 | 1300000 | Retaining wall for tapping of nearby nalla is broken
2021-09-12 | 26490 | 26.49 | 7.41 | 7.51 | 141 | 14 | 328 | 36 | 276 | 23 | NA | 700 | 0.3 | 24.1 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-09-13 | 27350 | 27.35 | 7.37 | 7.42 | 135 | 12 | 320 | 40 | 270 | 21 | NA | 600 | 0.2 | 24.3 | 1200000 | Retaining wall for tapping of nearby nalla is broken
2021-09-14 | 22790 | 22.79 | 7.48 | 7.56 | 141 | 13 | 336 | 44 | 278 | 19 | NA | 700 | 0.3 | 24.7 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-09-15 | 29660 | 29.66 | 7.32 | 7.49 | 138 | 12 | 312 | 40 | 265 | 17 | NA | 500 | 0.2 | 23.8 | 1500000 | Retaining wall for tapping of nearby nalla is broken
2021-09-16 | 31810 | 31.81 | 7.43 | 7.58 | 132 | 11 | 300 | 48 | 271 | 23 | NA | 600 | 0.2 | 23.1 | 1300000 | 1. Retaining wall for tapping of nearby nalla is broken. 2. Due to rise in river levet, inlet gate at tapping point of nearby nalla was closed on 16.09.2021.
2021-09-17 | 31560 | 31.56 | 7.29 | 7.47 | 135 | 12 | 288 | 48 | 262 | 24 | NA | 700 | 0.3 | 24 | 1400000 | 1. Retaining wall for tapping of nearby nalla is broken. 2. Tapping point for nearby nalla is closed.
2021-09-18 | 32130 | 32.13 | 7.37 | 7.51 | 138 | 13 | 280 | 40 | 259 | 23 | NA | 600 | 0.2 | 24.4 | 1500000
2021-09-19 | 33020 | 33.02 | 7.42 | 7.59 | 144 | 15 | 288 | 44 | 254 | 22 | NA | 700 | 0.2 | 23.4 | 1400000
2021-09-20 | 31750 | 31.75 | 7.49 | 7.63 | 138 | 14 | 292 | 40 | 262 | 19 | NA | 500 | 0.3 | 23.3 | 1300000 | 1. Retaining wall for tapping of nearby nalla is broken. 2. Due to fall in river levet, inlet gate at tapping point of nearby nalla was opened on 20.09.2021.
2021-09-21 | 31480 | 31.48 | 7.35 | 7.52 | 132 | 12 | 304 | 44 | 267 | 20 | NA | 600 | 0.2 | 23 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-09-22 | 30690 | 30.69 | 7.41 | 7.49 | 141 | 13 | 308 | 40 | 261 | 18 | NA | 700 | 0.2 | 24 | 1500000 | Retaining wall for tapping of nearby nalla is broken
2021-09-23 | 30480 | 30.48 | 7.39 | 7.43 | 138 | 14 | 312 | 44 | 269 | 20 | NA | 500 | 0.3 | 23.6 | 1200000 | Retaining wall for tapping of nearby nalla is broken
2021-09-24 | 29900 | 29.9 | 7.31 | 7.47 | 144 | 15 | 308 | 40 | 262 | 19 | NA | 700 | 0.2 | 24.1 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-09-25 | 30820 | 30.82 | 7.46 | 7.54 | 135 | 13 | 320 | 44 | 273 | 21 | NA | 600 | 0.2 | 24.3 | 1300000 | Retaining wall for tapping of nearby nalla is broken
2021-09-26 | 32710 | 32.71 | 7.43 | 7.61 | 147 | 14 | 316 | 36 | 264 | 19 | NA | 700 | 0.3 | 24.2 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-09-27 | 30060 | 30.06 | 7.34 | 7.56 | 141 | 13 | 324 | 40 | 272 | 21 | NA | 500 | 0.2 | 24.5 | 1200000 | Retaining wall for tapping of nearby nalla is broken
2021-09-28 | 28230 | 28.23 | 7.46 | 7.51 | 135 | 12 | 320 | 44 | 269 | 19 | NA | 600 | 0.2 | 24.6 | 1400000 | Retaining wall for tapping of nearby nalla is broken
2021-09-29 | 32170 | 32.17 | 7.42 | 7.65 | 144 | 15 | 332 | 44 | 277 | 20 | NA | 500 | 0.3 | 24.8 | 1200000 | Retaining wall for tapping of nearby nalla is broken
2021-09-30 | 30110 | 30.11 | 7.49 | 7.72 | 138 | 13 | 328 | 40 | 268 | 18 | NA | 700 | 0.2 | 24.7 | 1300000 | Retaining wall for tapping of nearby nalla is broken
Average | 29337.6667 | 29.3377 | 7.3983 | 7.5317 | 140.9 | 13.1333 | 316.9333 | 41.4667 | 273.6333 | 20.4667 | NA | 606.6667 | 0.23333 | 24.2133 | 1340000
880.13
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 22790 | 22.79 | 7.25 | 7.41 | 132 | 11 | 280 | 36 | 254 | 17 |  | 500 | 0.2 | 23 | 1200000
Max | 33020 | 33.02 | 7.49 | 7.72 | 150 | 15 | 336 | 48 | 301 | 24 |  | 700 | 0.3 | 25.2 | 1500000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-09-01 | 7920 | 7.92 | 7.13 | 7.36 | 135 | 14 | 300 | 44 | 263 | 24 | NA | 400 | 0.3 | 22.16 | 1200000
2021-09-02 | 7950 | 7.95 | 7.24 | 7.49 | 140 | 15 | 308 | 40 | 248 | 22 | NA | 500 | 0.2 | 21.46 | 1400000
2021-09-03 | 7970 | 7.97 | 7.29 | 7.56 | 145 | 13 | 316 | 36 | 255 | 20 | NA | 600 | 0.2 | 20.58 | 1600000
2021-09-04 | 7980 | 7.98 | 7.16 | 7.64 | 138 | 14 | 304 | 40 | 268 | 21 | NA | 500 | 0.3 | 22.43 | 1700000
2021-09-05 | 7960 | 7.96 | 7.27 | 7.44 | 142 | 15 | 312 | 38 | 252 | 23 | NA | 400 | 0.3 | 21.24 | 1300000
2021-09-06 | 7920 | 7.92 | 7.33 | 7.72 | 136 | 14 | 296 | 34 | 261 | 20 | NA | 500 | 0.2 | 23.11 | 1400000
2021-09-07 | 7950 | 7.95 | 7.18 | 7.53 | 140 | 15 | 308 | 40 | 240 | 22 | NA | 600 | 0.2 | 22.37 | 1600000
2021-09-08 | 7930 | 7.93 | 7.11 | 7.32 | 145 | 13 | 320 | 36 | 256 | 20 | NA | 500 | 0.3 | 21.91 | 1300000
2021-09-09 | 7900 | 7.9 | 7.26 | 7.61 | 138 | 14 | 310 | 32 | 264 | 19 | NA | 400 | 0.2 | 22.18 | 1700000
2021-09-10 | 7970 | 7.97 | 7.15 | 7.49 | 130 | 15 | 300 | 36 | 253 | 21 | NA | 500 | 0.2 | 22.67 | 1400000
2021-09-11 | 7940 | 7.94 | 7.22 | 7.58 | 135 | 16 | 316 | 40 | 260 | 23 | NA | 600 | 0.3 | 20.54 | 1600000
2021-09-12 | 7960 | 7.96 | 7.17 | 7.65 | 132 | 14 | 304 | 36 | 242 | 20 | NA | 500 | 0.2 | 21.32 | 1200000
2021-09-13 | 7980 | 7.98 | 7.21 | 7.77 | 140 | 15 | 312 | 40 | 258 | 22 | NA | 400 | 0.2 | 22.29 | 1400000
2021-09-14 | 7890 | 7.89 | 7.25 | 7.66 | 136 | 13 | 306 | 32 | 244 | 24 | NA | 500 | 0.2 | 21.47 | 1300000
2021-09-15 | 7950 | 7.95 | 7.31 | 7.52 | 130 | 15 | 296 | 38 | 257 | 21 | NA | 600 | 0.3 | 22.34 | 1600000
2021-09-16 | 7790 | 7.79 | 7.14 | 7.41 | 135 | 14 | 308 | 42 | 263 | 23 | NA | 400 | 0.3 | 21.74 | 1400000
2021-09-17 | 7820 | 7.82 | 7.27 | 7.62 | 132 | 13 | 302 | 36 | 272 | 20 | NA | 500 | 0.2 | 23.19 | 1300000
2021-09-18 | 7750 | 7.75 | 7.22 | 7.43 | 138 | 15 | 310 | 40 | 266 | 22 | NA | 400 | 0.3 | 22.54 | 1400000
2021-09-19 | 7820 | 7.82 | 7.12 | 7.56 | 142 | 13 | 316 | 38 | 276 | 23 | NA | 500 | 0.2 | 21.44 | 1600000
2021-09-20 | 7890 | 7.89 | 7.38 | 7.71 | 146 | 16 | 324 | 44 | 258 | 21 | NA | 600 | 0.2 | 22.84 | 1700000
2021-09-21 | 7910 | 7.91 | 7.27 | 7.65 | 140 | 14 | 312 | 40 | 241 | 22 | NA | 400 | 0.2 | 20.67 | 1100000
2021-09-22 | 7950 | 7.95 | 7.21 | 7.53 | 135 | 13 | 304 | 36 | 252 | 20 | NA | 700 | 0.3 | 21.76 | 1300000
2021-09-23 | 7810 | 7.81 | 7.16 | 7.68 | 130 | 15 | 292 | 44 | 268 | 24 | NA | 500 | 0.2 | 23.18 | 1600000
2021-09-24 | 7860 | 7.86 | 7.25 | 7.52 | 136 | 13 | 308 | 38 | 248 | 21 | NA | 600 | 0.3 | 22.55 | 1200000
2021-09-25 | 7500 | 7.5 | 7.13 | 7.62 | 145 | 15 | 320 | 42 | 270 | 23 | NA | 400 | 0.2 | 20.13 | 1400000
2021-09-26 | 7680 | 7.68 | 7.32 | 7.48 | 140 | 14 | 300 | 36 | 250 | 25 | NA | 500 | 0.2 | 21.33 | 1300000
2021-09-27 | 7720 | 7.72 | 7.26 | 7.59 | 132 | 16 | 316 | 40 | 265 | 22 | NA | 700 | 0.3 | 22.79 | 1600000
2021-09-28 | 7880 | 7.88 | 7.14 | 7.36 | 130 | 17 | 296 | 44 | 242 | 24 | NA | 400 | 0.2 | 20.48 | 1400000
2021-09-29 | 7660 | 7.66 | 7.23 | 7.48 | 138 | 14 | 312 | 36 | 256 | 21 | NA | 600 | 0.3 | 22.14 | 1700000
2021-09-30 | 7720 | 7.72 | 7.18 | 7.39 | 135 | 15 | 304 | 40 | 272 | 23 | NA | 500 | 0.2 | 23.2 | 1200000
Average | 7864.3333 | 7.8643 | 7.2187 | 7.5457 | 137.2 | 14.4 | 307.7333 | 38.6 | 257.3333 | 21.8667 | NA | 506.6667 | 0.24 | 21.935 | 1430000
235.93
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 7500 | 7.5 | 7.11 | 7.32 | 130 | 13 | 292 | 32 | 240 | 19 |  | 400 | 0.2 | 20.13 | 1100000
Max | 7980 | 7.98 | 7.38 | 7.77 | 146 | 17 | 324 | 44 | 276 | 25 |  | 700 | 0.3 | 23.2 | 1700000