## Naini I
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final BOD (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-08-01 | 107250 | 107.25 | 7.45 | 7.53 | 126 | 21 | 288 | 36 | 267 | 27 | NA | 700 | 0.2 | 22.7 | 1400000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availability is 100%
2021-08-02 | 85220 | 85.22 | 7.31 | 7.49 | 132 | 25 | 316 | 44 | 302 | 29 | NA | 600 | 0.2 | 22.7 | 1300000
2021-08-03 | 84140 | 84.14 | 7.43 | 7.51 | 129 | 24 | 304 | 40 | 291 | 26 | NA | 500 | 0.3 | 23.4 | 1200000
2021-08-04 | 88110 | 88.11 | 7.39 | 7.61 | 111 | 19 | 296 | 36 | 282 | 27 | NA | 700 | 0.2 | 24.4 | 1400000
2021-08-05 | 95190 | 95.19 | 7.28 | 7.43 | 120 | 21 | 308 | 44 | 281 | 30 | NA | 600 | 0.2 | 22.5 | 1300000
2021-08-06 | 91620 | 91.62 | 7.34 | 7.48 | 102 | 19 | 292 | 48 | 286 | 28 | NA | 700 | 0.3 | 24.8 | 1400000
2021-08-07 | 46630 | 46.63 | 7.4 | 7.53 | 96 | 17 | 284 | 40 | 274 | 32 | NA | 500 | 0.2 | 22.9 | 1200000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) STP was stopped around 2 PM as river water has come inside STP due to flood.
2021-08-08 | Plant is in shutdown due to flood | [14 empty] | 1) Plant was shut down as river water has come inside the STP due to flood. 2) Raw Sewage pumped from Gaughat MPS & Chacharnalla SPS were bypassed. 3) Electricity supply for the plant was cut off. 4) Equipment in Treated effluent pump house, Return sludge pump house, chlorination unit, mail MCC room, Solar panel room, Control panel room of DG, Gas holder, Panel room of 20 MLD stream were shutoff/dismantled as river water has reached these units.
2021-08-09
2021-08-10
2021-08-11
2021-08-12
2021-08-13
2021-08-14
2021-08-15
2021-08-16
2021-08-17
2021-08-18 | 18510 | 18.51 | 7.19 | 7.41 | 139 | 49 | 340 | 92 | 302 | 85 | NA | - | - | - | - | 1) Functioning of STP was restored on 18.08.2021 at 8 PM. 2) Reinstallation of chlorine unit was not started yet. 3) Sludge sampling was not done as sludge generation was not started and drying beds are wet due to flood. 4) KPIs are out of range due to new biomass generation in process units after restart of STP.
2021-08-19 | 75270 | 75.27 | 7.29 | 7.21 | 143 | 47 | 312 | 84 | 287 | 62 | NA | - | - | - | - | 1) Reinstallation of chlorine unit was not started yet. 2) Sludge sampling was not done as sludge generation was not started and drying beds are wet due to flood. 3) KPIs are out of range due to new biomass generation in process units after restart of STP.
2021-08-20 | 91760 | 91.76 | 7.33 | 7.41 | 136 | 45 | 304 | 96 | 284 | 72 | NA | - | - | - | -
2021-08-21 | 122880 | 122.88 | 7.28 | 7.43 | 133 | 38 | 296 | 92 | 278 | 76 | NA | - | - | - | - | 1) Reinstallation of chlorine unit was in progress. 2) Sludge sampling was not done as sludge generation was not started and drying beds are wet due to flood. 3) KPIs are out of range due to new biomass generation in process units after restart of STP.
2021-08-22 | 103980 | 103.98 | 7.31 | 7.39 | 129 | 41 | 304 | 88 | 286 | 74 | NA | - | - | - | -
2021-08-23 | 98620 | 98.62 | 7.33 | 7.42 | 136 | 45 | 320 | 92 | 294 | 76 | NA | - | - | - | -
2021-08-24 | 106980 | 106.98 | 7.44 | 7.49 | 143 | 42 | 328 | 76 | 302 | 68 | NA | - | - | - | -
2021-08-25 | 104180 | 104.18 | 7.39 | 7.46 | 139 | 39 | 324 | 60 | 288 | 53 | NA | 700 | 0.2 | - | 1400000 | 1) Reinstallation of chlorine unit is completed and unit is started. 2) Sludge sampling was started but testing of sludge concentration was not done as drying beds were wet due to flood. 3) KPIs are out of range due to new biomass generation in process units after restart of STP.
2021-08-26 | 100410 | 100.41 | 7.44 | 7.49 | 133 | 35 | 304 | 52 | 284 | 50 | NA | 600 | 0.3 | - | 1700000 | 1) Sludge sampling was started but testing of sludge concentration was not done as drying beds were wet due to flood. 2) KPIs are out of range due to new biomass generation in process units after restart of STP.
2021-08-27 | 102760 | 102.76 | 7.36 | 7.41 | 129 | 40 | 312 | 68 | 280 | 58 | NA | 500 | 0.2 | - | 1400000
2021-08-28 | 108860 | 108.86 | 7.53 | 7.62 | 136 | 44 | 324 | 64 | 296 | 59 | NA | 400 | 0.3 | 24.8 | 1700000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) KPIs are out of range due to new biomass generation in process units after restart of STP.
2021-08-29 | 102840 | 102.84 | 7.36 | 7.42 | 139 | 43 | 332 | 72 | 288 | 56 | NA | 600 | 0.2 | 24.9 | 1300000
2021-08-30 | 107540 | 107.54 | 7.41 | 7.51 | 133 | 41 | 328 | 68 | 302 | 54 | NA | 700 | 0.3 | 24.8 | 1100000
2021-08-31 | 94970 | 94.97 | 7.36 | 7.46 | 129 | 39 | 320 | 60 | 303 | 53 | NA | 500 | 0.2 | 24.1 | 1700000
Average | 92272.381 | 92.2724 | 7.3629 | 7.4624 | 129.1905 | 34.9524 | 311.2381 | 64.381 | 288.4286 | 52.1429 | NA | 592.8571 | 0.23571 | 23.8182 | 1392857.1429
1937.72
Source: | Logbook of Laboratory at Sewage Treatment Plant

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-08-01 | 94810 | 94.81 | 7.38 | 7.7 | 115 | 16 | 292 | 44 | 272 | 27 | NA | 700 | 0.2 | 21.48 | 1400000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2021-08-02 | 81800 | 81.8 | 7.35 | 7.68 | 120 | 15 | 272 | 40 | 284 | 25 | NA | 400 | 0.2 | 22.79 | 1300000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Inlet gate for Rajapur SPS is closed at 12:20 PM on 02.08.2021
2021-08-03 | 71460 | 71.46 | 7.5 | 7.65 | 130 | 14 | 312 | 40 | 278 | 28 | NA | 500 | 0.3 | 23.46 | 1400000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Rajapur SPS is in shutdown due to flood.
2021-08-04 | 70360 | 70.36 | 7.46 | 7.68 | 110 | 16 | 288 | 44 | 265 | 26 | NA | 600 | 0.2 | 21.52 | 1700000
2021-08-05 | 32050 | 32.05 | 7.47 | 7.65 | 105 | 15 | 272 | 36 | 232 | 24 | NA | 400 | 0.2 | 23.4 | 1100000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Rajapur SPS is in shutdown due to flood. 3) Mumfordganj SPS was shutdown at 9AM on 05.08.2021 due to flood and scour valve in rising main from Mumfordganj SPS to Rajapur STP was opened.
2021-08-06 | 4020 | 4.02 | Plant is in shutdown due to flood. | [12 empty] | 1) STP was shut down as percolation of water started inside STP from ground due to rise in river level because of flood. 2) Electricity supply was cut off and DG supply was started. 3) Water accumulated due to percolation and leakage from inlet gate was pumped regularly through flood pumping station. 4) Sludge was not removed from UASBs as all valve chambers were submereged in water.
2021-08-07 | 3470 | 3.47
2021-08-08 | 8590 | 8.59
2021-08-09 | 12650 | 12.65
2021-08-10 | 14790 | 14.79
2021-08-11 | 31630 | 31.63
2021-08-12 | 37370 | 37.37
2021-08-13 | 30160 | 30.16
2021-08-14 | 19510 | 19.51
2021-08-15 | 32500 | 32.5
2021-08-16 | 17890 | 17.89
2021-08-17 | 6710 | 6.71 | 7.5 | 7.64 | 100 | 23 | 272 | 60 | 210 | 32 | NA | 1200 | 0.4 | - | - | 1) Functioning of STP was restored in 17.08.2021. 2) Sludge sampling was not done as sludge generation was not started and drying beds are wet due to flood. 3) KPIs are out of range due to new biomass generation in process units after restart of STP. 4) Removal of sand bags from inlet pipe of Rajapur SPS is in progress.
2021-08-18 | 45040 | 45.04 | 7.48 | 7.7 | 105 | 22 | 288 | 52 | 252 | 30 | NA | 900 | 0.3 | - | - | 1) Functioning of STP was restored in 18.08.2021. 2) Sludge sampling was not done as sludge generation was not started and drying beds are wet due to flood. 3) KPIs are out of range due to new biomass generation in process units after restart of STP. 4) Mumforganj SPS was started on 18.08.2021 at 12:10 PM. 5) Removal of sand bags from inlet pipe of Rajapur SPS is in progress.
2021-08-19 | 76740 | 76.74 | 7.4 | 7.65 | 110 | 22 | 292 | 56 | 262 | 32 | NA | 900 | 0.4 | - | - | 1) Sludge sampling was not done as sludge generation was not started and drying beds are wet due to flood. 2) KPIs are out of range due to new biomass generation in process units after restart of STP. 3) Removal of sand bags from inlet pipe of Rajapur SPS is in progress.
2021-08-20 | 74640 | 74.64 | 7.42 | 7.68 | 120 | 20 | 304 | 52 | 278 | 29 | NA | 700 | 0.3 | - | -
2021-08-21 | 79950 | 79.95 | 7.45 | 7.65 | 125 | 18 | 296 | 48 | 262 | 27 | NA | 500 | 0.2 | - | - | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Removal of sand bags from inlet pipe of Rajapur SPS is in progress.
2021-08-22 | 75080 | 75.08 | 7.43 | 7.68 | 130 | 19 | 308 | 44 | 272 | 26 | NA | 600 | 0.3 | - | -
2021-08-23 | 85580 | 85.58 | 7.42 | 7.71 | 135 | 17 | 312 | 44 | 282 | 28 | NA | 500 | 0.2 | - | - | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Removal of sand bags from inlet pipe of Rajapur SPS is completed and SPS was running at full capacity.
2021-08-24 | 93620 | 93.62 | 7.43 | 7.75 | 115 | 18 | 304 | 48 | 284 | 25 | NA | 400 | 0.3 | 23.45 | 1300000 | 1) Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate. 2) Plant Availablity is 100%
2021-08-25 | 93390 | 93.39 | 7.4 | 7.69 | 120 | 19 | 312 | 44 | 272 | 27 | NA | 400 | 0.2 | 21.25 | 1400000
2021-08-26 | 81190 | 81.19 | 7.43 | 7.68 | 125 | 16 | 320 | 40 | 292 | 26 | NA | 700 | 0.3 | 21.54 | 1700000
2021-08-27 | 75730 | 75.73 | 7.38 | 7.7 | 130 | 18 | 328 | 48 | 310 | 28 | NA | 600 | 0.2 | 22.68 | 1400000
2021-08-28 | 78510 | 78.51 | 7.37 | 7.69 | 125 | 17 | 324 | 44 | 342 | 25 | NA | 700 | 0.2 | 23.32 | 1400000
2021-08-29 | 79080 | 79.08 | 7.4 | 7.71 | 135 | 17 | 320 | 40 | 305 | 27 | NA | 500 | 0.4 | 21.58 | 1300000
2021-08-30 | 76760 | 76.76 | 7.42 | 7.67 | 130 | 15 | 328 | 48 | 278 | 28 | NA | 700 | 0.2 | 22.74 | 1700000
2021-08-31 | 79890 | 79.89 | 7.38 | 7.69 | 125 | 18 | 316 | 40 | 262 | 26 | NA | 400 | 0.3 | 21.6 | 1300000
Average | 53708.7097 | 53.7087 | 7.4235 | 7.6825 | 120.5 | 17.75 | 303 | 45.6 | 274.7 | 27.3 | NA | 615 | 0.265 | 22.37 | 1415384.6154
1664.97
Source: | Logbook of Labarotory at Sewage Treament Plant