## Numayadahi
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-02-01 | 64260 | 64.26 | 7.15 | 7.8 | 140 | 15 | 328 | 40 | 244 | 28 | NA | 500 | 0.3 | 23.97 | 1400000
2022-02-02 | 67520 | 67.52 | 7.34 | 7.84 | 140 | 17 | 320 | 44 | 234 | 22 | NA | 400 | 0.3 | 24.41 | 1700000
2022-02-03 | 63900 | 63.9 | 7.2 | 7.82 | 130 | 15 | 316 | 36 | 268 | 28 | NA | 500 | 0.3 | 22.96 | 1300000
2022-02-04 | 62100 | 62.1 | 7.19 | 7.74 | 145 | 17 | 340 | 48 | 246 | 26 | NA | 700 | 0.3 | 25.12 | 1700000
2022-02-05 | 64210 | 64.21 | 7.22 | 7.64 | 135 | 15 | 328 | 40 | 248 | 28 | NA | 500 | 0.2 | 24.39 | 1300000
2022-02-06 | 65120 | 65.12 | 7.2 | 7.74 | 140 | 14 | 340 | 36 | 288 | 26 | NA | 400 | 0.3 | 24.13 | 1300000
2022-02-07 | 66010 | 66.01 | 7.25 | 7.68 | 145 | 16 | 344 | 36 | 256 | 24 | NA | 700 | 0.2 | 23.45 | 1700000
2022-02-08 | 64840 | 64.84 | 7.15 | 7.8 | 140 | 17 | 336 | 36 | 224 | 28 | NA | 500 | 0.2 | 24.95 | 1300000
2022-02-09 | 61310 | 61.31 | 7.2 | 7.64 | 135 | 14 | 320 | 40 | 248 | 24 | NA | 400 | 0.3 | 24.86 | 1400000
2022-02-10 | 60920 | 60.92 | 7.18 | 7.7 | 135 | 16 | 312 | 32 | 262 | 26 | NA | 400 | 0.3 | 23.93 | 1700000
2022-02-11 | 58900 | 58.9 | 7.27 | 7.56 | 130 | 15 | 308 | 36 | 230 | 26 | NA | 700 | 0.2 | 25.65 | 1300000
2022-02-12 | 57650 | 57.65 | 7.2 | 7.8 | 145 | 14 | 324 | 40 | 256 | 28 | NA | 500 | 0.3 | 25.59 | 1400000
2022-02-13 | 64320 | 64.32 | 7.24 | 7.84 | 130 | 16 | 320 | 44 | 294 | 24 | NA | 600 | 0.2 | 23.24 | 1100000
2022-02-14 | 65010 | 65.01 | 7.19 | 7.72 | 145 | 14 | 304 | 40 | 290 | 26 | NA | 400 | 0.2 | 23.35 | 1200000
2022-02-15 | 63890 | 63.89 | 7.28 | 7.78 | 135 | 12 | 364 | 32 | 246 | 25 | NA | 500 | 0.4 | 23.57 | 1300000
2022-02-16 | 64080 | 64.08 | 7.18 | 7.64 | 140 | 16 | 328 | 36 | 234 | 22 | NA | 700 | 0.3 | 23.11 | 1400000
2022-02-17 | 61770 | 61.77 | 7.2 | 7.74 | 135 | 18 | 344 | 40 | 250 | 28 | NA | 400 | 0.2 | 24.95 | 1400000
2022-02-18 | 62060 | 62.06 | 7.15 | 7.8 | 125 | 16 | 316 | 36 | 256 | 26 | NA | 700 | 0.2 | 24.73 | 1300000
2022-02-19 | 60850 | 60.85 | 7.22 | 7.7 | 145 | 17 | 324 | 40 | 272 | 28 | NA | 500 | 0.3 | 24.27 | 1300000
2022-02-20 | 60110 | 60.11 | 7.19 | 7.68 | 135 | 16 | 336 | 36 | 264 | 26 | NA | 400 | 0.2 | 24.47 | 1200000
2022-02-21 | 64150 | 64.15 | 7.19 | 7.72 | 150 | 14 | 320 | 40 | 228 | 22 | NA | 600 | 0.3 | 23.87 | 1100000
2022-02-22 | 62940 | 62.94 | 7.18 | 7.84 | 150 | 15 | 320 | 44 | 252 | 24 | NA | 400 | 0.3 | 24.22 | 1400000
2022-02-23 | 62620 | 62.62 | 7.2 | 7.7 | 145 | 13 | 336 | 40 | 246 | 26 | NA | 500 | 0.3 | 23.79 | 1300000
2022-02-24 | 63560 | 63.56 | 7.14 | 7.64 | 150 | 17 | 312 | 48 | 252 | 26 | NA | 700 | 0.3 | 25.77 | 1300000
2022-02-25 | 62890 | 62.89 | 7.16 | 7.7 | 135 | 14 | 304 | 36 | 296 | 24 | NA | 400 | 0.2 | 23.35 | 1400000
2022-02-26 | 62100 | 62.1 | 7.14 | 7.64 | 150 | 16 | 328 | 32 | 240 | 28 | NA | 700 | 0.3 | 24.22 | 1200000
2022-02-27 | 66110 | 66.11 | 7.21 | 7.69 | 145 | 17 | 312 | 32 | 250 | 26 | NA | 400 | 0.3 | 24.14 | 1400000
2022-02-28 | 63180 | 63.18 | 7.28 | 7.48 | 135 | 15 | 320 | 36 | 260 | 28 | NA | 700 | 0.3 | 25.6 | 1700000
Average | 63085 | 63.085 | 7.2036 | 7.7168 | 139.6429 | 15.3929 | 325.1429 | 38.4286 | 254.7857 | 25.8214 | #DIV/0! | 528.5714 | 0.26786 | 24.2879 | 1375000
1766.38
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 57650 | 57.65 | 7.14 | 7.48 | 125 | 12 | 304 | 32 | 224 | 22 |  | 400 | 0.2 | 22.96 | 1100000
Max | 67520 | 67.52 | 7.34 | 7.84 | 150 | 18 | 364 | 48 | 296 | 28 |  | 700 | 0.4 | 25.77 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-02-01 | 41430 | 41.43 | 7.29 | 7.56 | 163 | 23 | 348 | 44 | 297 | 38 | NA | 500 | 0.2 | 23.7 | 1100000
2022-02-02 | 38450 | 38.45 | 7.34 | 7.53 | 153 | 22 | 356 | 40 | 306 | 35 | NA | 700 | 0.3 | 24.9 | 1300000
2022-02-03 | 41320 | 41.32 | 7.26 | 7.58 | 159 | 26 | 360 | 44 | 313 | 39 | NA | 400 | 0.2 | 22.4 | 1400000
2022-02-04 | 41900 | 41.9 | 7.28 | 7.6 | 156 | 24 | 352 | 48 | 321 | 41 | NA | 600 | 0.3 | 24.2 | 1600000
2022-02-05 | 43270 | 43.27 | 7.3 | 7.57 | 163 | 25 | 364 | 44 | 324 | 40 | NA | 700 | 0.3 | 25 | 1100000
2022-02-06 | 40740 | 40.74 | 7.18 | 7.49 | 147 | 23 | 356 | 40 | 312 | 37 | NA | 500 | 0.2 | 23.9 | 1300000
2022-02-07 | 37520 | 37.52 | 7.33 | 7.61 | 153 | 26 | 344 | 36 | 293 | 32 | NA | 800 | 0.3 | 22.8 | 1200000
2022-02-08 | 37530 | 37.53 | 7.4 | 7.54 | 160 | 24 | 352 | 40 | 322 | 34 | NA | 600 | 0.2 | 24.2 | 1400000
2022-02-09 | 36550 | 36.55 | 7.35 | 7.47 | 146 | 21 | 360 | 44 | 308 | 36 | NA | 800 | 0.3 | 23 | 1100000
2022-02-10 | 38120 | 38.12 | 7.22 | 7.51 | 157 | 23 | 364 | 48 | 298 | 33 | NA | 700 | 0.2 | 25.2 | 1200000
2022-02-11 | 38820 | 38.82 | 7.37 | 7.55 | 153 | 25 | 360 | 40 | 311 | 35 | NA | 400 | 0.3 | 23.5 | 1300000
2022-02-12 | 39180 | 39.18 | 7.31 | 7.59 | 156 | 22 | 356 | 36 | 325 | 38 | NA | 500 | 0.3 | 24 | 1400000
2022-02-13 | 41350 | 41.35 | 7.27 | 7.48 | 162 | 27 | 368 | 44 | 329 | 40 | NA | 600 | 0.2 | 22.5 | 1600000
2022-02-14 | 37430 | 37.43 | 7.36 | 7.52 | 160 | 24 | 352 | 40 | 320 | 37 | NA | 700 | 0.3 | 24.2 | 1100000
2022-02-15 | 36260 | 36.26 | 7.4 | 7.56 | 154 | 23 | 344 | 32 | 305 | 31 | NA | 600 | 0.2 | 23.8 | 1700000
2022-02-16 | 36730 | 36.73 | 7.32 | 7.5 | 157 | 24 | 356 | 36 | 316 | 34 | NA | 800 | 0.2 | 25 | 1400000
2022-02-17 | 34620 | 34.62 | 7.35 | 7.51 | 146 | 21 | 352 | 32 | 314 | 30 | NA | 500 | 0.3 | 24.6 | 1300000
2022-02-18 | 35020 | 35.02 | 7.39 | 7.45 | 153 | 25 | 360 | 28 | 309 | 31 | NA | 700 | 0.2 | 25.1 | 1200000
2022-02-19 | 34370 | 34.37 | 7.38 | 7.48 | 159 | 22 | 364 | 32 | 312 | 28 | NA | 400 | 0.2 | 25.8 | 1600000
2022-02-20 | 34680 | 34.68 | 7.33 | 7.54 | 163 | 20 | 356 | 36 | 304 | 30 | NA | 600 | 0.3 | 24.2 | 1100000
2022-02-21 | 35700 | 35.7 | 7.36 | 7.6 | 156 | 23 | 348 | 40 | 319 | 33 | NA | 800 | 0.3 | 23.7 | 1300000
2022-02-22 | 33190 | 33.19 | 7.27 | 7.53 | 160 | 21 | 352 | 36 | 296 | 31 | NA | 500 | 0.2 | 22.6 | 1400000
2022-02-23 | 32600 | 32.6 | 7.41 | 7.58 | 153 | 24 | 344 | 32 | 301 | 29 | NA | 600 | 0.3 | 24.3 | 1300000
2022-02-24 | 34710 | 34.71 | 7.38 | 7.56 | 157 | 26 | 352 | 40 | 292 | 34 | NA | 700 | 0.2 | 21.9 | 1100000
2022-02-25 | 31420 | 31.42 | 7.24 | 7.61 | 144 | 22 | 364 | 36 | 315 | 30 | NA | 400 | 0.2 | 23.9 | 1400000
2022-02-26 | 33380 | 33.38 | 7.2 | 7.48 | 153 | 20 | 356 | 32 | 328 | 35 | NA | 500 | 0.3 | 22.1 | 1600000
2022-02-27 | 32120 | 32.12 | 7.37 | 7.5 | 159 | 23 | 348 | 40 | 305 | 34 | NA | 800 | 0.2 | 24.5 | 1200000
2022-02-28 | 30320 | 30.32 | 7.26 | 7.55 | 163 | 21 | 360 | 48 | 323 | 39 | NA | 600 | 0.3 | 24.1 | 1300000
Average | 36740.3571 | 36.7404 | 7.3186 | 7.5375 | 155.8929 | 23.2143 | 355.2857 | 38.8571 | 311.3571 | 34.4286 | NA | 607.1429 | 0.25 | 23.8964 | 1321428.5714
1028.73
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 30320 | 30.32 | 7.18 | 7.45 | 144 | 20 | 344 | 28 | 292 | 28 |  | 400 | 0.2 | 21.9 | 1100000
Max | 43270 | 43.27 | 7.41 | 7.61 | 163 | 27 | 368 | 48 | 329 | 41 |  | 800 | 0.3 | 25.8 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-02-01 | 28680 | 28.68 | 7.39 | 7.78 | 141 | 12 | 304 | 36 | 280 | 21 | NA | 700 | 0.2 | 22.74 | 1400000
2022-02-02 | 27120 | 27.12 | 7.34 | 7.69 | 147 | 14 | 312 | 40 | 284 | 22 | NA | 500 | 0.3 | 23.39 | 1200000
2022-02-03 | 29330 | 29.33 | 7.29 | 7.89 | 138 | 13 | 300 | 32 | 276 | 20 | NA | 400 | 0.2 | 23.16 | 1300000
2022-02-04 | 28570 | 28.57 | 7.37 | 7.74 | 144 | 12 | 312 | 36 | 269 | 21 | NA | 500 | 0.3 | 23.58 | 1400000
2022-02-05 | 29930 | 29.93 | 7.41 | 7.84 | 135 | 11 | 304 | 32 | 278 | 22 | NA | 600 | 0.2 | 23.08 | 1300000
2022-02-06 | 30070 | 30.07 | 7.26 | 7.73 | 141 | 13 | 316 | 36 | 265 | 20 | NA | 700 | 0.3 | 22.73 | 1400000
2022-02-07 | 28840 | 28.84 | 7.34 | 7.65 | 147 | 12 | 324 | 44 | 272 | 22 | NA | 400 | 0.2 | 22.94 | 1200000
2022-02-08 | 28510 | 28.51 | 7.29 | 7.69 | 140 | 13 | 308 | 40 | 268 | 21 | NA | 600 | 0.3 | 23.3 | 1300000
2022-02-09 | 26790 | 26.79 | 7.38 | 7.75 | 138 | 14 | 300 | 36 | 278 | 20 | NA | 500 | 0.2 | 23.04 | 1200000
2022-02-10 | 26850 | 26.85 | 7.31 | 7.7 | 132 | 11 | 312 | 32 | 284 | 19 | NA | 700 | 0.3 | 22.64 | 1400000
2022-02-11 | 27760 | 27.76 | 7.24 | 7.79 | 144 | 13 | 304 | 36 | 275 | 20 | NA | 500 | 0.2 | 23.16 | 1300000
2022-02-12 | 27890 | 27.89 | 7.34 | 7.66 | 135 | 12 | 316 | 40 | 268 | 22 | NA | 400 | 0.3 | 22.72 | 1200000
2022-02-13 | 28430 | 28.43 | 7.17 | 7.68 | 145 | 11 | 324 | 36 | 270 | 20 | NA | 600 | 0.2 | 21.44 | 1400000
2022-02-14 | 27020 | 27.02 | 7.28 | 7.59 | 138 | 13 | 308 | 32 | 277 | 21 | NA | 700 | 0.3 | 22.35 | 1300000
2022-02-15 | 28120 | 28.12 | 7.21 | 7.67 | 144 | 14 | 300 | 36 | 262 | 19 | NA | 500 | 0.2 | 23.17 | 1200000
2022-02-16 | 28400 | 28.4 | 7.32 | 7.75 | 150 | 13 | 312 | 40 | 282 | 20 | NA | 400 | 0.2 | 22.66 | 1400000
2022-02-17 | 27070 | 27.07 | 7.37 | 7.82 | 141 | 12 | 304 | 32 | 274 | 18 | NA | 700 | 0.3 | 22.8 | 1300000
2022-02-18 | 27630 | 27.63 | 7.26 | 7.63 | 147 | 14 | 316 | 36 | 286 | 21 | NA | 500 | 0.2 | 21.92 | 1200000
2022-02-19 | 28600 | 28.6 | 7.35 | 7.69 | 138 | 12 | 324 | 40 | 277 | 19 | NA | 600 | 0.3 | 23.2 | 1400000
2022-02-20 | 27510 | 27.51 | 7.29 | 7.74 | 144 | 13 | 312 | 36 | 268 | 20 | NA | 400 | 0.2 | 22.69 | 1200000
2022-02-21 | 28360 | 28.36 | 7.22 | 7.58 | 153 | 15 | 308 | 32 | 280 | 18 | NA | 500 | 0.2 | 22.18 | 1300000
2022-02-22 | 27520 | 27.52 | 7.32 | 7.66 | 147 | 13 | 316 | 44 | 273 | 21 | NA | 700 | 0.3 | 22.98 | 1400000
2022-02-23 | 28750 | 28.75 | 7.27 | 7.7 | 141 | 12 | 304 | 40 | 276 | 19 | NA | 600 | 0.2 | 21.88 | 1200000
2022-02-24 | 26560 | 26.56 | 7.38 | 7.62 | 144 | 13 | 312 | 36 | 263 | 20 | NA | 500 | 0.3 | 22.61 | 1300000
2022-02-25 | 29210 | 29.21 | 7.24 | 7.73 | 135 | 11 | 300 | 44 | 282 | 22 | NA | 400 | 0.2 | 23.09 | 1400000
2022-02-26 | 27730 | 27.73 | 7.31 | 7.66 | 138 | 13 | 320 | 32 | 275 | 19 | NA | 700 | 0.3 | 22.84 | 1300000
2022-02-27 | 28940 | 28.94 | 7.39 | 7.78 | 144 | 12 | 308 | 40 | 268 | 20 | NA | 500 | 0.2 | 22.55 | 1200000
2022-02-28 | 26420 | 26.42 | 7.27 | 7.59 | 147 | 14 | 316 | 36 | 258 | 18 | NA | 600 | 0.3 | 22.12 | 1400000
Average | 28093.2143 | 28.0932 | 7.3075 | 7.7071 | 142.0714 | 12.6786 | 310.5714 | 36.8571 | 273.8571 | 20.1786 | NA | 550 | 0.24643 | 22.7486 | 1303571.4286
786.61
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 26420 | 26.42 | 7.17 | 7.58 | 132 | 11 | 300 | 32 | 258 | 18 |  | 400 | 0.2 | 21.44 | 1200000
Max | 30070 | 30.07 | 7.41 | 7.89 | 153 | 15 | 324 | 44 | 286 | 22 |  | 700 | 0.3 | 23.58 | 1400000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-02-01 | 13030 | 13.03 | 7.13 | 7.51 | 138 | 13 | 296 | 36 | 259 | 22 | NA | 600 | 0.2 | 22.26 | 1400000
2022-02-02 | 11690 | 11.69 | 7.25 | 7.63 | 144 | 14 | 312 | 32 | 241 | 20 | NA | 500 | 0.3 | 20.66 | 1300000
2022-02-03 | 12680 | 12.68 | 7.16 | 7.44 | 150 | 16 | 320 | 40 | 261 | 23 | NA | 700 | 0.2 | 21.38 | 1400000
2022-02-04 | 12010 | 12.01 | 7.31 | 7.56 | 140 | 15 | 304 | 36 | 273 | 21 | NA | 500 | 0.3 | 22.51 | 1600000
2022-02-05 | 11270 | 11.27 | 7.42 | 7.74 | 145 | 16 | 316 | 40 | 284 | 23 | NA | 600 | 0.2 | 23.16 | 1300000
2022-02-06 | 11010 | 11.01 | 7.36 | 7.67 | 150 | 14 | 324 | 36 | 266 | 24 | NA | 500 | 0.3 | 21.73 | 1200000
2022-02-07 | 10980 | 10.98 | 7.18 | 7.48 | 140 | 15 | 308 | 44 | 258 | 22 | NA | 400 | 0.3 | 22.15 | 1400000
2022-02-08 | 12370 | 12.37 | 7.22 | 7.53 | 146 | 14 | 320 | 40 | 244 | 21 | NA | 500 | 0.2 | 22.58 | 1300000
2022-02-09 | 12180 | 12.18 | 7.11 | 7.62 | 138 | 15 | 304 | 44 | 260 | 24 | NA | 600 | 0.3 | 21.46 | 1600000
2022-02-10 | 11000 | 11 | 7.31 | 7.76 | 142 | 13 | 312 | 36 | 274 | 22 | NA | 500 | 0.2 | 20.87 | 1400000
2022-02-11 | 11450 | 11.45 | 7.15 | 7.43 | 147 | 14 | 300 | 40 | 253 | 23 | NA | 700 | 0.2 | 21.29 | 1300000
2022-02-12 | 11760 | 11.76 | 7.17 | 7.57 | 150 | 13 | 316 | 36 | 262 | 20 | NA | 600 | 0.3 | 22.3 | 1400000
2022-02-13 | 11960 | 11.96 | 7.29 | 7.66 | 155 | 14 | 324 | 32 | 276 | 18 | NA | 500 | 0.2 | 20.54 | 1600000
2022-02-14 | 12310 | 12.31 | 7.38 | 7.81 | 140 | 13 | 312 | 36 | 268 | 21 | NA | 400 | 0.3 | 21.63 | 1300000
2022-02-15 | 11980 | 11.98 | 7.33 | 7.75 | 145 | 15 | 320 | 40 | 255 | 23 | NA | 500 | 0.3 | 22.13 | 1400000
2022-02-16 | 12650 | 12.65 | 7.29 | 7.68 | 138 | 14 | 308 | 36 | 272 | 22 | NA | 600 | 0.2 | 22.73 | 1300000
2022-02-17 | 12780 | 12.78 | 7.18 | 7.49 | 142 | 15 | 312 | 40 | 265 | 24 | NA | 500 | 0.2 | 21.53 | 1600000
2022-02-18 | 12000 | 12 | 7.26 | 7.63 | 150 | 13 | 324 | 36 | 280 | 23 | NA | 700 | 0.3 | 20.83 | 1400000
2022-02-19 | 12960 | 12.96 | 7.37 | 7.78 | 136 | 14 | 308 | 40 | 269 | 21 | NA | 500 | 0.2 | 22.5 | 1300000
2022-02-20 | 12470 | 12.47 | 7.22 | 7.58 | 145 | 15 | 316 | 44 | 277 | 23 | NA | 600 | 0.3 | 21.68 | 1400000
2022-02-21 | 12580 | 12.58 | 7.19 | 7.41 | 155 | 14 | 328 | 38 | 257 | 19 | NA | 500 | 0.2 | 22.18 | 1200000
2022-02-22 | 11810 | 11.81 | 7.27 | 7.51 | 148 | 13 | 304 | 36 | 268 | 20 | NA | 400 | 0.2 | 22.76 | 1400000
2022-02-23 | 11090 | 11.09 | 7.16 | 7.62 | 152 | 15 | 312 | 40 | 253 | 22 | NA | 600 | 0.3 | 21.4 | 1600000
2022-02-24 | 10910 | 10.91 | 7.23 | 7.57 | 155 | 13 | 320 | 36 | 266 | 21 | NA | 500 | 0.2 | 22.36 | 1400000
2022-02-25 | 12470 | 12.47 | 7.31 | 7.66 | 142 | 14 | 308 | 40 | 274 | 23 | NA | 700 | 0.3 | 20.56 | 1600000
2022-02-26 | 12120 | 12.12 | 7.24 | 7.78 | 138 | 13 | 300 | 32 | 255 | 22 | NA | 600 | 0.2 | 21.24 | 1300000
2022-02-27 | 12260 | 12.26 | 7.18 | 7.53 | 144 | 14 | 316 | 36 | 261 | 20 | NA | 400 | 0.2 | 22.11 | 1400000
2022-02-28 | 12340 | 12.34 | 7.33 | 7.71 | 150 | 16 | 324 | 40 | 270 | 19 | NA | 500 | 0.3 | 23.18 | 1600000
Average | 12004.2857 | 12.0043 | 7.25 | 7.6111 | 145.1786 | 14.1786 | 313.1429 | 37.9286 | 264.3214 | 21.6429 | NA | 542.8571 | 0.24643 | 21.8468 | 1407142.8571
336.12
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 10910 | 10.91 | 7.11 | 7.41 | 136 | 13 | 296 | 32 | 241 | 18 |  | 400 | 0.2 | 20.54 | 1200000
Max | 13030 | 13.03 | 7.42 | 7.81 | 155 | 16 | 328 | 44 | 284 | 24 |  | 700 | 0.3 | 23.18 | 1600000