## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-04-01 | 60820 | 60.82 | 7.14 | 7.68 | 135 | 14 | 344 | 36 | 282 | 24 | NA | 500 | 0.3 | 24.04 | 1300000
2023-04-02 | 62150 | 62.15 | 7.18 | 7.66 | 145 | 16 | 324 | 40 | 293 | 24 | NA | 400 | 0.2 | 23.5 | 1700000
2023-04-03 | 57370 | 57.37 | 7.23 | 7.74 | 140 | 15 | 328 | 40 | 288 | 25 | NA | 700 | 0.2 | 23.69 | 1400000
2023-04-04 | 58080 | 58.08 | 7.26 | 7.72 | 135 | 14 | 312 | 36 | 296 | 27 | NA | 600 | 0.3 | 24.47 | 1300000
2023-04-05 | 57280 | 57.28 | 7.28 | 7.76 | 130 | 14 | 320 | 40 | 301 | 26 | NA | 500 | 0.2 | 23.44 | 1400000
2023-04-06 | 62780 | 62.78 | 7.22 | 7.69 | 135 | 13 | 324 | 36 | 298 | 25 | NA | 400 | 0.3 | 23.66 | 1300000
2023-04-07 | 61200 | 61.2 | 7.27 | 7.74 | 145 | 17 | 336 | 44 | 291 | 27 | NA | 700 | 0.3 | 24.82 | 1400000
2023-04-08 | 61270 | 61.27 | 7.23 | 7.72 | 130 | 14 | 308 | 40 | 286 | 24 | NA | 600 | 0.2 | 23.21 | 1700000
2023-04-09 | 61120 | 61.12 | 7.26 | 7.78 | 150 | 13 | 328 | 40 | 301 | 25 | NA | 400 | 0.3 | 24.23 | 1400000
2023-04-10 | 61780 | 61.78 | 7.24 | 7.68 | 145 | 15 | 320 | 36 | 298 | 26 | NA | 700 | 0.2 | 23.57 | 1300000
2023-04-11 | 62050 | 62.05 | 7.18 | 7.71 | 150 | 16 | 328 | 44 | 291 | 24 | NA | 500 | 0.3 | 23.55 | 1400000
2023-04-12 | 60030 | 60.03 | 7.29 | 7.78 | 135 | 12 | 316 | 40 | 296 | 26 | NA | 600 | 0.3 | 23.86 | 1700000
2023-04-13 | 63350 | 63.35 | 7.24 | 7.7 | 140 | 15 | 312 | 40 | 297 | 28 | NA | 700 | 0.2 | 23.22 | 1400000
2023-04-14 | 59150 | 59.15 | 7.26 | 7.73 | 150 | 16 | 320 | 36 | 286 | 23 | NA | 600 | 0.3 | 24.18 | 1300000
2023-04-15 | 60350 | 60.35 | 7.14 | 7.76 | 145 | 18 | 360 | 40 | 280 | 28 | NA | 500 | 0.3 | 22.53 | 1400000
2023-04-16 | 60570 | 60.57 | 7.12 | 7.7 | 150 | 19 | 320 | 48 | 268 | 26 | NA | 600 | 0.3 | 24.79 | 1700000
2023-04-17 | 63110 | 63.11 | 7.17 | 7.8 | 135 | 16 | 312 | 40 | 284 | 25 | NA | 400 | 0.3 | 24.16 | 1400000
2023-04-18 | 60830 | 60.83 | 7.28 | 7.64 | 145 | 15 | 328 | 36 | 284 | 24 | NA | 500 | 0.2 | 22.59 | 1300000
2023-04-19 | 63620 | 63.62 | 7.28 | 7.85 | 130 | 13 | 316 | 40 | 292 | 26 | NA | 400 | 0.3 | 24.79 | 1700000
2023-04-20 | 58930 | 58.93 | 7.22 | 7.76 | 135 | 15 | 312 | 36 | 306 | 28 | NA | 600 | 0.3 | 24.35 | 1400000
2023-04-21 | 61920 | 61.92 | 7.26 | 7.74 | 130 | 14 | 308 | 40 | 298 | 26 | NA | 400 | 0.2 | 23.76 | 1300000
2023-04-22 | 61950 | 61.95 | 7.42 | 7.78 | 145 | 17 | 324 | 44 | 302 | 28 | NA | 700 | 0.3 | 23.22 | 1400000
2023-04-23 | 57900 | 57.9 | 7.52 | 7.71 | 140 | 18 | 316 | 40 | 299 | 26 | NA | 500 | 0.3 | 24.47 | 1400000
2023-04-24 | 58270 | 58.27 | 7.58 | 7.81 | 130 | 14 | 312 | 36 | 305 | 24 | NA | 400 | 0.2 | 23.57 | 1700000
2023-04-25 | 61170 | 61.17 | 7.37 | 7.76 | 145 | 15 | 328 | 44 | 296 | 26 | NA | 600 | 0.3 | 24.82 | 1300000
2023-04-26 | 60670 | 60.67 | 7.42 | 7.8 | 135 | 14 | 308 | 40 | 288 | 25 | NA | 500 | 0.2 | 23.69 | 1400000
2023-04-27 | 60250 | 60.25 | 7.46 | 7.77 | 145 | 13 | 316 | 40 | 294 | 26 | NA | 700 | 0.3 | 23.5 | 1300000
2023-04-28 | 58630 | 58.63 | 7.36 | 7.72 | 140 | 14 | 324 | 36 | 276 | 28 | NA | 400 | 0.3 | 24.26 | 1400000
2023-04-29 | 59170 | 59.17 | 7.56 | 7.82 | 130 | 15 | 320 | 40 | 286 | 26 | NA | 600 | 0.2 | 24.23 | 1700000
2023-04-30 | 62180 | 62.18 | 7.44 | 7.76 | 150 | 14 | 312 | 40 | 295 | 25 | NA | 500 | 0.3 | 23.64 | 1300000
Average | 60598.3333 | 60.5983 | 7.296 | 7.7423 | 139.8333 | 14.9333 | 321.2 | 39.6 | 291.9 | 25.7 | NA | 540 | 0.26333 | 23.8603 | 1436666.6667
1817.95
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 57280 | 57.28 | 7.12 | 7.64 | 130 | 12 | 308 | 36 | 268 | 23 |  | 400 | 0.2 | 22.53 | 1300000
Max | 63620 | 63.62 | 7.58 | 7.85 | 150 | 19 | 360 | 48 | 306 | 28 |  | 700 | 0.3 | 24.82 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-04-01 | 41020 | 41.02 | 7.39 | 7.41 | 160 | 26 | 360 | 40 | 306 | 35 | NA | 400 | 0.3 | 24.4 | 1200000
2023-04-02 | 37410 | 37.41 | 7.37 | 7.4 | 165 | 28 | 364 | 40 | 309 | 37 | NA | 600 | 0.3 | 24.8 | 1400000
2023-04-03 | 36370 | 36.37 | 7.29 | 7.3 | 155 | 24 | 356 | 44 | 311 | 38 | NA | 800 | 0.2 | 23.9 | 1700000
2023-04-04 | 35810 | 35.81 | 7.01 | 7.15 | 160 | 27 | 360 | 40 | 320 | 40 | NA | 700 | 0.3 | 24.6 | 1300000
2023-04-05 | 36520 | 36.52 | 7.27 | 7.32 | 165 | 25 | 364 | 44 | 298 | 37 | NA | 500 | 0.2 | 24.2 | 1200000
2023-04-06 | 37230 | 37.23 | 7.51 | 7.58 | 155 | 28 | 356 | 44 | 290 | 38 | NA | 600 | 0.2 | 25.3 | 1400000
2023-04-07 | 36400 | 36.4 | 7.48 | 7.52 | 160 | 29 | 360 | 44 | 310 | 40 | NA | 800 | 0.3 | 24.2 | 1400000
2023-04-08 | 34820 | 34.82 | 7.53 | 7.59 | 165 | 26 | 364 | 40 | 308 | 37 | NA | 700 | 0.2 | 23.8 | 1700000
2023-04-09 | 37650 | 37.65 | 7.51 | 7.53 | 155 | 28 | 356 | 40 | 304 | 39 | NA | 600 | 0.3 | 24.7 | 1700000
2023-04-10 | 35780 | 35.78 | 7.54 | 7.58 | 160 | 27 | 360 | 44 | 302 | 42 | NA | 500 | 0.3 | 23.7 | 1400000
2023-04-11 | 36020 | 36.02 | 7.53 | 7.55 | 165 | 26 | 368 | 40 | 307 | 37 | NA | 700 | 0.2 | 23.8 | 1700000
2023-04-12 | 35580 | 35.58 | 7.49 | 7.52 | 160 | 28 | 356 | 44 | 303 | 40 | NA | 400 | 0.3 | 25.2 | 1200000
2023-04-13 | 34610 | 34.61 | 7.52 | 7.54 | 165 | 26 | 360 | 48 | 295 | 42 | NA | 500 | 0.2 | 24.8 | 1300000
2023-04-14 | 37040 | 37.04 | 7.55 | 7.62 | 150 | 24 | 356 | 44 | 298 | 39 | NA | 700 | 0.3 | 24.5 | 1400000
2023-04-15 | 35240 | 35.24 | 7.49 | 7.69 | 155 | 25 | 364 | 40 | 304 | 36 | NA | 600 | 0.2 | 25.3 | 1400000
2023-04-16 | 36980 | 36.98 | 7.54 | 7.58 | 160 | 27 | 356 | 44 | 295 | 42 | NA | 800 | 0.3 | 23.8 | 1700000
2023-04-17 | 36150 | 36.15 | 7.49 | 7.65 | 155 | 24 | 364 | 40 | 298 | 39 | NA | 500 | 0.2 | 24.6 | 1200000
2023-04-18 | 34860 | 34.86 | 7.52 | 7.62 | 160 | 26 | 360 | 44 | 305 | 43 | NA | 600 | 0.3 | 24.8 | 1300000
2023-04-19 | 33920 | 33.92 | 7.56 | 7.67 | 155 | 27 | 356 | 44 | 307 | 44 | NA | 400 | 0.3 | 25.3 | 1100000
2023-04-20 | 35260 | 35.26 | 7.52 | 7.58 | 160 | 23 | 360 | 48 | 302 | 46 | NA | 700 | 0.2 | 24.7 | 1400000
2023-04-21 | 34220 | 34.22 | 7.4 | 7.79 | 155 | 24 | 352 | 44 | 327 | 38 | NA | 500 | 0.3 | 24.1 | 1400000
2023-04-22 | 36500 | 36.5 | 7.46 | 7.68 | 160 | 24 | 360 | 44 | 314 | 39 | NA | 600 | 0.2 | 23.8 | 1300000
2023-04-23 | 32410 | 32.41 | 7.54 | 7.45 | 150 | 22 | 352 | 40 | 318 | 35 | NA | 400 | 0.2 | 24.5 | 1300000
2023-04-24 | 34020 | 34.02 | 7.43 | 7.49 | 155 | 25 | 364 | 40 | 308 | 37 | NA | 700 | 0.3 | 25.3 | 1400000
2023-04-25 | 35340 | 35.34 | 7.51 | 7.55 | 160 | 26 | 360 | 44 | 324 | 39 | NA | 800 | 0.3 | 24.8 | 1700000
2023-04-26 | 34240 | 34.24 | 7.46 | 7.57 | 155 | 24 | 352 | 40 | 304 | 42 | NA | 500 | 0.2 | 23.7 | 1200000
2023-04-27 | 36600 | 36.6 | 7.52 | 7.11 | 165 | 26 | 360 | 44 | 298 | 38 | NA | 600 | 0.3 | 24.6 | 1300000
2023-04-28 | 36580 | 36.58 | 7.37 | 7.53 | 160 | 25 | 348 | 36 | 289 | 31 | NA | 700 | 0.2 | 25.2 | 1100000
2023-04-29 | 35600 | 35.6 | 7.33 | 7.56 | 155 | 24 | 352 | 36 | 296 | 28 | NA | 500 | 0.2 | 24.9 | 1400000
2023-04-30 | 36980 | 36.98 | 7.35 | 7.48 | 160 | 26 | 344 | 40 | 332 | 30 | NA | 800 | 0.3 | 24.3 | 1700000
Average | 35905.3333 | 35.9053 | 7.4493 | 7.5203 | 158.6667 | 25.6667 | 358.1333 | 42.1333 | 306.0667 | 38.2667 | NA | 606.6667 | 0.25333 | 24.52 | 1396666.6667
1077.16
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 32410 | 32.41 | 7.01 | 7.11 | 150 | 22 | 344 | 36 | 289 | 28 |  | 400 | 0.2 | 23.7 | 1100000
Max | 41020 | 41.02 | 7.56 | 7.79 | 165 | 29 | 368 | 48 | 332 | 46 |  | 800 | 0.3 | 25.3 | 1700000

## Kodra
kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-04-01 | 30470 | 30.47 | 7.21 | 7.45 | 140 | 14 | 312 | 40 | 263 | 22 | NA | 400 | 0.3 | 23.45 | 1400000
2023-04-02 | 28720 | 28.72 | 7.18 | 7.51 | 145 | 16 | 320 | 44 | 270 | 28 | NA | 600 | 0.2 | 24.19 | 1300000
2023-04-03 | 28320 | 28.32 | 7.23 | 7.52 | 135 | 17 | 308 | 40 | 283 | 25 | NA | 500 | 0.2 | 23.63 | 1700000
2023-04-04 | 28080 | 28.08 | 7.26 | 7.55 | 140 | 14 | 316 | 44 | 276 | 24 | NA | 700 | 0.3 | 24.31 | 1200000
2023-04-05 | 27510 | 27.51 | 7.19 | 7.48 | 130 | 13 | 304 | 36 | 280 | 22 | NA | 500 | 0.2 | 23.29 | 1200000
2023-04-06 | 28600 | 28.6 | 7.25 | 7.53 | 145 | 15 | 320 | 40 | 268 | 23 | NA | 400 | 0.2 | 22.48 | 1400000
2023-04-07 | 28460 | 28.46 | 7.2 | 7.47 | 140 | 16 | 312 | 44 | 273 | 21 | NA | 600 | 0.3 | 23.11 | 1300000
2023-04-08 | 27170 | 27.17 | 7.26 | 7.5 | 135 | 13 | 308 | 40 | 284 | 28 | NA | 500 | 0.2 | 24.18 | 1200000
2023-04-09 | 29510 | 29.51 | 7.22 | 7.49 | 150 | 14 | 324 | 44 | 279 | 23 | NA | 700 | 0.2 | 24.35 | 1700000
2023-04-10 | 27950 | 27.95 | 7.28 | 7.51 | 145 | 15 | 316 | 40 | 265 | 24 | NA | 600 | 0.3 | 23.36 | 1300000
2023-04-11 | 28640 | 28.64 | 7.24 | 7.54 | 140 | 13 | 312 | 36 | 270 | 23 | NA | 400 | 0.3 | 22.98 | 1200000
2023-04-12 | 28520 | 28.52 | 7.21 | 7.46 | 145 | 14 | 320 | 40 | 263 | 22 | NA | 500 | 0.2 | 23.49 | 1400000
2023-04-13 | 28050 | 28.05 | 7.25 | 7.49 | 155 | 17 | 328 | 48 | 277 | 26 | NA | 400 | 0.2 | 24.16 | 1300000
2023-04-14 | 29190 | 29.19 | 7.27 | 7.55 | 145 | 15 | 316 | 40 | 284 | 22 | NA | 600 | 0.3 | 23.56 | 1700000
2023-04-15 | 28410 | 28.41 | 7.23 | 7.53 | 130 | 13 | 308 | 36 | 266 | 24 | NA | 500 | 0.2 | 24.63 | 1400000
2023-04-16 | 29030 | 29.03 | 7.2 | 7.56 | 135 | 14 | 312 | 40 | 274 | 25 | NA | 700 | 0.3 | 22.5 | 1200000
2023-04-17 | 28070 | 28.07 | 7.18 | 7.48 | 140 | 13 | 304 | 36 | 281 | 23 | NA | 600 | 0.2 | 24.09 | 1300000
2023-04-18 | 26980 | 26.98 | 7.24 | 7.52 | 150 | 14 | 316 | 40 | 258 | 21 | NA | 400 | 0.3 | 23.37 | 1700000
2023-04-19 | 28010 | 28.01 | 7.28 | 7.45 | 155 | 13 | 324 | 36 | 270 | 24 | NA | 500 | 0.2 | 23.59 | 1400000
2023-04-20 | 28140 | 28.14 | 7.22 | 7.5 | 145 | 12 | 312 | 36 | 276 | 22 | NA | 600 | 0.2 | 24.29 | 1300000
2023-04-21 | 29750 | 29.75 | 7.26 | 7.49 | 140 | 13 | 320 | 40 | 283 | 21 | NA | 500 | 0.3 | 23.18 | 1200000
2023-04-22 | 29780 | 29.78 | 7.21 | 7.54 | 135 | 12 | 308 | 36 | 261 | 22 | NA | 400 | 0.2 | 24.33 | 1400000
2023-04-23 | 28650 | 28.65 | 7.24 | 7.51 | 130 | 13 | 300 | 36 | 273 | 21 | NA | 600 | 0.2 | 23.41 | 1300000
2023-04-24 | 27880 | 27.88 | 7.22 | 7.44 | 140 | 14 | 312 | 40 | 286 | 27 | NA | 700 | 0.3 | 22.71 | 1200000
2023-04-25 | 29710 | 29.71 | 7.25 | 7.47 | 130 | 15 | 304 | 44 | 279 | 22 | NA | 500 | 0.3 | 23.63 | 1300000
2023-04-26 | 27850 | 27.85 | 7.2 | 7.48 | 145 | 16 | 316 | 40 | 269 | 23 | NA | 600 | 0.2 | 24.08 | 1700000
2023-04-27 | 28290 | 28.29 | 7.23 | 7.53 | 150 | 11 | 320 | 36 | 275 | 21 | NA | 700 | 0.3 | 24.29 | 1400000
2023-04-28 | 29410 | 29.41 | 7.19 | 7.49 | 140 | 12 | 312 | 32 | 284 | 20 | NA | 500 | 0.3 | 23.31 | 1300000
2023-04-29 | 28870 | 28.87 | 7.24 | 7.52 | 130 | 11 | 300 | 36 | 278 | 22 | NA | 400 | 0.2 | 24.19 | 1400000
2023-04-30 | 30830 | 30.83 | 7.21 | 7.43 | 135 | 13 | 308 | 40 | 265 | 20 | NA | 600 | 0.2 | 23.55 | 1200000
Average | 28628.3333 | 28.6283 | 7.2283 | 7.4997 | 140.6667 | 13.8333 | 313.0667 | 39.3333 | 273.7667 | 23.0333 | NA | 540 | 0.24333 | 23.6563 | 1366666.6667
858.85
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 26980 | 26.98 | 7.18 | 7.43 | 130 | 11 | 300 | 32 | 258 | 20 |  | 400 | 0.2 | 22.48 | 1200000
Max | 30830 | 30.83 | 7.28 | 7.56 | 155 | 17 | 328 | 48 | 286 | 28 |  | 700 | 0.3 | 24.63 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-04-01 | 12690 | 12.69 | 7.3 | 7.44 | 135 | 17 | 308 | 44 | 297 | 24 | NA | 500 | 0.3 | 22.29 | 1300000
2023-04-02 | 13290 | 13.29 | 7.34 | 7.43 | 140 | 15 | 312 | 48 | 256 | 22 | NA | 400 | 0.3 | 22.82 | 1200000
2023-04-03 | 12770 | 12.77 | 7.36 | 7.47 | 130 | 18 | 304 | 40 | 284 | 23 | NA | 500 | 0.3 | 23.2 | 1400000
2023-04-04 | 13550 | 13.35 | 7.38 | 7.49 | 145 | 17 | 314 | 44 | 274 | 25 | NA | 600 | 0.2 | 23.86 | 1700000
2023-04-05 | 12750 | 12.75 | 7.35 | 7.51 | 140 | 15 | 316 | 48 | 289 | 26 | NA | 400 | 0.3 | 23.59 | 1300000
2023-04-06 | 12860 | 12.86 | 7.37 | 7.49 | 130 | 16 | 324 | 44 | 276 | 27 | NA | 500 | 0.2 | 22.56 | 1200000
2023-04-07 | 13130 | 13.13 | 7.32 | 7.53 | 150 | 15 | 312 | 40 | 265 | 24 | NA | 700 | 0.2 | 23.39 | 1400000
2023-04-08 | 12860 | 12.86 | 7.25 | 7.58 | 155 | 17 | 320 | 44 | 280 | 23 | NA | 400 | 0.3 | 22.46 | 1300000
2023-04-09 | 13450 | 13.45 | 7.21 | 7.5 | 145 | 18 | 308 | 48 | 268 | 24 | NA | 300 | 0.2 | 23.18 | 1200000
2023-04-10 | 12910 | 12.91 | 7.3 | 7.52 | 135 | 15 | 316 | 40 | 282 | 23 | NA | 500 | 0.3 | 23.51 | 1400000
2023-04-11 | 13330 | 13.33 | 7.42 | 7.51 | 140 | 17 | 304 | 44 | 293 | 28 | NA | 400 | 0.3 | 23.72 | 1300000
2023-04-12 | 13650 | 13.65 | 7.44 | 7.55 | 150 | 16 | 312 | 48 | 272 | 27 | NA | 500 | 0.3 | 23.41 | 1400000
2023-04-13 | 12600 | 12.6 | 7.4 | 7.54 | 145 | 18 | 308 | 44 | 280 | 28 | NA | 700 | 0.3 | 22.47 | 1700000
2023-04-14 | 13670 | 13.67 | 7.42 | 7.56 | 130 | 17 | 316 | 48 | 256 | 26 | NA | 600 | 0.3 | 21.9 | 1400000
2023-04-15 | 12560 | 12.56 | 7.44 | 7.54 | 150 | 16 | 320 | 44 | 296 | 27 | NA | 400 | 0.2 | 23.56 | 1200000
2023-04-16 | 13720 | 13.72 | 7.43 | 7.56 | 145 | 17 | 304 | 48 | 263 | 26 | NA | 600 | 0.3 | 23.46 | 1300000
2023-04-17 | 12060 | 12.06 | 7.37 | 7.5 | 130 | 16 | 312 | 44 | 284 | 25 | NA | 500 | 0.3 | 22.97 | 1400000
2023-04-18 | 12480 | 12.48 | 7.34 | 7.59 | 135 | 18 | 320 | 48 | 274 | 27 | NA | 400 | 0.3 | 23.46 | 1300000
2023-04-19 | 13180 | 13.18 | 7.36 | 7.57 | 145 | 17 | 324 | 44 | 293 | 28 | NA | 600 | 0.2 | 23.58 | 1200000
2023-04-20 | 13270 | 13.27 | 7.32 | 7.55 | 130 | 16 | 314 | 48 | 276 | 27 | NA | 500 | 0.3 | 22.8 | 1400000
2023-04-21 | 14390 | 14.39 | 7.34 | 7.58 | 140 | 18 | 308 | 44 | 286 | 28 | NA | 400 | 0.3 | 22.35 | 1300000
2023-04-22 | 13560 | 13.56 | 7.33 | 7.59 | 155 | 17 | 304 | 48 | 288 | 29 | NA | 600 | 0.2 | 22.44 | 1200000
2023-04-23 | 13220 | 13.22 | 7.3 | 7.51 | 135 | 18 | 324 | 44 | 266 | 28 | NA | 500 | 0.3 | 22.42 | 1400000
2023-04-24 | 13490 | 13.49 | 7.34 | 7.59 | 140 | 16 | 312 | 48 | 269 | 26 | NA | 400 | 0.3 | 22.35 | 1200000
2023-04-25 | 12640 | 12.64 | 7.38 | 7.58 | 150 | 17 | 316 | 44 | 268 | 29 | NA | 300 | 0.3 | 23.07 | 1300000
2023-04-26 | 13010 | 13.01 | 7.36 | 7.57 | 145 | 18 | 304 | 48 | 287 | 28 | NA | 500 | 0.2 | 23.72 | 1400000
2023-04-27 | 12560 | 12.56 | 7.4 | 7.56 | 135 | 16 | 320 | 40 | 293 | 23 | NA | 400 | 0.3 | 22.51 | 1200000
2023-04-28 | 12420 | 12.42 | 7.42 | 7.59 | 150 | 15 | 314 | 44 | 272 | 27 | NA | 300 | 0.3 | 23.5 | 1300000
2023-04-29 | 13070 | 13.07 | 7.46 | 7.6 | 130 | 17 | 324 | 48 | 284 | 28 | NA | 600 | 0.3 | 22.25 | 1400000
2023-04-30 | 13890 | 13.89 | 7.4 | 7.58 | 145 | 16 | 308 | 44 | 298 | 26 | NA | 400 | 0.3 | 22.42 | 1200000
Average | 13101 | 13.0943 | 7.3617 | 7.5393 | 141 | 16.6333 | 313.4 | 45.0667 | 278.9667 | 26.0667 | NA | 480 | 0.27333 | 22.974 | 1330000
392.83
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 12060 | 12.06 | 7.21 | 7.43 | 130 | 15 | 304 | 40 | 256 | 22 |  | 300 | 0.2 | 21.9 | 1200000
Max | 14390 | 14.39 | 7.46 | 7.6 | 155 | 18 | 324 | 48 | 298 | 29 |  | 700 | 0.3 | 23.86 | 1700000