## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-04-01 | 62050 | 62.05 | 7.24 | 7.6 | 140 | 14 | 320 | 36 | 269 | 24 | NA | 600 | 0.3 | 24.44 | 1400000
2022-04-02 | 61900 | 61.9 | 7.12 | 7.64 | 130 | 16 | 312 | 40 | 244 | 28 | NA | 600 | 0.4 | 24.16 | 1300000
2022-04-03 | 63450 | 63.45 | 7.12 | 7.84 | 135 | 15 | 328 | 36 | 284 | 26 | NA | 400 | 0.2 | 25.01 | 1400000
2022-04-04 | 57120 | 57.12 | 7.2 | 7.68 | 140 | 15 | 304 | 40 | 286 | 28 | NA | 700 | 0.3 | 24.04 | 1700000
2022-04-05 | 53870 | 53.87 | 7.27 | 7.84 | 135 | 17 | 328 | 44 | 264 | 26 | NA | 400 | 0.3 | 23.51 | 1400000
2022-04-06 | 60520 | 60.52 | 7.29 | 7.94 | 145 | 16 | 320 | 36 | 280 | 24 | NA | 600 | 0.2 | 23.63 | 1400000
2022-04-07 | 62140 | 62.14 | 7.15 | 7.8 | 140 | 15 | 332 | 40 | 230 | 28 | NA | 500 | 0.3 | 22.19 | 1300000
2022-04-08 | 61120 | 61.12 | 7.24 | 7.89 | 130 | 13 | 352 | 44 | 278 | 26 | NA | 400 | 0.2 | 21.82 | 1400000
2022-04-09 | 58450 | 58.45 | 7.19 | 7.8 | 150 | 16 | 328 | 36 | 288 | 26 | NA | 700 | 0.2 | 24.25 | 1700000
2022-04-10 | 64900 | 64.9 | 7.28 | 7.82 | 130 | 15 | 280 | 40 | 256 | 24 | NA | 500 | 0.2 | 23.26 | 1300000
2022-04-11 | 61570 | 61.57 | 7.34 | 7.76 | 140 | 16 | 332 | 36 | 258 | 28 | NA | 500 | 0.3 | 24.24 | 1300000
2022-04-12 | 59610 | 59.61 | 7.32 | 7.84 | 150 | 14 | 324 | 40 | 287 | 26 | NA | 700 | 0.2 | 23.98 | 1700000
2022-04-13 | 60100 | 60.1 | 7.18 | 7.71 | 145 | 15 | 320 | 40 | 240 | 24 | NA | 400 | 0.2 | 24.88 | 1400000
2022-04-14 | 55250 | 55.25 | 7.22 | 7.8 | 135 | 17 | 304 | 44 | 266 | 22 | NA | 700 | 0.3 | 23.35 | 1700000
2022-04-15 | 60790 | 60.79 | 7.19 | 7.78 | 140 | 16 | 296 | 40 | 264 | 28 | NA | 500 | 0.2 | 22.5 | 1300000
2022-04-16 | 60610 | 60.61 | 7.22 | 7.84 | 135 | 19 | 304 | 40 | 290 | 26 | NA | 400 | 0.3 | 22.81 | 1400000
2022-04-17 | 63840 | 63.84 | 7.16 | 7.88 | 145 | 16 | 360 | 36 | 255 | 24 | NA | 600 | 0.3 | 24.97 | 1400000 | Aeration tank no. 3 is taken in shutdown from 17.04.2022 for maintenance of diffusers.
2022-04-18 | 64020 | 64.02 | 7.18 | 7.84 | 135 | 14 | 328 | 36 | 286 | 26 | NA | 400 | 0.2 | 24.86 | 1300000
2022-04-19 | 60150 | 60.15 | 7.14 | 7.82 | 140 | 17 | 332 | 40 | 255 | 30 | NA | 700 | 0.2 | 24.33 | 1700000
2022-04-20 | 52710 | 52.71 | 7.18 | 7.8 | 145 | 18 | 320 | 36 | 246 | 28 | NA | 600 | 0.2 | 23.36 | 1400000
2022-04-21 | 61370 | 61.37 | 7.18 | 7.64 | 150 | 19 | 312 | 40 | 250 | 30 | NA | 400 | 0.3 | 23.12 | 1700000
2022-04-22 | 62240 | 62.24 | 7.14 | 7.74 | 140 | 17 | 320 | 36 | 280 | 24 | NA | 500 | 0.2 | 23.38 | 1300000
2022-04-23 | 59110 | 59.11 | 7.2 | 7.8 | 145 | 16 | 336 | 48 | 260 | 28 | NA | 700 | 0.2 | 22.18 | 1700000 | 1) Maintenance work for Aeration tank no. 3 is completed and it is taken into operation. 2) Aeration tank no. 2 is taken in shutdown from 23.04.2022 for maintenance of diffusers.
2022-04-24 | 56140 | 56.14 | 7.22 | 7.74 | 150 | 17 | 316 | 40 | 265 | 30 | NA | 600 | 0.2 | 21.15 | 1400000 | 1) Maintenance of diffusers in Aeration tank no. 2 is in progress. 2) SST no. 1 was in shutdown from 25.04.2022 to 27.04.2022 for maintenance of drain valve. 3) Raw sewage received on 25.04.2022 is less due to sudden breakdown of SST no. 1.
2022-04-25 | 49720 | 49.72 | 7.26 | 7.64 | 140 | 14 | 324 | 48 | 244 | 28 | NA | 700 | 0.3 | 24.09 | 1700000
2022-04-26 | 55970 | 55.97 | 7.27 | 7.84 | 130 | 19 | 316 | 44 | 285 | 28 | NA | 600 | 0.2 | 21.86 | 1400000
2022-04-27 | 57430 | 57.43 | 7.19 | 7.64 | 140 | 18 | 320 | 40 | 255 | 28 | NA | 900 | 0.2 | 21.72 | 1700000
2022-04-28 | 61320 | 61.32 | 7.24 | 7.74 | 135 | 17 | 328 | 40 | 287 | 30 | NA | 400 | 0.3 | 22.41 | 1400000
2022-04-29 | 60530 | 60.53 | 7.16 | 7.78 | 150 | 14 | 316 | 36 | 250 | 24 | NA | 600 | 0.3 | 21.13 | 1300000
2022-04-30 | 64510 | 64.51 | 7.1 | 7.8 | 140 | 17 | 280 | 40 | 205 | 26 | NA | 500 | 0.2 | 21.74 | 1400000
Average | 59750.3333 | 59.7503 | 7.2063 | 7.776 | 140.1667 | 16.0667 | 319.7333 | 39.7333 | 263.5667 | 26.6 | NA | 560 | 0.24667 | 23.279 | 1463333.3333
| 1792510 | 1792.51
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 49720 | 49.72 | 7.1 | 7.6 | 130 | 13 | 280 | 36 | 205 | 22 |  | 400 | 0.2 | 21.13 | 1300000
Max | 64900 | 64.9 | 7.34 | 7.94 | 150 | 19 | 360 | 48 | 290 | 30 |  | 900 | 0.4 | 25.01 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-04-01 | 33410 | 33.41 | 7.28 | 7.59 | 153 | 23 | 352 | 44 | 312 | 35 | NA | 600 | 0.3 | 22.7 | 1400000
2022-04-02 | 34920 | 34.92 | 7.34 | 7.63 | 162 | 25 | 344 | 40 | 320 | 33 | NA | 500 | 0.2 | 23.1 | 1200000
2022-04-03 | 33860 | 33.86 | 7.21 | 7.54 | 156 | 22 | 356 | 44 | 305 | 34 | NA | 700 | 0.3 | 22.9 | 1300000
2022-04-04 | 35060 | 35.06 | 7.26 | 7.67 | 165 | 26 | 348 | 36 | 316 | 31 | NA | 400 | 0.2 | 22.5 | 1100000
2022-04-05 | 34560 | 34.56 | 7.31 | 7.62 | 159 | 24 | 364 | 44 | 308 | 36 | NA | 600 | 0.3 | 23.2 | 1200000
2022-04-06 | 34200 | 34.2 | 7.4 | 7.56 | 153 | 23 | 352 | 40 | 320 | 32 | NA | 700 | 0.2 | 23.5 | 1400000
2022-04-07 | 33500 | 33.5 | 7.36 | 7.65 | 162 | 25 | 340 | 36 | 312 | 37 | NA | 500 | 0.2 | 23.1 | 1100000
2022-04-08 | 32520 | 32.52 | 7.23 | 7.59 | 156 | 22 | 348 | 44 | 306 | 33 | NA | 600 | 0.3 | 23.6 | 1300000
2022-04-09 | 32210 | 32.21 | 7.33 | 7.67 | 159 | 24 | 356 | 48 | 316 | 35 | NA | 400 | 0.2 | 22.9 | 1200000
2022-04-10 | 33950 | 33.95 | 7.29 | 7.62 | 153 | 21 | 364 | 44 | 322 | 34 | NA | 800 | 0.3 | 23.4 | 1600000
2022-04-11 | 33530 | 33.53 | 7.37 | 7.71 | 144 | 19 | 352 | 40 | 307 | 38 | NA | 700 | 0.2 | 22.7 | 1400000
2022-04-12 | 35020 | 35.02 | 7.25 | 7.64 | 156 | 22 | 344 | 36 | 318 | 32 | NA | 500 | 0.2 | 23.6 | 1200000
2022-04-13 | 35930 | 35.93 | 7.32 | 7.58 | 153 | 24 | 356 | 44 | 298 | 35 | NA | 600 | 0.3 | 23.1 | 1300000
2022-04-14 | 33050 | 33.05 | 7.38 | 7.69 | 162 | 25 | 348 | 40 | 312 | 33 | NA | 700 | 0.2 | 23.5 | 1600000
2022-04-15 | 33910 | 33.91 | 7.22 | 7.62 | 152 | 21 | 360 | 44 | 305 | 31 | NA | 400 | 0.3 | 23.3 | 1100000
2022-04-16 | 32330 | 32.33 | 7.29 | 7.56 | 153 | 23 | 352 | 36 | 315 | 34 | NA | 500 | 0.2 | 24.1 | 1200000
2022-04-17 | 33200 | 33.2 | 7.35 | 7.67 | 162 | 25 | 340 | 40 | 302 | 32 | NA | 400 | 0.2 | 23.6 | 1200000
2022-04-18 | 31470 | 31.47 | 7.28 | 7.59 | 156 | 22 | 336 | 36 | 312 | 34 | NA | 400 | 0.3 | 23.9 | 1100000
2022-04-19 | 33120 | 33.12 | 7.22 | 7.63 | 159 | 24 | 364 | 44 | 318 | 32 | NA | 500 | 0.2 | 23.5 | 1400000
2022-04-20 | 31620 | 31.62 | 7.29 | 7.32 | 164 | 27 | 348 | 36 | 306 | 33 | NA | 600 | 0.3 | 23.8 | 1300000
2022-04-21 | 33140 | 33.14 | 7.38 | 7.69 | 147 | 23 | 348 | 44 | 320 | 32 | NA | 700 | 0.3 | 23.6 | 1400000
2022-04-22 | 32990 | 32.99 | 7.35 | 7.63 | 160 | 24 | 352 | 36 | 312 | 34 | NA | 400 | 0.2 | 26.2 | 1200000
2022-04-23 | 32490 | 32.49 | 7.38 | 7.6 | 164 | 26 | 344 | 40 | 308 | 36 | NA | 600 | 0.2 | 24.9 | 1100000
2022-04-24 | 32180 | 32.18 | 7.26 | 7.67 | 172 | 25 | 360 | 32 | 309 | 34 | NA | 800 | 0.3 | 25 | 1600000
2022-04-25 | 32400 | 32.4 | 7.37 | 7.58 | 167 | 26 | 364 | 44 | 338 | 44 | NA | 700 | 0.2 | 25.4 | 1700000
2022-04-26 | 31310 | 31.31 | 7.39 | 7.55 | 156 | 23 | 336 | 40 | 324 | 42 | NA | 600 | 0.3 | 24.2 | 1300000
2022-04-27 | 32340 | 32.34 | 7.4 | 7.56 | 146 | 20 | 340 | 36 | 312 | 37 | NA | 500 | 0.2 | 23.9 | 1400000
2022-04-28 | 30830 | 30.83 | 7.42 | 7.49 | 154 | 18 | 360 | 40 | 319 | 34 | NA | 800 | 0.3 | 24.8 | 1200000
2022-04-29 | 30130 | 30.13 | 7.33 | 7.6 | 160 | 21 | 368 | 44 | 313 | 35 | NA | 700 | 0.3 | 25.1 | 1300000
2022-04-30 | 32130 | 32.13 | 7.39 | 7.53 | 158 | 24 | 356 | 40 | 340 | 42 | NA | 500 | 0.2 | 23 | 1600000
Average | 33043.6667 | 33.0437 | 7.3217 | 7.6017 | 157.4333 | 23.2333 | 351.7333 | 40.4 | 314.1667 | 34.8 | NA | 580 | 0.24667 | 23.7367 | 1313333.3333
| 991310 | 991.31
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 30130 | 30.13 | 7.21 | 7.32 | 144 | 18 | 336 | 32 | 298 | 31 |  | 400 | 0.2 | 22.5 | 1100000
Max | 35930 | 35.93 | 7.42 | 7.71 | 172 | 27 | 368 | 48 | 340 | 44 |  | 800 | 0.3 | 26.2 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-04-01 | 26030 | 26.03 | 7.34 | 7.65 | 143 | 13 | 316 | 36 | 255 | 19 | NA | 500 | 0.3 | 22.87 | 1600000
2022-04-02 | 26910 | 26.91 | 7.41 | 7.57 | 137 | 14 | 336 | 32 | 249 | 18 | NA | 600 | 0.2 | 23.5 | 1400000
2022-04-03 | 27720 | 27.72 | 7.29 | 7.48 | 146 | 13 | 320 | 36 | 265 | 20 | NA | 400 | 0.3 | 22.67 | 1300000
2022-04-04 | 25540 | 25.54 | 7.24 | 7.63 | 141 | 15 | 308 | 32 | 272 | 21 | NA | 500 | 0.2 | 21.77 | 1700000
2022-04-05 | 26690 | 26.69 | 7.18 | 7.41 | 135 | 12 | 300 | 36 | 259 | 19 | NA | 600 | 0.2 | 23.63 | 1400000
2022-04-06 | 27010 | 27.01 | 7.31 | 7.68 | 145 | 14 | 328 | 40 | 277 | 23 | NA | 500 | 0.3 | 21.56 | 1300000
2022-04-07 | 27380 | 27.38 | 7.26 | 7.52 | 140 | 13 | 304 | 32 | 261 | 21 | NA | 700 | 0.2 | 22.81 | 1400000
2022-04-08 | 27960 | 27.96 | 7.36 | 7.66 | 150 | 14 | 324 | 40 | 285 | 18 | NA | 400 | 0.2 | 23.58 | 1100000
2022-04-09 | 28720 | 28.72 | 7.29 | 7.58 | 138 | 12 | 316 | 36 | 268 | 20 | NA | 500 | 0.3 | 23.34 | 1300000
2022-04-10 | 28960 | 28.96 | 7.22 | 7.64 | 132 | 13 | 308 | 32 | 274 | 19 | NA | 600 | 0.2 | 22.91 | 1400000
2022-04-11 | 29210 | 29.21 | 7.33 | 7.69 | 142 | 12 | 320 | 36 | 281 | 21 | NA | 500 | 0.3 | 23.44 | 1200000
2022-04-12 | 28890 | 28.89 | 7.21 | 7.56 | 135 | 14 | 304 | 40 | 266 | 20 | NA | 400 | 0.3 | 21.83 | 1400000
2022-04-13 | 28820 | 28.82 | 7.27 | 7.61 | 141 | 13 | 312 | 32 | 278 | 22 | NA | 500 | 0.2 | 22.76 | 1600000
2022-04-14 | 27920 | 27.92 | 7.16 | 7.46 | 147 | 15 | 300 | 36 | 254 | 19 | NA | 600 | 0.3 | 23.31 | 1300000
2022-04-15 | 28040 | 28.04 | 7.25 | 7.72 | 140 | 14 | 316 | 40 | 267 | 23 | NA | 700 | 0.2 | 21.64 | 1400000
2022-04-16 | 27300 | 27.3 | 7.31 | 7.68 | 153 | 15 | 328 | 36 | 276 | 21 | NA | 800 | 0.3 | 22.26 | 1600000
2022-04-17 | 27460 | 27.46 | 7.22 | 7.59 | 143 | 13 | 320 | 44 | 264 | 24 | NA | 500 | 0.2 | 23.44 | 1300000 | Aeration tank no. 1 is taken in shutdown from 17.04.2022 for maintenance of diffusers.
2022-04-18 | 26880 | 26.88 | 7.34 | 7.65 | 136 | 14 | 324 | 48 | 272 | 22 | NA | 600 | 0.3 | 23.18 | 1400000
2022-04-19 | 27070 | 27.07 | 7.28 | 7.69 | 140 | 13 | 316 | 44 | 279 | 23 | NA | 700 | 0.2 | 23.77 | 1600000
2022-04-20 | 26460 | 26.46 | 7.19 | 7.54 | 147 | 15 | 308 | 48 | 268 | 25 | NA | 800 | 0.3 | 24.11 | 1700000
2022-04-21 | 26290 | 26.29 | 7.24 | 7.59 | 143 | 14 | 324 | 44 | 274 | 24 | NA | 600 | 0.2 | 23.64 | 1300000
2022-04-22 | 26410 | 26.41 | 7.32 | 7.65 | 136 | 13 | 328 | 48 | 284 | 26 | NA | 700 | 0.3 | 23.47 | 1400000
2022-04-23 | 26580 | 26.58 | 7.37 | 7.69 | 156 | 16 | 320 | 40 | 264 | 25 | NA | 500 | 0.2 | 22.8 | 1600000 | 1) Aeration tank no. 1 is taken in shutdown from 17.04.2022 for maintenance of diffusers. 2) Aeration tank no. 2 is taken in shutdown from 23.04.2022 for maintenance of diffusers.
2022-04-24 | 26230 | 26.23 | 7.28 | 7.55 | 147 | 15 | 312 | 44 | 277 | 24 | NA | 600 | 0.2 | 23.03 | 1300000 | Maintenance of diffusers in Aeration tank no. 2 is in progress.
2022-04-25 | 25800 | 25.8 | 7.23 | 7.62 | 136 | 14 | 316 | 40 | 268 | 22 | NA | 400 | 0.3 | 23.92 | 1600000
2022-04-26 | 26370 | 26.37 | 7.34 | 7.71 | 143 | 16 | 324 | 44 | 275 | 24 | NA | 700 | 0.2 | 24.32 | 1400000
2022-04-27 | 26320 | 26.32 | 7.25 | 7.67 | 133 | 13 | 312 | 36 | 262 | 21 | NA | 600 | 0.3 | 23.77 | 1700000 | Aeration tank no. 1 is taken in shutdown from 17.04.2022 for maintenance of diffusers.
2022-04-28 | 26740 | 26.74 | 7.37 | 7.64 | 140 | 15 | 320 | 44 | 280 | 23 | NA | 500 | 0.2 | 23.09 | 1200000
2022-04-29 | 27630 | 27.63 | 7.29 | 7.58 | 147 | 14 | 308 | 36 | 271 | 20 | NA | 700 | 0.3 | 23.51 | 1300000
2022-04-30 | 27180 | 27.18 | 7.34 | 7.66 | 143 | 16 | 316 | 40 | 278 | 22 | NA | 400 | 0.2 | 22.92 | 1200000
Average | 27217.3333 | 27.2173 | 7.283 | 7.6123 | 141.8333 | 13.9 | 316.2667 | 39.0667 | 270.1 | 21.6333 | NA | 570 | 0.24667 | 23.095 | 1413333.3333
| 816520 | 816.52
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 25540 | 25.54 | 7.16 | 7.41 | 132 | 12 | 300 | 32 | 249 | 18 |  | 400 | 0.2 | 21.56 | 1100000
Max | 29210 | 29.21 | 7.41 | 7.72 | 156 | 16 | 336 | 48 | 285 | 26 |  | 800 | 0.3 | 24.32 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-04-01 | 12310 | 12.31 | 7.27 | 7.56 | 140 | 15 | 316 | 40 | 270 | 23 | NA | 400 | 0.2 | 21.33 | 1600000
2022-04-02 | 12710 | 12.71 | 7.36 | 7.71 | 145 | 14 | 324 | 36 | 246 | 21 | NA | 500 | 0.3 | 22.15 | 1400000
2022-04-03 | 11980 | 11.98 | 7.25 | 7.63 | 138 | 16 | 312 | 40 | 264 | 22 | NA | 600 | 0.3 | 23.25 | 1300000
2022-04-04 | 11240 | 11.24 | 7.18 | 7.48 | 150 | 18 | 320 | 44 | 257 | 24 | NA | 500 | 0.2 | 22.34 | 1700000
2022-04-05 | 10770 | 10.77 | 7.33 | 7.67 | 144 | 17 | 308 | 40 | 276 | 26 | NA | 600 | 0.3 | 21.56 | 1400000
2022-04-06 | 11850 | 11.85 | 7.26 | 7.51 | 138 | 16 | 324 | 36 | 261 | 23 | NA | 700 | 0.2 | 22.78 | 1600000
2022-04-07 | 13020 | 13.02 | 7.21 | 7.64 | 135 | 18 | 316 | 44 | 260 | 20 | NA | 500 | 0.3 | 23.12 | 1200000
2022-04-08 | 13710 | 13.71 | 7.31 | 7.58 | 130 | 16 | 304 | 40 | 280 | 22 | NA | 600 | 0.3 | 22.69 | 1300000
2022-04-09 | 13860 | 13.86 | 7.23 | 7.71 | 140 | 15 | 332 | 36 | 271 | 24 | NA | 400 | 0.2 | 23.58 | 1700000
2022-04-10 | 14270 | 14.27 | 7.36 | 7.67 | 145 | 17 | 324 | 40 | 265 | 23 | NA | 500 | 0.3 | 23.12 | 1400000
2022-04-11 | 12750 | 12.75 | 7.28 | 7.73 | 138 | 16 | 312 | 36 | 258 | 21 | NA | 700 | 0.2 | 22.88 | 1600000
2022-04-12 | 13840 | 13.84 | 7.26 | 7.61 | 142 | 15 | 320 | 40 | 262 | 25 | NA | 600 | 0.2 | 21.66 | 1200000
2022-04-13 | 13460 | 13.46 | 7.34 | 7.55 | 135 | 17 | 308 | 44 | 278 | 22 | NA | 500 | 0.3 | 22.18 | 1400000
2022-04-14 | 13410 | 13.41 | 7.25 | 7.46 | 144 | 16 | 328 | 40 | 253 | 20 | NA | 600 | 0.2 | 20.92 | 1300000
2022-04-15 | 13290 | 13.29 | 7.16 | 7.32 | 138 | 15 | 316 | 36 | 264 | 23 | NA | 400 | 0.3 | 21.41 | 1600000
2022-04-16 | 13750 | 13.75 | 7.24 | 7.56 | 142 | 16 | 304 | 44 | 280 | 24 | NA | 500 | 0.3 | 22.83 | 1700000
2022-04-17 | 13540 | 13.54 | 7.32 | 7.66 | 146 | 17 | 312 | 36 | 276 | 22 | NA | 700 | 0.3 | 21.64 | 1400000
2022-04-18 | 13700 | 13.7 | 7.17 | 7.58 | 138 | 15 | 300 | 40 | 266 | 25 | NA | 600 | 0.2 | 22.36 | 1300000
2022-04-19 | 15360 | 15.36 | 7.25 | 7.64 | 143 | 16 | 308 | 36 | 272 | 24 | NA | 500 | 0.3 | 21.81 | 1600000
2022-04-20 | 13150 | 13.15 | 7.29 | 7.55 | 140 | 15 | 316 | 44 | 264 | 23 | NA | 700 | 0.2 | 22.43 | 1400000
2022-04-21 | 12970 | 12.97 | 7.34 | 7.61 | 146 | 17 | 324 | 40 | 259 | 25 | NA | 400 | 0.3 | 21.62 | 1300000
2022-04-22 | 13720 | 13.72 | 7.27 | 7.67 | 138 | 16 | 312 | 44 | 268 | 24 | NA | 600 | 0.2 | 22.68 | 1400000
2022-04-23 | 12720 | 12.72 | 7.21 | 7.72 | 133 | 15 | 320 | 36 | 274 | 23 | NA | 700 | 0.3 | 23.21 | 1600000
2022-04-24 | 14660 | 14.66 | 7.32 | 7.64 | 143 | 17 | 308 | 40 | 265 | 22 | NA | 500 | 0.2 | 22.51 | 1300000
2022-04-25 | 12640 | 12.64 | 7.38 | 7.69 | 138 | 16 | 316 | 44 | 278 | 24 | NA | 700 | 0.2 | 21.79 | 1400000
2022-04-26 | 14020 | 14.02 | 7.24 | 7.58 | 146 | 18 | 324 | 40 | 271 | 23 | NA | 600 | 0.3 | 22.12 | 1600000
2022-04-27 | 12210 | 12.21 | 7.29 | 7.67 | 140 | 15 | 312 | 36 | 282 | 25 | NA | 500 | 0.2 | 22.86 | 1200000
2022-04-28 | 15340 | 15.34 | 7.36 | 7.63 | 133 | 16 | 304 | 40 | 258 | 22 | NA | 400 | 0.3 | 23.24 | 1400000
2022-04-29 | 13300 | 13.3 | 7.31 | 7.59 | 142 | 18 | 316 | 32 | 264 | 23 | NA | 700 | 0.2 | 22.31 | 1300000
2022-04-30 | 13160 | 13.16 | 7.25 | 7.66 | 138 | 17 | 308 | 36 | 269 | 21 | NA | 500 | 0.3 | 22.87 | 1200000
Average | 13223.6667 | 13.2237 | 7.2763 | 7.6093 | 140.2667 | 16.1667 | 314.9333 | 39.3333 | 267.0333 | 22.9667 | NA | 556.6667 | 0.25333 | 22.375 | 1426666.6667
| 396710 | 396.71
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 10770 | 10.77 | 7.16 | 7.32 | 130 | 14 | 300 | 32 | 246 | 20 |  | 400 | 0.2 | 20.92 | 1200000
Max | 15360 | 15.36 | 7.38 | 7.73 | 150 | 18 | 332 | 44 | 282 | 26 |  | 700 | 0.3 | 23.58 | 1700000