## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-04-01 | 58100 | 58.1 | 7.2 | 7.65 | 145 | 15 | 340 | 36 | 265 | 25 | NA | 400 | 0.3 | 23.14 | 1100000
2024-04-02 | 57700 | 57.7 | 7.32 | 7.78 | 135 | 17 | 320 | 44 | 280 | 29 | NA | 700 | 0.3 | 22.7 | 1400000
2024-04-03 | 53690 | 53.69 | 7.36 | 7.7 | 145 | 16 | 312 | 44 | 270 | 26 | NA | 500 | 0.3 | 22.69 | 1300000
2024-04-04 | 59480 | 59.48 | 7.33 | 7.68 | 135 | 14 | 324 | 44 | 305 | 27 | NA | 400 | 0.2 | 22.71 | 1100000
2024-04-05 | 60830 | 60.83 | 7.35 | 7.8 | 140 | 15 | 352 | 40 | 265 | 25 | NA | 400 | 0.3 | 23.71 | 1400000
2024-04-06 | 60520 | 60.52 | 7.24 | 7.68 | 135 | 16 | 304 | 36 | 288 | 28 | NA | 500 | 0.3 | 23.13 | 1200000
2024-04-07 | 58900 | 58.9 | 7.27 | 7.64 | 130 | 17 | 308 | 44 | 277 | 26 | NA | 600 | 0.2 | 22.73 | 1300000
2024-04-08 | 60940 | 60.94 | 7.23 | 7.79 | 135 | 15 | 324 | 40 | 316 | 27 | NA | 700 | 0.3 | 23.04 | 1700000
2024-04-09 | 54650 | 54.65 | 7.35 | 7.66 | 140 | 20 | 316 | 48 | 300 | 29 | NA | 400 | 0.3 | 22.54 | 1100000
2024-04-10 | 60900 | 60.9 | 7.26 | 7.62 | 135 | 15 | 356 | 36 | 376 | 26 | NA | 500 | 0.2 | 23.71 | 1400000
2024-04-11 | 61400 | 61.4 | 7.31 | 7.6 | 140 | 16 | 316 | 44 | 302 | 27 | NA | 600 | 0.2 | 22.74 | 1200000
2024-04-12 | 59750 | 59.75 | 7.3 | 7.7 | 130 | 15 | 300 | 40 | 260 | 28 | NA | 500 | 0.3 | 22.79 | 1200000
2024-04-13 | 57400 | 57.4 | 7.34 | 7.68 | 135 | 14 | 308 | 36 | 286 | 25 | NA | 600 | 0.3 | 23.71 | 1100000
2024-04-14 | 58350 | 58.35 | 7.35 | 7.7 | 140 | 16 | 324 | 40 | 264 | 28 | NA | 400 | 0.3 | 22.1 | 1700000
2024-04-15 | 56800 | 56.8 | 7.22 | 7.65 | 135 | 14 | 336 | 44 | 344 | 26 | NA | 700 | 0.2 | 22.23 | 1300000
2024-04-16 | 58440 | 58.44 | 7.3 | 7.65 | 130 | 17 | 352 | 40 | 366 | 26 | NA | 500 | 0.2 | 23.03 | 1400000
2024-04-17 | 55780 | 55.78 | 7.29 | 7.6 | 140 | 19 | 304 | 44 | 283 | 28 | NA | 600 | 0.3 | 23.05 | 1200000
2024-04-18 | 56500 | 56.5 | 7.25 | 7.62 | 135 | 17 | 296 | 40 | 270 | 26 | NA | 400 | 0.2 | 22.3 | 1100000
2024-04-19 | 56260 | 56.26 | 7.32 | 7.68 | 140 | 14 | 308 | 36 | 290 | 27 | NA | 700 | 0.2 | 22.51 | 1300000
2024-04-20 | 57850 | 57.85 | 7.28 | 7.66 | 145 | 18 | 300 | 44 | 270 | 28 | NA | 700 | 0.3 | 22.32 | 1400000
2024-04-21 | 57870 | 57.87 | 7.24 | 7.65 | 140 | 16 | 308 | 40 | 276 | 25 | NA | 500 | 0.3 | 23 | 1200000
2024-04-22 | 58190 | 58.19 | 7.22 | 7.69 | 135 | 15 | 336 | 44 | 288 | 26 | NA | 600 | 0.2 | 23.01 | 1100000
2024-04-23 | 55780 | 55.78 | 7.18 | 7.61 | 140 | 16 | 320 | 40 | 298 | 29 | NA | 700 | 0.3 | 22.98 | 1200000
2024-04-24 | 56840 | 56.84 | 7.32 | 7.64 | 145 | 14 | 328 | 44 | 300 | 27 | NA | 500 | 0.2 | 23.06 | 1300000
2024-04-25 | 56900 | 56.9 | 7.28 | 7.62 | 130 | 15 | 320 | 36 | 316 | 24 | NA | 700 | 0.2 | 23.31 | 1700000
2024-04-26 | 57500 | 57.5 | 7.3 | 7.65 | 135 | 14 | 308 | 40 | 302 | 26 | NA | 400 | 0.2 | 22.96 | 1100000
2024-04-27 | 59400 | 59.4 | 7.24 | 7.6 | 140 | 16 | 312 | 44 | 288 | 27 | NA | 600 | 0.3 | 23.13 | 1200000
2024-04-28 | 57300 | 57.3 | 7.26 | 7.63 | 130 | 15 | 332 | 40 | 322 | 25 | NA | 500 | 0.2 | 22.99 | 1300000
2024-04-29 | 30100 | 30.1 | 7.32 | 7.64 | 145 | 18 | 300 | 44 | 270 | 26 | NA | 600 | 0.3 | 23.42 | 1100000 | Due to leakage in rising main to Numayadahi STP, Ghagharnalla MPS was shutdown from 1 PM on date 29/04/2024. Subsequently, Numayadahi STP & Sasurkadheri SPS were also stopped.
2024-04-30 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | 22.33 | 1700000
Average | 55137.3333 | 55.1373 | 7.2838 | 7.6645 | 137.4138 | 15.8276 | 319.4483 | 41.1034 | 294.3793 | 26.6207 |  | 548.2759 | 0.25517 | 22.9023 | 1293333.3333
1654.12
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.18 | 7.6 | 130 | 14 | 296 | 36 | 260 | 24 |  | 400 | 0.2 | 22.1 | 1100000
Max | 61400 | 61.4 | 7.36 | 7.8 | 145 | 20 | 356 | 48 | 376 | 29 |  | 700 | 0.3 | 23.71 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-04-01 | 36730 | 36.73 | 7.23 | 7.44 | 160 | 24 | 360 | 40 | 357 | 36 | NA | 500 | 0.2 | 22.29 | 1700000
2024-04-02 | 35140 | 35.14 | 7.25 | 7.46 | 160 | 25 | 356 | 40 | 347 | 35 | NA | 700 | 0.3 | 24.15 | 1200000
2024-04-03 | 36210 | 36.21 | 7.22 | 7.42 | 155 | 25 | 348 | 44 | 310 | 32 | NA | 600 | 0.3 | 23.72 | 1400000
2024-04-04 | 35910 | 35.91 | 7.2 | 7.46 | 160 | 27 | 352 | 44 | 318 | 35 | NA | 400 | 0.2 | 24.36 | 1300000
2024-04-05 | 37470 | 37.47 | 7.24 | 7.48 | 150 | 23 | 356 | 40 | 337 | 36 | NA | 600 | 0.3 | 24.41 | 1200000
2024-04-06 | 39980 | 39.98 | 7.22 | 7.43 | 155 | 22 | 352 | 36 | 344 | 34 | NA | 700 | 0.3 | 23.57 | 1700000
2024-04-07 | 37420 | 37.42 | 7.17 | 7.45 | 160 | 24 | 356 | 40 | 352 | 37 | NA | 500 | 0.3 | 24.42 | 1300000
2024-04-08 | 37360 | 37.36 | 7.15 | 7.47 | 160 | 25 | 360 | 44 | 355 | 36 | NA | 400 | 0.3 | 23.97 | 1100000
2024-04-09 | 38490 | 38.49 | 7.24 | 7.45 | 155 | 24 | 356 | 44 | 341 | 35 | NA | 600 | 0.3 | 24.62 | 1400000
2024-04-10 | 38870 | 38.87 | 7.27 | 7.53 | 160 | 26 | 364 | 48 | 348 | 37 | NA | 500 | 0.3 | 24.04 | 1200000
2024-04-11 | 39120 | 39.12 | 7.1 | 7.45 | 165 | 25 | 360 | 44 | 342 | 33 | NA | 600 | 0.3 | 23.18 | 1700000
2024-04-12 | 38450 | 38.45 | 7.21 | 7.49 | 155 | 23 | 356 | 40 | 347 | 35 | NA | 700 | 0.3 | 24.83 | 1300000
2024-04-13 | 39670 | 39.67 | 7.42 | 7.54 | 160 | 24 | 356 | 44 | 354 | 37 | NA | 400 | 0.3 | 22.98 | 1100000
2024-04-14 | 39680 | 39.68 | 7.24 | 7.47 | 150 | 23 | 360 | 40 | 342 | 34 | NA | 600 | 0.3 | 23.47 | 1200000
2024-04-15 | 38320 | 38.32 | 7.1 | 7.42 | 155 | 25 | 368 | 48 | 357 | 39 | NA | 700 | 0.3 | 24.02 | 1700000
2024-04-16 | 39560 | 39.56 | 7.08 | 7.46 | 165 | 26 | 364 | 48 | 354 | 38 | NA | 600 | 0.3 | 24.1 | 1200000
2024-04-17 | 37290 | 37.29 | 7.46 | 7.57 | 160 | 22 | 360 | 44 | 334 | 47 | NA | 400 | 0.3 | 24.19 | 1700000
2024-04-18 | 37400 | 37.4 | 7.1 | 7.54 | 145 | 21 | 360 | 48 | 338 | 48 | NA | 500 | 0.3 | 24.61 | 1200000
2024-04-19 | 35960 | 35.96 | 7.22 | 7.56 | 140 | 22 | 364 | 44 | 355 | 46 | NA | 700 | 0.3 | 22.97 | 1400000
2024-04-20 | 37100 | 37.1 | 7.17 | 7.54 | 150 | 24 | 368 | 40 | 375 | 38 | NA | 600 | 0.3 | 23.12 | 1700000
2024-04-21 | 35170 | 35.17 | 7.24 | 7.57 | 160 | 23 | 368 | 36 | 378 | 36 | NA | 400 | 0.3 | 24.35 | 1200000
2024-04-22 | 35080 | 35.08 | 7.22 | 7.67 | 155 | 24 | 364 | 36 | 360 | 32 | NA | 700 | 0.3 | 23.1 | 1700000
2024-04-23 | 36360 | 36.36 | 7.41 | 7.72 | 160 | 25 | 348 | 40 | 350 | 31 | NA | 500 | 0.3 | 23.81 | 1100000
2024-04-24 | 36590 | 36.59 | 7.2 | 7.59 | 165 | 24 | 360 | 36 | 355 | 30 | NA | 400 | 0.3 | 24.64 | 1400000
2024-04-25 | 35560 | 35.56 | 7.17 | 7.53 | 155 | 23 | 368 | 40 | 372 | 33 | NA | 700 | 0.3 | 22.92 | 1700000
2024-04-26 | 37740 | 37.74 | 7.08 | 7.55 | 160 | 25 | 364 | 44 | 370 | 37 | NA | 600 | 0.3 | 23.12 | 1200000
2024-04-27 | 36730 | 36.73 | 7.25 | 7.6 | 165 | 23 | 368 | 40 | 364 | 34 | NA | 700 | 0.3 | 23.2 | 1700000
2024-04-28 | 35560 | 35.56 | 7.22 | 7.54 | 160 | 24 | 360 | 44 | 347 | 40 | NA | 600 | 0.3 | 22.63 | 1400000
2024-04-29 | 35620 | 35.62 | 7.28 | 7.62 | 150 | 22 | 368 | 40 | 345 | 38 | NA | 500 | 0.3 | 22.56 | 1300000
2024-04-30 | 36900 | 36.9 | 7.35 | 7.7 | 155 | 21 | 364 | 36 | 360 | 31 | NA | 400 | 0.3 | 22.98 | 1100000
Average | 37248 | 37.248 | 7.2237 | 7.524 | 156.8333 | 23.8 | 360.2667 | 41.7333 | 350.2667 | 36.3333 |  | 560 | 0.29333 | 23.6777 | 1383333.3333
1117.44
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 35080 | 35.08 | 7.08 | 7.42 | 140 | 21 | 348 | 36 | 310 | 30 |  | 400 | 0.2 | 22.29 | 1100000
Max | 39980 | 39.98 | 7.46 | 7.72 | 165 | 27 | 368 | 48 | 378 | 48 |  | 700 | 0.3 | 24.83 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-04-01 | 28850 | 28.85 | 6.95 | 7.26 | 140 | 15 | 304 | 40 | 261 | 17 | NA | 400 | 0.3 | 23.18 | 1700000
2024-04-02 | 26800 | 26.8 | 6.91 | 7.39 | 145 | 14 | 316 | 44 | 272 | 16 | NA | 600 | 0.3 | 23.87 | 1400000
2024-04-03 | 28160 | 28.16 | 7.11 | 7.43 | 135 | 13 | 312 | 36 | 279 | 15 | NA | 500 | 0.3 | 22.68 | 1100000
2024-04-04 | 27930 | 27.93 | 7.06 | 7.25 | 140 | 14 | 320 | 40 | 286 | 16 | NA | 600 | 0.3 | 24.06 | 1400000
2024-04-05 | 29670 | 29.67 | 7.13 | 7.24 | 135 | 15 | 308 | 44 | 277 | 17 | NA | 700 | 0.3 | 23.18 | 1300000
2024-04-06 | 29030 | 29.03 | 7.09 | 7.28 | 145 | 14 | 304 | 40 | 265 | 16 | NA | 400 | 0.3 | 23.49 | 1200000
2024-04-07 | 31500 | 31.5 | 7.05 | 7.23 | 130 | 15 | 316 | 44 | 292 | 17 | NA | 500 | 0.3 | 22.91 | 1700000
2024-04-08 | 29610 | 29.61 | 7.14 | 7.28 | 135 | 12 | 324 | 36 | 278 | 15 | NA | 400 | 0.2 | 23.59 | 1300000
2024-04-09 | 30150 | 30.15 | 7.02 | 7.25 | 140 | 13 | 320 | 40 | 285 | 16 | NA | 600 | 0.2 | 21.65 | 1700000
2024-04-10 | 29510 | 29.51 | 7.11 | 7.19 | 130 | 14 | 328 | 44 | 298 | 18 | NA | 500 | 0.3 | 22.25 | 1400000
2024-04-11 | 29580 | 29.58 | 7.18 | 7.26 | 145 | 15 | 332 | 40 | 305 | 15 | NA | 700 | 0.3 | 22.81 | 1200000
2024-04-12 | 30040 | 30.04 | 7.13 | 7.29 | 150 | 11 | 324 | 32 | 293 | 17 | NA | 600 | 0.2 | 22.48 | 1400000
2024-04-13 | 29470 | 29.47 | 7.1 | 7.33 | 140 | 12 | 336 | 36 | 303 | 16 | NA | 700 | 0.2 | 24.38 | 1300000
2024-04-14 | 30210 | 30.21 | 7.4 | 7.44 | 130 | 11 | 320 | 32 | 283 | 17 | NA | 400 | 0.2 | 24.64 | 1700000
2024-04-15 | 29600 | 29.6 | 7.42 | 7.24 | 135 | 12 | 304 | 36 | 264 | 18 | NA | 500 | 0.2 | 22.57 | 1200000
2024-04-16 | 29650 | 29.65 | 7.26 | 7.35 | 140 | 11 | 328 | 36 | 278 | 17 | NA | 800 | 0.2 | 23.67 | 1400000
2024-04-17 | 28430 | 28.43 | 7.12 | 7.31 | 145 | 13 | 316 | 40 | 287 | 16 | NA | 700 | 0.2 | 24.24 | 1700000
2024-04-18 | 27480 | 27.48 | 6.92 | 7.28 | 140 | 12 | 320 | 36 | 281 | 16 | NA | 600 | 0.2 | 23.56 | 1400000
2024-04-19 | 28580 | 28.58 | 7.15 | 7.25 | 130 | 14 | 312 | 36 | 286 | 17 | NA | 700 | 0.2 | 24.16 | 1200000
2024-04-20 | 27860 | 27.86 | 7.29 | 7.31 | 135 | 15 | 324 | 40 | 279 | 18 | NA | 400 | 0.3 | 22.63 | 1100000
2024-04-21 | 28080 | 28.08 | 7.24 | 7.29 | 140 | 14 | 332 | 44 | 293 | 15 | NA | 500 | 0.3 | 23.9 | 1300000
2024-04-22 | 27510 | 27.51 | 7.18 | 7.28 | 135 | 12 | 320 | 40 | 296 | 17 | NA | 400 | 0.2 | 23.18 | 1400000
2024-04-23 | 27460 | 27.46 | 7.31 | 7.22 | 130 | 14 | 308 | 40 | 276 | 16 | NA | 600 | 0.3 | 24.19 | 1700000
2024-04-24 | 26750 | 26.75 | 7.28 | 7.3 | 140 | 13 | 316 | 44 | 269 | 17 | NA | 700 | 0.3 | 24.33 | 1200000
2024-04-25 | 26750 | 26.75 | 7.3 | 7.33 | 130 | 12 | 324 | 36 | 284 | 16 | NA | 500 | 0.2 | 23.59 | 1300000
2024-04-26 | 27770 | 27.77 | 7.18 | 7.37 | 135 | 14 | 320 | 40 | 276 | 17 | NA | 400 | 0.3 | 23.08 | 1400000
2024-04-27 | 27840 | 27.84 | 7.15 | 7.36 | 140 | 15 | 316 | 40 | 282 | 16 | NA | 500 | 0.3 | 22.44 | 1200000
2024-04-28 | 29080 | 29.08 | 7.19 | 7.26 | 135 | 13 | 344 | 36 | 296 | 17 | NA | 400 | 0.2 | 23.6 | 1700000
2024-04-29 | 28730 | 28.73 | 7.28 | 7.2 | 145 | 12 | 328 | 40 | 287 | 16 | NA | 700 | 0.2 | 24.81 | 1300000
2024-04-30 | 28570 | 28.57 | 7.36 | 7.21 | 140 | 14 | 320 | 36 | 314 | 18 | NA | 600 | 0.3 | 23.58 | 1700000
Average | 28688.3333 | 28.6883 | 7.167 | 7.2893 | 137.8333 | 13.2667 | 319.8667 | 38.9333 | 284.1667 | 16.5 |  | 553.3333 | 0.25333 | 23.4233 | 1400000
860.65
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 26750 | 26.75 | 6.91 | 7.19 | 130 | 11 | 304 | 32 | 261 | 15 |  | 400 | 0.2 | 21.65 | 1100000
Max | 31500 | 31.5 | 7.42 | 7.44 | 150 | 15 | 344 | 44 | 314 | 18 |  | 800 | 0.3 | 24.81 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-04-01 | 13170 | 13.17 | 7.28 | 7.64 | 135 | 16 | 308 | 36 | 242 | 22 | NA | 500 | 0.3 | 23.02 | 1300000
2024-04-02 | 12470 | 12.47 | 7.32 | 7.6 | 130 | 17 | 296 | 36 | 227 | 25 | NA | 700 | 0.2 | 23.48 | 1400000
2024-04-03 | 13240 | 13.24 | 7.34 | 7.62 | 135 | 15 | 304 | 40 | 234 | 27 | NA | 400 | 0.3 | 23.18 | 1200000
2024-04-04 | 12570 | 12.57 | 7.41 | 7.59 | 125 | 16 | 300 | 36 | 239 | 23 | NA | 600 | 0.2 | 22.93 | 1300000
2024-04-05 | 13060 | 13.06 | 7.36 | 7.61 | 130 | 15 | 292 | 32 | 216 | 22 | NA | 500 | 0.3 | 23.34 | 1700000
2024-04-06 | 12520 | 12.52 | 7.24 | 7.58 | 140 | 17 | 304 | 40 | 229 | 25 | NA | 400 | 0.2 | 23.08 | 1200000
2024-04-07 | 11930 | 11.93 | 7.19 | 7.62 | 135 | 16 | 308 | 36 | 237 | 23 | NA | 500 | 0.3 | 22.74 | 1100000
2024-04-08 | 12470 | 12.47 | 7.28 | 7.47 | 130 | 18 | 276 | 40 | 217 | 27 | NA | 700 | 0.2 | 24.33 | 1300000
2024-04-09 | 12320 | 12.32 | 7.35 | 7.55 | 135 | 17 | 284 | 32 | 223 | 24 | NA | 800 | 0.3 | 23.15 | 1400000
2024-04-10 | 12590 | 12.59 | 7.31 | 7.53 | 130 | 16 | 280 | 36 | 211 | 21 | NA | 500 | 0.2 | 22.31 | 1200000
2024-04-11 | 11930 | 11.93 | 7.42 | 7.5 | 125 | 15 | 292 | 36 | 238 | 25 | NA | 700 | 0.3 | 23.15 | 1700000
2024-04-12 | 11810 | 11.81 | 7.44 | 7.54 | 140 | 16 | 300 | 32 | 227 | 21 | NA | 400 | 0.2 | 21.36 | 1300000
2024-04-13 | 11850 | 11.85 | 7.41 | 7.56 | 135 | 15 | 276 | 36 | 213 | 23 | NA | 600 | 0.3 | 23.67 | 1400000
2024-04-14 | 13210 | 13.21 | 7.32 | 7.66 | 140 | 17 | 288 | 32 | 223 | 26 | NA | 500 | 0.2 | 22.87 | 1200000
2024-04-15 | 11240 | 11.24 | 7.38 | 7.63 | 130 | 16 | 296 | 36 | 226 | 22 | NA | 700 | 0.3 | 23.02 | 1300000
2024-04-16 | 12750 | 12.75 | 7.43 | 7.67 | 140 | 15 | 304 | 32 | 242 | 21 | NA | 400 | 0.2 | 22.62 | 1700000
2024-04-17 | 11970 | 11.97 | 7.41 | 7.64 | 135 | 16 | 300 | 36 | 228 | 24 | NA | 600 | 0.3 | 23.43 | 1400000
2024-04-18 | 13140 | 13.14 | 7.36 | 7.65 | 120 | 15 | 296 | 32 | 252 | 25 | NA | 500 | 0.2 | 23.1 | 1200000
2024-04-19 | 14120 | 14.12 | 7.42 | 7.66 | 140 | 16 | 292 | 36 | 224 | 24 | NA | 700 | 0.3 | 22.81 | 1300000
2024-04-20 | 11950 | 11.95 | 7.39 | 7.68 | 135 | 15 | 300 | 32 | 237 | 21 | NA | 600 | 0.2 | 22.13 | 1700000
2024-04-21 | 12050 | 12.05 | 7.42 | 7.71 | 140 | 16 | 312 | 36 | 249 | 23 | NA | 400 | 0.3 | 23.16 | 1200000
2024-04-22 | 12920 | 12.92 | 7.45 | 7.67 | 135 | 17 | 296 | 36 | 218 | 24 | NA | 500 | 0.2 | 22.96 | 1400000
2024-04-23 | 12020 | 12.02 | 7.47 | 7.62 | 145 | 16 | 308 | 40 | 253 | 27 | NA | 700 | 0.3 | 24.06 | 1700000
2024-04-24 | 12550 | 12.55 | 7.51 | 7.6 | 140 | 15 | 316 | 36 | 242 | 24 | NA | 600 | 0.2 | 23.88 | 1300000
2024-04-25 | 12640 | 12.64 | 7.44 | 7.61 | 130 | 17 | 324 | 40 | 289 | 26 | NA | 400 | 0.3 | 22.1 | 1400000
2024-04-26 | 13570 | 13.57 | 7.38 | 7.64 | 145 | 16 | 296 | 36 | 223 | 21 | NA | 600 | 0.2 | 23.27 | 1700000
2024-04-27 | 12910 | 12.91 | 7.42 | 7.66 | 140 | 17 | 304 | 40 | 234 | 28 | NA | 800 | 0.3 | 24.03 | 1200000
2024-04-28 | 13760 | 13.76 | 7.51 | 7.63 | 145 | 16 | 328 | 36 | 272 | 24 | NA | 500 | 0.3 | 23.7 | 1400000
2024-04-29 | 13230 | 13.23 | 7.53 | 7.59 | 135 | 17 | 308 | 40 | 283 | 25 | NA | 700 | 0.2 | 22.33 | 1300000
2024-04-30 | 12590 | 12.59 | 7.63 | 7.55 | 140 | 15 | 292 | 36 | 225 | 23 | NA | 400 | 0.3 | 22.36 | 1700000
Average | 12618.3333 | 12.6183 | 7.394 | 7.6093 | 135.3333 | 16.0333 | 299.3333 | 36 | 235.7667 | 23.8667 |  | 563.3333 | 0.25333 | 23.0523 | 1386666.6667
378.55
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11240 | 11.24 | 7.19 | 7.47 | 120 | 15 | 276 | 32 | 211 | 21 |  | 400 | 0.2 | 21.36 | 1100000
Max | 14120 | 14.12 | 7.63 | 7.71 | 145 | 18 | 328 | 40 | 289 | 28 |  | 800 | 0.3 | 24.33 | 1700000