## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-08-01 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | 23.22 | 1700000 | Maintenance work for rising main from Ghagharnalla MPS to Numayadahi STP is in progress.
2022-08-02 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-08-03 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-08-04 | 8390 | 8.39 | 7.28 | 7.67 | 145 | 18 | 324 | 44 | 265 | 27 | NA | 600 | 0.3 | 24.27 | 1400000 | Maintenance work in rising main from Ghagharnalla MPS to Numayadahi STP was completed on 04.08.2022 at 5 PM. Subsequently, Ghagharnalla MPS, Sasus Khaderi SPS and Numayadahi STP were teken into operation.
2022-08-05 | 59640 | 59.64 | 7.18 | 7.85 | 140 | 12 | 320 | 48 | 252 | 25 | NA | 400 | 0.2 | 23.69 | 1200000
2022-08-06 | 67370 | 67.37 | 7.26 | 7.78 | 150 | 15 | 312 | 40 | 245 | 26 | NA | 500 | 0.3 | 24.59 | 1400000
2022-08-07 | 64530 | 64.53 | 7.46 | 7.64 | 140 | 13 | 328 | 36 | 265 | 22 | NA | 700 | 0.3 | 24.3 | 1300000
2022-08-08 | 64650 | 64.65 | 7.19 | 7.72 | 135 | 14 | 312 | 40 | 236 | 24 | NA | 600 | 0.3 | 23.38 | 1200000
2022-08-09 | 66110 | 66.11 | 7.22 | 7.76 | 140 | 15 | 324 | 44 | 252 | 27 | NA | 400 | 0.2 | 24.54 | 1400000
2022-08-10 | 55630 | 55.63 | 7.14 | 7.69 | 135 | 15 | 280 | 36 | 260 | 24 | NA | 600 | 0.3 | 24.37 | 1400000
2022-08-11 | 61520 | 61.52 | 7.25 | 7.78 | 130 | 12 | 308 | 40 | 258 | 24 | NA | 700 | 0.3 | 22.83 | 1200000
2022-08-12 | 63710 | 63.71 | 7.19 | 7.64 | 135 | 13 | 296 | 36 | 284 | 20 | NA | 500 | 0.3 | 24.19 | 1300000
2022-08-13 | 60150 | 60.15 | 7.22 | 7.7 | 130 | 14 | 320 | 40 | 236 | 22 | NA | 400 | 0.3 | 22.85 | 1400000
2022-08-14 | 61250 | 61.25 | 7.27 | 7.68 | 130 | 12 | 304 | 36 | 255 | 26 | NA | 600 | 0.3 | 23.5 | 1300000
2022-08-15 | 58070 | 58.07 | 7.54 | 7.69 | 140 | 15 | 312 | 40 | 280 | 22 | NA | 400 | 0.3 | 22.43 | 1200000
2022-08-16 | 55840 | 55.84 | 7.19 | 7.64 | 135 | 13 | 296 | 32 | 252 | 20 | NA | 500 | 0.3 | 23.71 | 1300000 | Sasur Kadheri SPS was stopped at 5:30 PM on 16.08.2022 due to rise in water level of Yamuna river because of flood.
2022-08-17 | 35660 | 35.66 | 7.22 | 7.78 | 140 | 11 | 280 | 36 | 236 | 22 | NA | 400 | 0.3 | 24.14 | 1200000
2022-08-18 | 32320 | 32.32 | 7.18 | 7.21 | 130 | 12 | 300 | 32 | 240 | 24 | NA | 600 | 0.3 | 22.41 | 1400000 | 1. Inlet gate of Ghagharnalla MPS was reduced by 70% for reducing raw sewage pumping from Ghagharnalla MPS at 10:30 AM on 18.08.2022 due to rise in water level of Yamuna river because of flood. 2. Sasur Kadheri SPS is not in operation since 16.08.2022 due to flood.
2022-08-19 | 31710 | 31.71 | 7.24 | 7.56 | 135 | 13 | 280 | 28 | 254 | 18 | NA | 500 | 0.2 | 23.5 | 1700000 | 1. Raw sewage pumping from Ghagarnalla MPS is reduced since 18.08.2022 due to flood. 2. Sasur Kadheri SPS is not in operation since 16.08.2022 due to flood.
2022-08-20 | 31950 | 31.95 | 7.21 | 7.64 | 125 | 12 | 308 | 40 | 248 | 22 | NA | 600 | 0.3 | 24.37 | 1400000
2022-08-21 | 34380 | 34.38 | 7.28 | 7.79 | 135 | 15 | 292 | 32 | 252 | 25 | NA | 400 | 0.3 | 22.51 | 1300000
2022-08-22 | 25750 | 25.75 | 7.21 | 7.39 | 130 | 13 | 284 | 40 | 220 | 18 | NA | 600 | 0.3 | 23.1 | 1700000
2022-08-23 | 20800 | 20.8 | 7.19 | 7.64 | 120 | 11 | 300 | 44 | 240 | 21 | NA | 500 | 0.2 | 21.99 | 1200000
2022-08-24 | 24100 | 24.1 | 7.23 | 7.58 | 125 | 14 | 308 | 36 | 264 | 24 | NA | 600 | 0.3 | 24.47 | 1300000
2022-08-25 | 26520 | 26.52 | 7.18 | 7.63 | 135 | 13 | 296 | 40 | 243 | 22 | NA | 400 | 0.2 | 24.59 | 1700000
2022-08-26 | 29700 | 29.7 | 7.24 | 7.78 | 140 | 12 | 292 | 32 | 262 | 25 | NA | 700 | 0.3 | 22.33 | 1200000
2022-08-27 | 38810 | 38.81 | 7.22 | 7.67 | 130 | 15 | 320 | 40 | 268 | 23 | NA | 500 | 0.3 | 22.74 | 1400000
2022-08-28 | 46630 | 46.63 | 7.26 | 7.72 | 140 | 14 | 288 | 36 | 256 | 22 | NA | 400 | 0.2 | 23.76 | 1300000
2022-08-29 | 50130 | 50.13 | 7.29 | 7.67 | 135 | 12 | 292 | 32 | 266 | 24 | NA | 600 | 0.3 | 24.1 | 1700000
2022-08-30 | 47090 | 47.09 | 7.22 | 7.73 | 140 | 15 | 304 | 36 | 257 | 26 | NA | 700 | 0.3 | 22.84 | 1400000
2022-08-31 | 40920 | 40.92 | 7.24 | 7.84 | 135 | 14 | 312 | 40 | 263 | 23 | NA | 500 | 0.3 | 24.21 | 1200000
Average | 40752.5806 | 40.7526 | 7.2429 | 7.6739 | 135 | 13.4643 | 303.2857 | 37.7143 | 253.8929 | 23.1429 | NA | 532.1429 | 0.27857 | 23.5493 | 1372413.7931
1263.33
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.14 | 7.21 | 120 | 11 | 280 | 28 | 220 | 18 |  | 400 | 0.2 | 21.99 | 1200000
Max | 67370 | 67.37 | 7.54 | 7.85 | 150 | 18 | 328 | 48 | 284 | 27 |  | 700 | 0.3 | 24.59 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-08-01 | 13030 | 13.03 | 7.27 | 7.33 | 153 | 20 | 348 | 32 | 310 | 28 | NA | 400 | 0.2 | 24 | 1200000 | Tapping point at Amitabh bachchan culvert is closed at 6:30 PM on 29.07.2022 due to increase in river level. Currently, raw sewage is being received from Allahpur drain and house connections.
2022-08-02 | 23150 | 23.15 | 7.23 | 7.28 | 159 | 22 | 356 | 40 | 295 | 30 | NA | 600 | 0.3 | 23.2 | 1700000
2022-08-03 | 22150 | 22.15 | 7.24 | 7.27 | 156 | 19 | 352 | 36 | 308 | 32 | NA | 500 | 0.3 | 23.8 | 1400000
2022-08-04 | 28490 | 28.49 | 7.29 | 7.47 | 162 | 20 | 356 | 40 | 305 | 35 | NA | 600 | 0.2 | 24.1 | 1300000 | Tapping point at Amitabh bachchan culvert was opened at 2:00 PM on 04.08.2022 due to increase in river level. Currently, complete raw sewage is being received at Salori STP.
2022-08-05 | 43200 | 43.2 | 7.21 | 7.32 | 159 | 26 | 352 | 44 | 312 | 40 | NA | 700 | 0.3 | 23.9 | 1200000
2022-08-06 | 39920 | 39.92 | 7.24 | 7.31 | 153 | 24 | 356 | 40 | 308 | 38 | NA | 800 | 0.3 | 24 | 1400000
2022-08-07 | 40340 | 40.34 | 7.15 | 7.26 | 156 | 26 | 352 | 44 | 303 | 39 | NA | 600 | 0.2 | 23.2 | 1700000
2022-08-08 | 35910 | 35.91 | 7.2 | 7.23 | 159 | 25 | 360 | 48 | 317 | 36 | NA | 400 | 0.2 | 23.5 | 1300000
2022-08-09 | 33340 | 33.34 | 7.31 | 7.4 | 156 | 23 | 356 | 40 | 322 | 34 | NA | 500 | 0.3 | 24.3 | 1400000
2022-08-10 | 31490 | 31.49 | 7.26 | 7.34 | 162 | 22 | 352 | 36 | 315 | 31 | NA | 600 | 0.3 | 25.2 | 1100000
2022-08-11 | 32280 | 32.28 | 7.34 | 7.45 | 159 | 20 | 348 | 28 | 302 | 28 | NA | 400 | 0.2 | 25.8 | 1400000
2022-08-12 | 32060 | 32.06 | 7.27 | 7.3 | 153 | 21 | 356 | 36 | 304 | 29 | NA | 500 | 0.3 | 25.6 | 1200000
2022-08-13 | 32190 | 32.19 | 7.28 | 7.47 | 159 | 24 | 352 | 32 | 310 | 30 | NA | 400 | 0.3 | 24.9 | 1100000
2022-08-14 | 32010 | 32.01 | 7.32 | 7.43 | 156 | 22 | 348 | 32 | 318 | 28 | NA | 600 | 0.2 | 25.1 | 1400000
2022-08-15 | 33390 | 33.39 | 7.29 | 7.37 | 162 | 24 | 356 | 36 | 302 | 31 | NA | 400 | 0.2 | 25 | 1200000
2022-08-16 | 21150 | 21.15 | 7.28 | 7.41 | 159 | 23 | 352 | 28 | 298 | 27 | NA | 500 | 0.2 | 24.5 | 1100000 | 1. Tapping point at Amitabh bachchan culvert is closed at 4:15 PM on 16.08.2022 due to increase in river level. 2. Inlet gate for raw sewage from Allahpur drain were closed at 10:15 AM on 16.08.2022 by flood department due to increase in river level. 3. Currently, raw sewage is being received from house connections only.
2022-08-17 | 8180 | 8.18 | 7.31 | 7.39 | 153 | 20 | 368 | 36 | 300 | 29 | NA | 400 | 0.3 | 25.2 | 1300000
2022-08-18 | 7250 | 7.25 | 7.42 | 7.56 | 156 | 18 | 356 | 32 | 303 | 26 | NA | 500 | 0.2 | 24.3 | 1200000
2022-08-19 | 8750 | 8.75 | 7.29 | 7.31 | 159 | 20 | 352 | 28 | 312 | 27 | NA | 600 | 0.2 | 24.9 | 1100000
2022-08-20 | 7140 | 7.14 | 7.38 | 7.52 | 156 | 17 | 356 | 32 | 308 | 25 | NA | 400 | 0.3 | 25.6 | 1300000
2022-08-21 | 14800 | 14.8 | 7.22 | 7.5 | 159 | 16 | 348 | 32 | 305 | 28 | NA | 500 | 0.2 | 24.8 | 1400000
2022-08-22 | 11940 | 11.94 | 7.24 | 7.41 | 156 | 14 | 352 | 28 | 302 | 26 | NA | 600 | 0.2 | 25.1 | 1100000
2022-08-23 | 11030 | 11.03 | 7.38 | 7.53 | 153 | 15 | 356 | 32 | 310 | 24 | NA | 400 | 0.3 | 25 | 1300000
2022-08-24 | 12850 | 12.85 | 7.35 | 7.48 | 150 | 16 | 348 | 28 | 309 | 25 | NA | 500 | 0.2 | 24.7 | 1200000
2022-08-25 | 11350 | 11.35 | 7.16 | 7.22 | 153 | 15 | 352 | 24 | 303 | 23 | NA | 600 | 0.3 | 25.4 | 1300000
2022-08-26 | 13890 | 13.89 | 7.24 | 7.31 | 156 | 14 | 356 | 28 | 283 | 25 | NA | 400 | 0.2 | 24.5 | 1100000
2022-08-27 | 13790 | 13.79 | 7.2 | 7.25 | 159 | 16 | 352 | 24 | 300 | 22 | NA | 500 | 0.2 | 24.9 | 1200000
2022-08-28 | 13020 | 13.02 | 7.52 | 7.65 | 153 | 17 | 356 | 28 | 302 | 20 | NA | 400 | 0.2 | 25 | 1400000
2022-08-29 | 13750 | 13.75 | 7.55 | 7.68 | 159 | 15 | 328 | 24 | 298 | 22 | NA | 600 | 0.2 | 24.7 | 1300000
2022-08-30 | 11660 | 11.66 | 7.52 | 7.63 | 156 | 14 | 356 | 28 | 309 | 23 | NA | 500 | 0.3 | 25.1 | 1100000
2022-08-31 | 10100 | 10.1 | 7.49 | 7.59 | 153 | 15 | 352 | 24 | 312 | 25 | NA | 400 | 0.3 | 25.8 | 1200000
Average | 21406.4516 | 21.4065 | 7.3048 | 7.4087 | 156.5806 | 19.4516 | 352.9032 | 32.9032 | 305.9677 | 28.5806 | NA | 509.6774 | 0.24516 | 24.6806 | 1277419.3548
663.6
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 7140 | 7.14 | 7.15 | 7.22 | 150 | 14 | 328 | 24 | 283 | 20 |  | 400 | 0.2 | 23.2 | 1100000
Max | 43200 | 43.2 | 7.55 | 7.68 | 162 | 26 | 368 | 48 | 322 | 40 |  | 800 | 0.3 | 25.8 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-08-01 | 27910 | 27.91 | 7.32 | 7.58 | 140 | 13 | 328 | 40 | 288 | 21 | NA | 600 | 0.2 | 24.25 | 1300000
2022-08-02 | 31220 | 31.22 | 7.19 | 7.66 | 136 | 14 | 316 | 36 | 274 | 18 | NA | 400 | 0.3 | 23.87 | 1700000
2022-08-03 | 30730 | 30.73 | 7.24 | 7.53 | 143 | 15 | 324 | 40 | 284 | 20 | NA | 700 | 0.2 | 24.46 | 1400000
2022-08-04 | 27750 | 27.75 | 7.29 | 7.61 | 133 | 12 | 320 | 36 | 279 | 19 | NA | 500 | 0.3 | 23.94 | 1300000
2022-08-05 | 28230 | 28.23 | 7.34 | 7.65 | 139 | 13 | 308 | 32 | 286 | 21 | NA | 600 | 0.2 | 23.38 | 1400000
2022-08-06 | 31670 | 31.67 | 7.22 | 7.69 | 133 | 12 | 312 | 36 | 271 | 22 | NA | 500 | 0.2 | 22.86 | 1200000
2022-08-07 | 31850 | 31.85 | 7.31 | 7.56 | 130 | 14 | 324 | 40 | 282 | 20 | NA | 700 | 0.3 | 23.38 | 1300000
2022-08-08 | 28190 | 28.19 | 7.43 | 7.66 | 136 | 15 | 316 | 44 | 276 | 19 | NA | 600 | 0.2 | 23.84 | 1100000
2022-08-09 | 28870 | 28.87 | 7.36 | 7.7 | 130 | 13 | 308 | 40 | 268 | 21 | NA | 400 | 0.3 | 24.36 | 1700000
2022-08-10 | 26960 | 26.96 | 7.28 | 7.63 | 133 | 14 | 320 | 36 | 273 | 22 | NA | 700 | 0.2 | 23.56 | 1400000
2022-08-11 | 27540 | 27.54 | 7.39 | 7.59 | 140 | 15 | 312 | 32 | 283 | 18 | NA | 500 | 0.3 | 23.93 | 1200000
2022-08-12 | 31020 | 31.02 | 7.43 | 7.68 | 136 | 14 | 308 | 40 | 265 | 22 | NA | 600 | 0.3 | 24.21 | 1300000
2022-08-13 | 21940 | 21.94 | 7.26 | 7.57 | 130 | 15 | 300 | 36 | 275 | 20 | NA | 500 | 0.2 | 23.74 | 1700000 | Retaining wall for nearby nalla is broken from 4:00 AM to 7:45 PM due to heavy rain hence raw sewage pumping is less.
2022-08-14 | 29910 | 29.91 | 7.34 | 7.65 | 126 | 13 | 304 | 44 | 261 | 21 | NA | 700 | 0.3 | 24.16 | 1400000
2022-08-15 | 28430 | 28.43 | 7.29 | 7.51 | 120 | 14 | 296 | 40 | 253 | 19 | NA | 400 | 0.2 | 23.59 | 1200000
2022-08-16 | 29190 | 29.19 | 7.24 | 7.57 | 123 | 13 | 288 | 44 | 279 | 22 | NA | 600 | 0.3 | 23.28 | 1400000
2022-08-17 | 28870 | 28.87 | 7.18 | 7.49 | 120 | 12 | 292 | 40 | 264 | 20 | NA | 500 | 0.2 | 24.29 | 1300000
2022-08-18 | 31190 | 31.19 | 7.15 | 7.42 | 116 | 13 | 272 | 36 | 255 | 23 | NA | 400 | 0.3 | 23.74 | 1700000 | 1. Inlet gate at tapping point for nearby drain is closed at around 9:30 AM on 25.08.2022 due to rise in water level of Yamuna river due to flood. 2. Currently, raw sewage is being received from Vivekanand park SPS and Kalimandir SPS.
2022-08-19 | 29700 | 29.7 | 7.26 | 7.51 | 110 | 14 | 260 | 40 | 241 | 21 | NA | 700 | 0.3 | 24.46 | 1400000
2022-08-20 | 27170 | 27.17 | 7.2 | 7.57 | 113 | 12 | 248 | 36 | 234 | 19 | NA | 500 | 0.2 | 23.94 | 1200000
2022-08-21 | 26810 | 26.81 | 7.31 | 7.65 | 106 | 14 | 236 | 32 | 218 | 20 | NA | 700 | 0.3 | 24.37 | 1300000
2022-08-22 | 27230 | 27.23 | 7.24 | 7.61 | 110 | 13 | 240 | 36 | 227 | 22 | NA | 600 | 0.2 | 23.17 | 1400000
2022-08-23 | 26480 | 26.48 | 7.17 | 7.54 | 103 | 12 | 228 | 40 | 196 | 21 | NA | 500 | 0.3 | 22.79 | 1700000
2022-08-24 | 27820 | 27.82 | 7.06 | 7.48 | 110 | 14 | 216 | 36 | 205 | 19 | NA | 400 | 0.3 | 22.17 | 1200000
2022-08-25 | 27040 | 27.04 | 7.21 | 7.56 | 106 | 15 | 208 | 40 | 194 | 20 | NA | 700 | 0.2 | 23.07 | 1400000
2022-08-26 | 27410 | 27.41 | 7.14 | 7.65 | 103 | 13 | 204 | 32 | 188 | 18 | NA | 600 | 0.3 | 23.47 | 1300000
2022-08-27 | 25780 | 25.78 | 7.19 | 7.52 | 110 | 14 | 212 | 36 | 197 | 21 | NA | 500 | 0.3 | 22.88 | 1700000
2022-08-28 | 26010 | 26.01 | 7.26 | 7.45 | 106 | 13 | 196 | 40 | 184 | 20 | NA | 700 | 0.2 | 22.36 | 1300000
2022-08-29 | 27450 | 27.45 | 7.21 | 7.58 | 103 | 15 | 204 | 36 | 191 | 22 | NA | 400 | 0.3 | 23.14 | 1200000
2022-08-30 | 27360 | 27.36 | 7.15 | 7.49 | 113 | 14 | 216 | 40 | 206 | 19 | NA | 600 | 0.3 | 22.74 | 1700000
2022-08-31 | 26880 | 26.88 | 7.31 | 7.43 | 120 | 13 | 232 | 32 | 217 | 20 | NA | 700 | 0.2 | 23.42 | 1400000
Average | 28213.2258 | 28.2132 | 7.2571 | 7.5739 | 121.8387 | 13.5484 | 272.5161 | 37.6774 | 245.6129 | 20.3226 | NA | 564.5161 | 0.25484 | 23.5748 | 1393548.3871
874.61
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 21940 | 21.94 | 7.06 | 7.42 | 103 | 12 | 196 | 32 | 184 | 18 |  | 400 | 0.2 | 22.17 | 1100000
Max | 31850 | 31.85 | 7.43 | 7.7 | 143 | 15 | 328 | 44 | 288 | 23 |  | 700 | 0.3 | 24.46 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-08-01 | 13590 | 13.59 | 7.27 | 7.55 | 140 | 15 | 320 | 40 | 271 | 22 | NA | 600 | 0.2 | 22.48 | 1400000
2022-08-02 | 15350 | 15.35 | 7.24 | 7.59 | 143 | 14 | 328 | 36 | 284 | 20 | NA | 500 | 0.2 | 21.67 | 1300000
2022-08-03 | 14690 | 14.69 | 7.19 | 7.63 | 139 | 16 | 316 | 40 | 269 | 23 | NA | 700 | 0.2 | 20.58 | 1700000
2022-08-04 | 15700 | 15.7 | 7.29 | 7.66 | 146 | 15 | 324 | 44 | 276 | 21 | NA | 400 | 0.3 | 22.56 | 1200000
2022-08-05 | 15310 | 15.31 | 7.26 | 7.71 | 136 | 14 | 312 | 40 | 271 | 22 | NA | 600 | 0.2 | 21.37 | 1300000
2022-08-06 | 15840 | 15.84 | 7.22 | 7.76 | 149 | 13 | 320 | 36 | 266 | 24 | NA | 500 | 0.2 | 23.16 | 1400000
2022-08-07 | 13730 | 13.73 | 7.31 | 7.69 | 143 | 14 | 316 | 40 | 278 | 23 | NA | 400 | 0.3 | 22.75 | 1200000
2022-08-08 | 13190 | 13.19 | 7.28 | 7.61 | 137 | 13 | 304 | 32 | 261 | 20 | NA | 500 | 0.2 | 21.68 | 1400000
2022-08-09 | 14290 | 14.29 | 7.23 | 7.58 | 131 | 15 | 312 | 36 | 273 | 22 | NA | 600 | 0.3 | 22.38 | 1700000
2022-08-10 | 13780 | 13.78 | 7.33 | 7.65 | 139 | 14 | 308 | 40 | 267 | 21 | NA | 700 | 0.2 | 22.68 | 1300000
2022-08-11 | 14190 | 14.19 | 7.25 | 7.56 | 146 | 13 | 320 | 32 | 280 | 20 | NA | 500 | 0.2 | 22.4 | 1100000
2022-08-12 | 13100 | 13.1 | 7.18 | 7.61 | 136 | 15 | 304 | 36 | 277 | 22 | NA | 400 | 0.3 | 21.98 | 1400000
2022-08-13 | 14720 | 14.72 | 7.27 | 7.52 | 143 | 14 | 316 | 32 | 265 | 19 | NA | 500 | 0.2 | 22.44 | 1200000
2022-08-14 | 14830 | 14.83 | 7.2 | 7.57 | 133 | 13 | 300 | 36 | 259 | 21 | NA | 400 | 0.3 | 22.34 | 1300000
2022-08-15 | 14120 | 14.12 | 7.29 | 7.64 | 136 | 14 | 308 | 40 | 269 | 23 | NA | 600 | 0.2 | 21.86 | 1700000
2022-08-16 | 14520 | 14.52 | 7.23 | 7.55 | 140 | 13 | 316 | 36 | 256 | 22 | NA | 500 | 0.2 | 22.11 | 1400000
2022-08-17 | 14270 | 14.27 | 7.32 | 7.57 | 133 | 14 | 324 | 40 | 267 | 23 | NA | 600 | 0.2 | 21.56 | 1300000
2022-08-18 | 13060 | 13.06 | 7.26 | 7.63 | 130 | 15 | 312 | 36 | 258 | 21 | NA | 400 | 0.3 | 22.13 | 1200000
2022-08-19 | 12840 | 12.84 | 7.24 | 7.59 | 136 | 13 | 304 | 32 | 270 | 20 | NA | 500 | 0.2 | 21.74 | 1400000
2022-08-20 | 12160 | 12.16 | 7.3 | 7.69 | 140 | 14 | 320 | 36 | 278 | 22 | NA | 600 | 0.3 | 22.53 | 1300000
2022-08-21 | 12350 | 12.35 | 7.33 | 7.64 | 135 | 15 | 308 | 40 | 271 | 24 | NA | 700 | 0.2 | 21.87 | 1200000
2022-08-22 | 13580 | 13.58 | 7.21 | 7.56 | 143 | 13 | 316 | 36 | 265 | 23 | NA | 500 | 0.3 | 22.46 | 1400000
2022-08-23 | 14650 | 14.65 | 7.28 | 7.68 | 133 | 14 | 312 | 32 | 259 | 21 | NA | 400 | 0.3 | 21.66 | 1700000
2022-08-24 | 14780 | 14.78 | 7.23 | 7.58 | 130 | 15 | 300 | 36 | 275 | 22 | NA | 600 | 0.2 | 21.35 | 1300000
2022-08-25 | 16470 | 16.47 | 7.33 | 7.61 | 123 | 14 | 304 | 32 | 261 | 20 | NA | 500 | 0.3 | 23.13 | 1200000
2022-08-26 | 12680 | 12.68 | 7.36 | 7.66 | 120 | 16 | 292 | 40 | 248 | 21 | NA | 700 | 0.2 | 21.85 | 1400000
2022-08-27 | 13640 | 13.64 | 7.18 | 7.46 | 117 | 15 | 280 | 36 | 236 | 23 | NA | 600 | 0.3 | 21.48 | 1200000
2022-08-28 | 12710 | 12.71 | 7.22 | 7.51 | 120 | 14 | 288 | 40 | 265 | 20 | NA | 400 | 0.2 | 22.27 | 1700000
2022-08-29 | 12510 | 12.51 | 7.29 | 7.58 | 111 | 13 | 276 | 36 | 255 | 22 | NA | 500 | 0.3 | 22.59 | 1400000
2022-08-30 | 12670 | 12.67 | 7.2 | 7.62 | 114 | 16 | 284 | 40 | 262 | 21 | NA | 600 | 0.3 | 21.76 | 1300000
2022-08-31 | 12700 | 12.7 | 7.24 | 7.68 | 127 | 15 | 304 | 36 | 271 | 23 | NA | 500 | 0.2 | 21.55 | 1700000
Average | 13936.129 | 13.9361 | 7.259 | 7.611 | 133.8387 | 14.2258 | 308 | 36.9032 | 266.5484 | 21.6452 | NA | 532.2581 | 0.24194 | 22.0765 | 1377419.3548
432.02
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 12160 | 12.16 | 7.18 | 7.46 | 111 | 13 | 276 | 32 | 236 | 19 |  | 400 | 0.2 | 20.58 | 1100000
Max | 16470 | 16.47 | 7.36 | 7.76 | 149 | 16 | 328 | 44 | 284 | 24 |  | 700 | 0.3 | 23.16 | 1700000