## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-08-01 | 59830 | 59.83 | 7.37 | 7.76 | 135 | 15 | 312 | 40 | 280 | 24 | NA | 500 | 0.3 | 23.57 | 1400000
2023-08-02 | 54850 | 54.85 | 7.32 | 7.72 | 140 | 13 | 308 | 36 | 246 | 21 | NA | 500 | 0.3 | 23.87 | 1700000
2023-08-03 | 60840 | 60.84 | 7.69 | 7.69 | 130 | 16 | 320 | 40 | 284 | 24 | NA | 600 | 0.3 | 24.04 | 1400000
2023-08-04 | 63940 | 63.94 | 7.34 | 7.76 | 135 | 17 | 296 | 44 | 280 | 23 | NA | 600 | 0.3 | 22.77 | 1300000
2023-08-05 | 63600 | 63.6 | 7.3 | 7.68 | 125 | 15 | 304 | 36 | 305 | 24 | NA | 700 | 0.3 | 24.09 | 1100000
2023-08-06 | 54580 | 54.58 | 7.34 | 7.57 | 120 | 15 | 312 | 40 | 264 | 23 | NA | 500 | 0.2 | 24.78 | 1400000 | Operations of Sasur Kadheri SPS were stopped from 9:40 PM on 06.08.2023 to 11:50 PM on 10.08.2023 as I&D was submerged in river water due to flood and water entered into the premises of SPS
2023-08-07 | 44900 | 44.9 | 7.32 | 7.59 | 130 | 14 | 256 | 40 | 234 | 21 | NA | 600 | 0.2 | 22.99 | 1700000
2023-08-08 | 39150 | 39.15 | 7.35 | 7.68 | 145 | 15 | 304 | 36 | 264 | 24 | NA | 400 | 0.3 | 23.22 | 1100000
2023-08-09 | 32340 | 32.34 | 7.32 | 7.71 | 135 | 14 | 276 | 40 | 271 | 24 | NA | 700 | 0.2 | 24.16 | 1400000
2023-08-10 | 43880 | 43.88 | 7.43 | 7.66 | 145 | 16 | 284 | 36 | 262 | 23 | NA | 500 | 0.2 | 22.7 | 1300000
2023-08-11 | 59150 | 59.15 | 7.38 | 7.72 | 130 | 17 | 300 | 44 | 281 | 25 | NA | 400 | 0.3 | 24.82 | 1700000
2023-08-12 | 60300 | 60.3 | 7.42 | 7.76 | 125 | 15 | 288 | 40 | 257 | 23 | NA | 600 | 0.2 | 23.38 | 1400000
2023-08-13 | 62200 | 62.2 | 7.31 | 7.69 | 140 | 17 | 316 | 44 | 288 | 25 | NA | 400 | 0.3 | 24.04 | 1100000
2023-08-14 | 61180 | 61.18 | 7.36 | 7.72 | 130 | 14 | 304 | 40 | 258 | 24 | NA | 700 | 0.3 | 24.79 | 1300000
2023-08-15 | 57740 | 57.74 | 7.21 | 7.74 | 145 | 16 | 312 | 44 | 242 | 22 | NA | 500 | 0.2 | 23.75 | 1400000
2023-08-16 | 59700 | 59.7 | 7.28 | 7.67 | 135 | 15 | 300 | 40 | 254 | 26 | NA | 700 | 0.3 | 24.34 | 1400000
2023-08-17 | 59120 | 59.12 | 7.22 | 7.74 | 140 | 17 | 308 | 44 | 262 | 28 | NA | 400 | 0.3 | 24.04 | 1300000
2023-08-18 | 60070 | 60.07 | 7.28 | 7.76 | 125 | 18 | 324 | 44 | 258 | 25 | NA | 600 | 0.2 | 24.54 | 1700000
2023-08-19 | 59530 | 59.53 | 7.26 | 7.74 | 135 | 16 | 320 | 40 | 262 | 26 | NA | 500 | 0.3 | 23.24 | 1400000
2023-08-20 | 60660 | 60.66 | 7.32 | 7.78 | 145 | 18 | 328 | 40 | 278 | 25 | NA | 400 | 0.2 | 24.37 | 1100000
2023-08-21 | 60800 | 60.8 | 7.36 | 7.66 | 140 | 18 | 320 | 44 | 266 | 27 | NA | 600 | 0.2 | 23.54 | 1300000
2023-08-22 | 52200 | 52.2 | 7.26 | 7.69 | 145 | 19 | 304 | 48 | 253 | 26 | NA | 500 | 0.3 | 24.4 | 1400000
2023-08-23 | 60400 | 60.4 | 7.19 | 7.7 | 135 | 18 | 288 | 40 | 239 | 27 | NA | 700 | 0.3 | 23.35 | 1700000
2023-08-24 | 61500 | 61.5 | 7.27 | 7.71 | 130 | 16 | 296 | 44 | 256 | 24 | NA | 400 | 0.2 | 23.44 | 1300000
2023-08-25 | 62330 | 62.33 | 7.26 | 7.62 | 130 | 15 | 304 | 36 | 248 | 22 | NA | 600 | 0.3 | 23.64 | 1400000
2023-08-26 | 58850 | 58.85 | 7.29 | 7.78 | 145 | 15 | 316 | 40 | 258 | 24 | NA | 500 | 0.3 | 24.01 | 1100000
2023-08-27 | 59180 | 59.18 | 7.24 | 7.62 | 140 | 16 | 300 | 44 | 247 | 23 | NA | 700 | 0.2 | 24.82 | 1300000
2023-08-28 | 57650 | 57.65 | 7.31 | 7.74 | 130 | 17 | 312 | 40 | 252 | 24 | NA | 400 | 0.3 | 23.54 | 1400000
2023-08-29 | 60450 | 60.45 | 7.36 | 7.78 | 135 | 17 | 304 | 44 | 272 | 26 | NA | 600 | 0.3 | 23.11 | 1700000
2023-08-30 | 62750 | 62.75 | 7.38 | 7.69 | 135 | 18 | 316 | 44 | 289 | 27 | NA | 500 | 0.2 | 24.79 | 1300000
2023-08-31 | 61120 | 61.12 | 7.28 | 7.71 | 140 | 17 | 304 | 40 | 267 | 26 | NA | 700 | 0.3 | 23.75 | 1700000
Average | 57251.2903 | 57.2513 | 7.3232 | 7.7045 | 135.3226 | 16.0968 | 304.3871 | 41.0323 | 263.7742 | 24.3871 | NA | 548.3871 | 0.26129 | 23.8674 | 1393548.3871
1774.79
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 32340 | 32.34 | 7.19 | 7.57 | 120 | 13 | 256 | 36 | 234 | 21 |  | 400 | 0.2 | 22.7 | 1100000
Max | 63940 | 63.94 | 7.69 | 7.78 | 145 | 19 | 328 | 48 | 305 | 28 |  | 700 | 0.3 | 24.82 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-08-01 | 40610 | 40.61 | 7.62 | 7.64 | 165 | 28 | 364 | 44 | 329 | 33 | NA | 600 | 0.3 | 24.3 | 1400000
2023-08-02 | 33800 | 33.8 | 7.58 | 7.65 | 145 | 22 | 352 | 36 | 338 | 31 | NA | 400 | 0.2 | 23.4 | 1100000
2023-08-03 | 35520 | 35.52 | 7.63 | 7.67 | 155 | 26 | 360 | 40 | 324 | 32 | NA | 700 | 0.3 | 25.3 | 1400000
2023-08-04 | 38540 | 38.54 | 7.56 | 7.62 | 160 | 25 | 352 | 36 | 318 | 31 | NA | 800 | 0.2 | 23.8 | 1700000
2023-08-05 | 35420 | 35.42 | 7.63 | 7.66 | 155 | 25 | 356 | 40 | 326 | 30 | NA | 600 | 0.3 | 24.3 | 1300000 | Sluice Gate at Amitabh Bachchan Culvert is closed at 8:00 PM on 05.08.2023 due to rise in river level because of flood.
2023-08-06 | 9910 | 9.91 | 7.58 | 7.69 | 160 | 20 | 204 | 32 | 218 | 33 | NA | 500 | 0.2 | 25.2 | 1100000 | 1. Sluice Gate at Amitabh Bachchan Culvert is closed at 8:00 PM on 05.08.2023 due to rise in river level because of flood. 2. Sluice gates of Allahapur drain are closed at 4:00 PM on 06.08.2023 due to rise in river level because of flood.
2023-08-07 | 8590 | 8.59 | 7.61 | 7.67 | 155 | 19 | 208 | 40 | 210 | 36 | NA | 700 | 0.3 | 24.6 | 1700000
2023-08-08 | 8000 | 8 | 7.63 | 7.66 | 165 | 17 | 236 | 36 | 253 | 35 | NA | 600 | 0.3 | 23.8 | 1200000
2023-08-09 | 7750 | 7.75 | 7.65 | 7.69 | 155 | 22 | 288 | 36 | 259 | 31 | NA | 400 | 0.2 | 24.7 | 1300000
2023-08-10 | 11710 | 11.71 | 7.63 | 7.82 | 160 | 20 | 320 | 32 | 292 | 27 | NA | 700 | 0.2 | 24.9 | 1400000 | 1. Sluice gates of Allahapur drain are opened at 9:00 PM on 10.08.2023 due to fall in river level. 2. Sluice Gate at Amitabh Bachchan Culvert is stiil close.
2023-08-11 | 18170 | 18.17 | 7.63 | 7.76 | 155 | 21 | 256 | 36 | 310 | 24 | NA | 600 | 0.3 | 23.7 | 1200000
2023-08-12 | 25120 | 25.12 | 7.36 | 7.68 | 165 | 22 | 252 | 36 | 322 | 28 | NA | 700 | 0.2 | 25.3 | 1300000
2023-08-13 | 31690 | 31.69 | 7.29 | 7.72 | 160 | 20 | 360 | 32 | 335 | 27 | NA | 500 | 0.3 | 24.6 | 1100000 | Sluice Gate at Amitabh Bachchan Culvert is opened at 4:30 PM on 13.08.2023 due to fall in river level. Now complete sewage is coming inside the STP.
2023-08-14 | 34550 | 34.55 | 7.63 | 7.73 | 155 | 23 | 364 | 40 | 329 | 29 | NA | 600 | 0.3 | 24.8 | 1400000
2023-08-15 | 34380 | 34.38 | 7.57 | 7.68 | 160 | 18 | 360 | 40 | 334 | 33 | NA | 500 | 0.2 | 23.9 | 1200000
2023-08-16 | 37880 | 37.88 | 7.62 | 7.68 | 145 | 19 | 352 | 36 | 324 | 32 | NA | 400 | 0.3 | 25.4 | 1300000
2023-08-17 | 39020 | 39.02 | 7.35 | 7.57 | 155 | 21 | 356 | 40 | 319 | 30 | NA | 700 | 0.2 | 24.6 | 1700000
2023-08-18 | 40430 | 40.43 | 7.46 | 7.63 | 160 | 20 | 364 | 40 | 313 | 29 | NA | 700 | 0.3 | 24.8 | 1400000
2023-08-19 | 36660 | 36.66 | 7.21 | 7.49 | 155 | 24 | 348 | 44 | 298 | 31 | NA | 700 | 0.3 | 23.1 | 1700000
2023-08-20 | 36670 | 36.67 | 7.35 | 7.66 | 165 | 27 | 356 | 40 | 308 | 30 | NA | 800 | 0.2 | 24.3 | 1400000
2023-08-21 | 38540 | 38.54 | 7.03 | 7.68 | 160 | 23 | 368 | 32 | 347 | 32 | NA | 600 | 0.3 | 23.5 | 1100000
2023-08-22 | 37840 | 37.84 | 7.24 | 7.64 | 155 | 22 | 360 | 36 | 321 | 30 | NA | 500 | 0.2 | 24.2 | 1300000
2023-08-23 | 36200 | 36.2 | 7.35 | 7.58 | 160 | 24 | 328 | 36 | 291 | 29 | NA | 600 | 0.2 | 23.7 | 1700000
2023-08-24 | 36360 | 36.36 | 7.03 | 7.55 | 155 | 19 | 352 | 34 | 305 | 26 | NA | 700 | 0.3 | 24.7 | 1200000
2023-08-25 | 37690 | 37.69 | 7.32 | 7.64 | 165 | 21 | 352 | 36 | 312 | 27 | NA | 500 | 0.3 | 24.6 | 1400000
2023-08-26 | 38150 | 38.15 | 7.09 | 7.68 | 155 | 20 | 364 | 40 | 326 | 30 | NA | 400 | 0.3 | 23.9 | 1300000
2023-08-27 | 39010 | 39.01 | 7.23 | 7.56 | 160 | 18 | 348 | 36 | 318 | 34 | NA | 600 | 0.2 | 23.2 | 1700000
2023-08-28 | 40330 | 40.33 | 7.31 | 7.58 | 155 | 19 | 356 | 36 | 337 | 29 | NA | 700 | 0.3 | 24.5 | 1200000
2023-08-29 | 39930 | 39.93 | 7.33 | 7.61 | 165 | 21 | 360 | 32 | 328 | 28 | NA | 400 | 0.2 | 23.8 | 1700000
2023-08-30 | 37860 | 37.86 | 7.38 | 7.55 | 170 | 27 | 352 | 44 | 332 | 31 | NA | 500 | 0.3 | 24.3 | 1400000
2023-08-31 | 38870 | 38.87 | 7.36 | 7.58 | 155 | 22 | 356 | 40 | 328 | 32 | NA | 700 | 0.3 | 25.4 | 1300000
Average | 31780.6452 | 31.7806 | 7.4277 | 7.6458 | 158.2258 | 21.7742 | 332.3871 | 37.3548 | 309.8065 | 30.3226 | NA | 593.5484 | 0.25806 | 24.3419 | 1374193.5484
985.2
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 7750 | 7.75 | 7.03 | 7.49 | 145 | 17 | 204 | 32 | 210 | 24 |  | 400 | 0.2 | 23.1 | 1100000
Max | 40610 | 40.61 | 7.65 | 7.82 | 170 | 28 | 368 | 44 | 347 | 36 |  | 800 | 0.3 | 25.4 | 1700000

## Kodra
kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-08-01 | 31270 | 31.27 | 7.22 | 7.53 | 125 | 11 | 308 | 36 | 272 | 23 | NA | 500 | 0.3 | 23.63 | 1300000
2023-08-02 | 30430 | 30.43 | 7.18 | 7.5 | 120 | 13 | 324 | 40 | 263 | 22 | NA | 400 | 0.2 | 24.31 | 1400000
2023-08-03 | 29770 | 29.77 | 7.2 | 7.52 | 130 | 14 | 312 | 44 | 282 | 21 | NA | 600 | 0.3 | 24.43 | 1200000
2023-08-04 | 31530 | 31.53 | 7.23 | 7.49 | 120 | 11 | 296 | 36 | 260 | 22 | NA | 500 | 0.2 | 23.54 | 1700000
2023-08-05 | 30790 | 30.79 | 7.18 | 7.47 | 125 | 10 | 284 | 32 | 266 | 20 | NA | 400 | 0.2 | 25.15 | 1100000
2023-08-06 | 31230 | 31.23 | 7.19 | 7.51 | 130 | 12 | 304 | 36 | 275 | 22 | NA | 700 | 0.3 | 24.82 | 1300000
2023-08-07 | 32240 | 32.24 | 7.16 | 7.48 | 120 | 11 | 288 | 32 | 270 | 20 | NA | 500 | 0.3 | 23.2 | 1400000
2023-08-08 | 29980 | 29.98 | 7.21 | 7.46 | 115 | 10 | 276 | 36 | 254 | 21 | NA | 600 | 0.3 | 23.24 | 1300000
2023-08-09 | 29220 | 29.22 | 7.17 | 7.44 | 125 | 12 | 292 | 32 | 260 | 20 | NA | 500 | 0.2 | 24.18 | 1200000
2023-08-10 | 29910 | 29.91 | 7.24 | 7.49 | 120 | 11 | 284 | 36 | 272 | 22 | NA | 400 | 0.3 | 24.69 | 1100000
2023-08-11 | 30400 | 30.4 | 7.26 | 7.47 | 125 | 13 | 260 | 40 | 254 | 21 | NA | 600 | 0.2 | 23.96 | 1700000
2023-08-12 | 30240 | 30.24 | 7.23 | 7.53 | 130 | 12 | 256 | 36 | 246 | 23 | NA | 500 | 0.2 | 23.99 | 1300000
2023-08-13 | 31330 | 31.33 | 7.27 | 7.5 | 115 | 13 | 264 | 32 | 250 | 22 | NA | 700 | 0.3 | 23.22 | 1200000
2023-08-14 | 30220 | 30.22 | 7.18 | 7.49 | 110 | 12 | 272 | 36 | 258 | 24 | NA | 600 | 0.2 | 23.19 | 1400000
2023-08-15 | 29540 | 29.54 | 7.23 | 7.51 | 120 | 14 | 256 | 40 | 247 | 22 | NA | 400 | 0.2 | 24.6 | 1200000
2023-08-16 | 30540 | 30.54 | 7.19 | 7.47 | 115 | 13 | 276 | 36 | 256 | 25 | NA | 700 | 0.2 | 24.42 | 1300000
2023-08-17 | 30160 | 30.16 | 7.28 | 7.52 | 110 | 12 | 284 | 36 | 262 | 24 | NA | 500 | 0.3 | 24.48 | 1400000
2023-08-18 | 31530 | 31.53 | 7.26 | 7.48 | 120 | 13 | 272 | 40 | 252 | 23 | NA | 600 | 0.3 | 24.33 | 1200000
2023-08-19 | 31030 | 31.03 | 7.32 | 7.53 | 105 | 10 | 252 | 32 | 244 | 22 | NA | 700 | 0.3 | 24.49 | 1400000
2023-08-20 | 30060 | 30.06 | 7.33 | 7.5 | 125 | 11 | 276 | 36 | 250 | 21 | NA | 600 | 0.3 | 24.57 | 1300000
2023-08-21 | 30440 | 30.44 | 7.3 | 7.46 | 110 | 12 | 260 | 32 | 253 | 22 | NA | 400 | 0.2 | 25.31 | 1200000
2023-08-22 | 30210 | 30.21 | 7.37 | 7.49 | 115 | 13 | 268 | 40 | 246 | 23 | NA | 500 | 0.2 | 25.25 | 1400000
2023-08-23 | 29620 | 29.62 | 7.16 | 7.46 | 125 | 14 | 272 | 36 | 240 | 24 | NA | 700 | 0.3 | 24.16 | 1200000
2023-08-24 | 29650 | 29.65 | 7.19 | 7.44 | 120 | 10 | 256 | 32 | 247 | 22 | NA | 400 | 0.3 | 24.43 | 1300000
2023-08-25 | 30060 | 30.06 | 7.18 | 7.42 | 125 | 11 | 264 | 36 | 258 | 23 | NA | 500 | 0.3 | 23.74 | 1400000
2023-08-26 | 28640 | 28.64 | 7.22 | 7.5 | 110 | 13 | 252 | 40 | 243 | 22 | NA | 600 | 0.2 | 23.92 | 1700000
2023-08-27 | 28480 | 28.48 | 7.31 | 7.47 | 105 | 16 | 276 | 44 | 262 | 24 | NA | 500 | 0.3 | 24.74 | 1400000
2023-08-28 | 29870 | 29.87 | 7.28 | 7.51 | 115 | 11 | 268 | 32 | 254 | 22 | NA | 700 | 0.3 | 24.2 | 1200000
2023-08-29 | 30180 | 30.18 | 7.26 | 7.55 | 125 | 12 | 284 | 36 | 262 | 23 | NA | 600 | 0.2 | 24.21 | 1300000
2023-08-30 | 29200 | 29.2 | 7.22 | 7.42 | 120 | 14 | 276 | 40 | 258 | 22 | NA | 700 | 0.3 | 24.43 | 1700000
2023-08-31 | 29900 | 29.9 | 7.26 | 7.52 | 110 | 13 | 268 | 36 | 253 | 21 | NA | 400 | 0.3 | 23.39 | 1400000
Average | 30247.4194 | 30.2474 | 7.2348 | 7.4881 | 118.871 | 12.1613 | 276.7742 | 36.3871 | 257.0645 | 22.1935 | NA | 548.3871 | 0.25806 | 24.2006 | 1341935.4839
937.67
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 28480 | 28.48 | 7.16 | 7.42 | 105 | 10 | 252 | 32 | 240 | 20 |  | 400 | 0.2 | 23.19 | 1100000
Max | 32240 | 32.24 | 7.37 | 7.55 | 130 | 16 | 324 | 44 | 282 | 25 |  | 700 | 0.3 | 25.31 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-08-01 | 13610 | 13.61 | 7.42 | 7.78 | 135 | 17 | 312 | 44 | 278 | 26 | NA | 400 | 0.3 | 23.18 | 1300000
2023-08-02 | 13850 | 13.85 | 7.38 | 7.71 | 125 | 18 | 304 | 48 | 282 | 25 | NA | 700 | 0.3 | 22.75 | 1400000
2023-08-03 | 13770 | 13.77 | 7.45 | 7.59 | 120 | 19 | 300 | 44 | 272 | 24 | NA | 500 | 0.2 | 22.59 | 1700000
2023-08-04 | 14600 | 14.6 | 7.27 | 7.65 | 125 | 17 | 286 | 48 | 264 | 23 | NA | 400 | 0.2 | 23.19 | 1500000
2023-08-05 | 14030 | 14.03 | 7.38 | 7.69 | 128 | 18 | 284 | 40 | 274 | 23 | NA | 600 | 0.3 | 24.35 | 1400000
2023-08-06 | 14060 | 14.06 | 7.4 | 7.35 | 120 | 19 | 304 | 36 | 278 | 28 | NA | 500 | 0.3 | 23.78 | 1300000
2023-08-07 | 13820 | 13.82 | 7.28 | 7.44 | 125 | 19 | 278 | 40 | 258 | 27 | NA | 400 | 0.2 | 22.94 | 1200000
2023-08-08 | 13490 | 13.49 | 7.25 | 7.86 | 126 | 18 | 272 | 44 | 260 | 22 | NA | 500 | 0.3 | 22.78 | 1400000
2023-08-09 | 13010 | 13.01 | 7.32 | 7.82 | 130 | 17 | 268 | 48 | 254 | 21 | NA | 600 | 0.3 | 23.28 | 1300000
2023-08-10 | 12990 | 12.99 | 7.28 | 7.85 | 120 | 18 | 270 | 44 | 258 | 22 | NA | 500 | 0.3 | 22.85 | 1700000
2023-08-11 | 13580 | 13.58 | 7.33 | 7.75 | 125 | 17 | 264 | 48 | 249 | 21 | NA | 400 | 0.2 | 22.75 | 1500000
2023-08-12 | 14960 | 14.96 | 7.26 | 7.61 | 130 | 18 | 272 | 40 | 253 | 24 | NA | 600 | 0.2 | 23.51 | 1400000
2023-08-13 | 13770 | 13.77 | 7.2 | 7.72 | 125 | 16 | 282 | 44 | 258 | 22 | NA | 500 | 0.3 | 22.86 | 1300000
2023-08-14 | 11740 | 11.74 | 7.24 | 7.68 | 130 | 18 | 276 | 48 | 249 | 21 | NA | 400 | 0.3 | 23.36 | 1700000
2023-08-15 | 13440 | 13.44 | 7.29 | 7.75 | 120 | 16 | 280 | 44 | 256 | 22 | NA | 500 | 0.2 | 23.61 | 1500000
2023-08-16 | 13990 | 13.99 | 7.32 | 7.78 | 125 | 17 | 284 | 48 | 264 | 23 | NA | 400 | 0.3 | 22.73 | 1300000
2023-08-17 | 14070 | 14.07 | 7.28 | 7.73 | 130 | 18 | 272 | 44 | 252 | 25 | NA | 600 | 0.2 | 23.28 | 1200000
2023-08-18 | 12640 | 12.64 | 7.32 | 7.76 | 120 | 16 | 282 | 48 | 264 | 22 | NA | 500 | 0.3 | 22.9 | 1500000
2023-08-19 | 11160 | 11.16 | 7.27 | 7.78 | 125 | 17 | 278 | 44 | 258 | 21 | NA | 400 | 0.3 | 23.12 | 1400000
2023-08-20 | 12790 | 12.79 | 7.3 | 7.74 | 120 | 18 | 286 | 48 | 268 | 22 | NA | 600 | 0.2 | 23.47 | 1300000
2023-08-21 | 13490 | 13.49 | 7.34 | 7.78 | 130 | 16 | 272 | 44 | 256 | 23 | NA | 500 | 0.3 | 22.78 | 1200000
2023-08-22 | 12830 | 12.83 | 7.26 | 7.65 | 135 | 18 | 278 | 48 | 260 | 22 | NA | 400 | 0.3 | 23.32 | 1400000
2023-08-23 | 13240 | 13.24 | 7.31 | 7.51 | 130 | 16 | 266 | 44 | 264 | 23 | NA | 600 | 0.3 | 23.67 | 1300000
2023-08-24 | 12800 | 12.8 | 7.29 | 7.74 | 125 | 18 | 276 | 48 | 258 | 22 | NA | 500 | 0.2 | 23.25 | 1200000
2023-08-25 | 12230 | 12.23 | 7.34 | 7.69 | 135 | 17 | 270 | 44 | 262 | 21 | NA | 400 | 0.3 | 23.7 | 1400000
2023-08-26 | 13230 | 13.23 | 7.27 | 7.72 | 130 | 18 | 282 | 48 | 268 | 22 | NA | 600 | 0.3 | 23.46 | 1500000
2023-08-27 | 12670 | 12.67 | 7.32 | 7.75 | 125 | 17 | 288 | 44 | 258 | 21 | NA | 500 | 0.2 | 23.53 | 1200000
2023-08-28 | 12300 | 12.3 | 7.36 | 7.81 | 135 | 18 | 276 | 48 | 266 | 23 | NA | 400 | 0.3 | 24.15 | 1300000
2023-08-29 | 12840 | 12.84 | 7.3 | 7.76 | 120 | 17 | 294 | 44 | 270 | 26 | NA | 600 | 0.2 | 23.85 | 1400000
2023-08-30 | 12650 | 12.65 | 7.26 | 7.71 | 130 | 16 | 300 | 48 | 278 | 23 | NA | 500 | 0.3 | 23.64 | 1500000
2023-08-31 | 12770 | 12.77 | 7.34 | 7.68 | 135 | 18 | 308 | 44 | 268 | 24 | NA | 400 | 0.2 | 23.4 | 1300000
Average | 13239.3548 | 13.2394 | 7.3106 | 7.7045 | 126.9032 | 17.4194 | 282.7097 | 45.0323 | 263.129 | 23.0323 | NA | 496.7742 | 0.26129 | 23.2913 | 1387096.7742
410.42
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11160 | 11.16 | 7.2 | 7.35 | 120 | 16 | 264 | 36 | 249 | 21 |  | 400 | 0.2 | 22.59 | 1200000
Max | 14960 | 14.96 | 7.45 | 7.86 | 135 | 19 | 312 | 48 | 282 | 28 |  | 700 | 0.3 | 24.35 | 1700000