## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-12-01 | 50030 | 50.03 | 7.19 | 7.7 | 139 | 16 | 328 | 36 | 248 | 19 | NA | 400 | 0.3 | 24.37 | 1400000
2022-12-02 | 50040 | 50.04 | 7.17 | 7.58 | 133 | 15 | 312 | 40 | 278 | 19 | NA | 500 | 0.3 | 23.79 | 1300000
2022-12-03 | 52120 | 52.12 | 7.29 | 7.65 | 136 | 16 | 336 | 40 | 255 | 18 | NA | 600 | 0.3 | 23.14 | 1200000
2022-12-04 | 55820 | 55.82 | 7.21 | 7.72 | 129 | 14 | 324 | 36 | 298 | 20 | NA | 400 | 0.3 | 23.42 | 1400000
2022-12-05 | 59550 | 59.55 | 7.2 | 7.68 | 136 | 18 | 320 | 40 | 266 | 19 | NA | 500 | 0.2 | 23.93 | 1700000
2022-12-06 | 58520 | 58.52 | 7.32 | 7.62 | 130 | 12 | 328 | 32 | 280 | 20 | NA | 600 | 0.3 | 23.05 | 1300000
2022-12-07 | 56630 | 56.63 | 7.19 | 7.64 | 143 | 16 | 340 | 40 | 244 | 19 | NA | 400 | 0.3 | 24.41 | 1200000
2022-12-08 | 57010 | 57.01 | 7.24 | 7.46 | 140 | 17 | 336 | 36 | 289 | 17 | NA | 600 | 0.2 | 25.01 | 1200000
2022-12-09 | 58300 | 58.3 | 7.16 | 7.62 | 136 | 13 | 328 | 36 | 240 | 20 | NA | 500 | 0.3 | 24.26 | 1700000
2022-12-10 | 59200 | 59.2 | 7.17 | 7.68 | 160 | 14 | 316 | 40 | 269 | 18 | NA | 400 | 0.4 | 24.28 | 1400000
2022-12-11 | 61480 | 61.48 | 7.16 | 7.72 | 140 | 17 | 324 | 36 | 272 | 19 | NA | 600 | 0.3 | 24.82 | 1100000
2022-12-12 | 59930 | 59.93 | 7.31 | 7.52 | 150 | 16 | 332 | 40 | 255 | 18 | NA | 500 | 0.2 | 23.7 | 1200000
2022-12-13 | 60130 | 60.13 | 7.42 | 7.67 | 135 | 17 | 328 | 44 | 260 | 20 | NA | 600 | 0.3 | 24.2 | 1200000
2022-12-14 | 60430 | 60.43 | 7.28 | 7.69 | 130 | 19 | 340 | 40 | 280 | 19 | NA | 400 | 0.4 | 24.8 | 1300000
2022-12-15 | 61490 | 61.49 | 7.1 | 7.72 | 140 | 15 | 336 | 36 | 232 | 18 | NA | 600 | 0.2 | 23.59 | 1200000
2022-12-16 | 58370 | 58.37 | 7.18 | 7.74 | 155 | 13 | 344 | 40 | 268 | 19 | NA | 500 | 0.3 | 24.91 | 1200000
2022-12-17 | 60660 | 60.66 | 7.16 | 7.64 | 130 | 15 | 320 | 36 | 282 | 20 | NA | 400 | 0.3 | 23.11 | 1700000
2022-12-18 | 63090 | 63.09 | 7.19 | 7.6 | 140 | 16 | 328 | 40 | 280 | 18 | NA | 600 | 0.4 | 24.82 | 1300000
2022-12-19 | 59780 | 59.78 | 7.22 | 7.72 | 145 | 17 | 320 | 44 | 268 | 21 | NA | 500 | 0.3 | 23.58 | 1700000
2022-12-20 | 60190 | 60.19 | 7.16 | 7.64 | 140 | 15 | 340 | 40 | 260 | 19 | NA | 400 | 0.4 | 24.91 | 1400000
2022-12-21 | 58750 | 58.75 | 7.24 | 7.72 | 130 | 16 | 332 | 40 | 252 | 20 | NA | 600 | 0.4 | 23.35 | 1700000
2022-12-22 | 57420 | 57.42 | 7.21 | 7.68 | 150 | 18 | 308 | 36 | 289 | 18 | NA | 400 | 0.3 | 23.91 | 1400000
2022-12-23 | 56950 | 56.95 | 7.24 | 7.7 | 145 | 16 | 340 | 40 | 252 | 23 | NA | 500 | 0.4 | 24.5 | 1300000
2022-12-24 | 58810 | 58.81 | 7.12 | 7.8 | 135 | 14 | 328 | 36 | 272 | 21 | NA | 500 | 0.4 | 23.89 | 1400000
2022-12-25 | 60720 | 60.72 | 7.18 | 7.66 | 140 | 12 | 324 | 40 | 268 | 20 | NA | 400 | 0.3 | 24.98 | 1200000
2022-12-26 | 60390 | 60.39 | 7.14 | 7.6 | 135 | 18 | 320 | 44 | 240 | 21 | NA | 600 | 0.3 | 23.93 | 1400000
2022-12-27 | 55810 | 55.81 | 7.22 | 7.72 | 150 | 18 | 336 | 36 | 292 | 24 | NA | 400 | 0.4 | 23.47 | 1300000
2022-12-28 | 57850 | 57.85 | 7.19 | 7.64 | 140 | 15 | 344 | 40 | 284 | 22 | NA | 500 | 0.4 | 23.44 | 1300000
2022-12-29 | 59770 | 59.77 | 7.15 | 7.72 | 130 | 13 | 324 | 44 | 266 | 20 | NA | 600 | 0.4 | 23.52 | 1400000
2022-12-30 | 60470 | 60.47 | 7.21 | 7.79 | 140 | 17 | 328 | 44 | 274 | 21 | NA | 400 | 0.3 | 23.56 | 1700000
2022-12-31 | 59430 | 59.43 | 7.15 | 7.66 | 140 | 16 | 320 | 40 | 263 | 21 | NA | 500 | 0.4 | 22.47 | 1300000
Average | 58359.3548 | 58.3594 | 7.2055 | 7.6677 | 139.4194 | 15.6129 | 328.5161 | 39.0968 | 266.9677 | 19.7097 | NA | 496.7742 | 0.32258 | 23.9716 | 1370967.7419
1809.14
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 50030 | 50.03 | 7.1 | 7.46 | 129 | 12 | 308 | 32 | 232 | 17 |  | 400 | 0.2 | 22.47 | 1100000
Max | 63090 | 63.09 | 7.42 | 7.8 | 160 | 19 | 344 | 44 | 298 | 24 |  | 600 | 0.4 | 25.01 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-12-01 | 35640 | 35.64 | 7.32 | 7.45 | 155 | 25 | 352 | 40 | 306 | 27 | NA | 800 | 0.2 | 24.8 | 1400000
2022-12-02 | 34430 | 34.43 | 7.27 | 7.43 | 160 | 24 | 356 | 36 | 318 | 26 | NA | 500 | 0.3 | 24.6 | 1300000
2022-12-03 | 33720 | 33.72 | 7.33 | 7.48 | 165 | 23 | 348 | 40 | 314 | 28 | NA | 700 | 0.3 | 23.9 | 1700000
2022-12-04 | 36630 | 36.63 | 7.37 | 7.46 | 155 | 25 | 340 | 36 | 298 | 32 | NA | 500 | 0.2 | 24.2 | 1300000
2022-12-05 | 38470 | 38.47 | 7.51 | 7.63 | 160 | 24 | 352 | 40 | 308 | 34 | NA | 600 | 0.2 | 25.1 | 1400000
2022-12-06 | 36110 | 36.11 | 7.32 | 7.47 | 155 | 26 | 368 | 44 | 324 | 37 | NA | 800 | 0.3 | 24.8 | 1100000
2022-12-07 | 36020 | 36.02 | 7.3 | 7.52 | 160 | 26 | 360 | 44 | 315 | 38 | NA | 600 | 0.2 | 25.3 | 1400000
2022-12-08 | 37530 | 37.53 | 7.38 | 7.52 | 165 | 25 | 352 | 40 | 332 | 39 | NA | 400 | 0.3 | 24.6 | 1200000
2022-12-09 | 35830 | 35.83 | 7.36 | 7.49 | 155 | 26 | 356 | 44 | 326 | 37 | NA | 500 | 0.2 | 25 | 1100000
2022-12-10 | 36190 | 36.19 | 7.31 | 7.54 | 160 | 24 | 360 | 40 | 338 | 40 | NA | 700 | 0.3 | 23.7 | 1300000
2022-12-11 | 37480 | 37.48 | 7.28 | 7.42 | 155 | 27 | 352 | 48 | 305 | 42 | NA | 800 | 0.3 | 24.2 | 1700000
2022-12-12 | 35570 | 35.57 | 7.27 | 7.49 | 160 | 25 | 348 | 44 | 296 | 41 | NA | 600 | 0.2 | 24.6 | 1400000
2022-12-13 | 35080 | 35.08 | 7.35 | 7.38 | 155 | 24 | 356 | 43 | 312 | 38 | NA | 500 | 0.3 | 24.6 | 1200000
2022-12-14 | 36390 | 36.39 | 7.32 | 7.45 | 160 | 26 | 352 | 46 | 309 | 40 | NA | 700 | 0.2 | 24.5 | 1700000
2022-12-15 | 40660 | 40.66 | 7.36 | 7.52 | 155 | 25 | 348 | 48 | 302 | 42 | NA | 800 | 0.3 | 24.8 | 1400000
2022-12-16 | 36570 | 36.57 | 7.41 | 7.48 | 160 | 24 | 360 | 44 | 292 | 40 | NA | 600 | 0.3 | 25.1 | 1100000
2022-12-17 | 35030 | 35.03 | 7.38 | 7.5 | 165 | 23 | 352 | 40 | 298 | 35 | NA | 500 | 0.3 | 25.3 | 1100000
2022-12-18 | 38890 | 38.89 | 7.35 | 7.46 | 160 | 22 | 356 | 36 | 316 | 32 | NA | 400 | 0.2 | 24.9 | 1200000
2022-12-19 | 41320 | 41.32 | 7.41 | 7.52 | 155 | 24 | 360 | 40 | 288 | 34 | NA | 700 | 0.3 | 25.2 | 1400000
2022-12-20 | 44710 | 44.71 | 7.31 | 7.47 | 160 | 23 | 340 | 40 | 312 | 31 | NA | 800 | 0.2 | 24.3 | 1700000
2022-12-21 | 43180 | 43.18 | 7.38 | 7.49 | 165 | 24 | 364 | 44 | 328 | 39 | NA | 700 | 0.2 | 23.9 | 1300000
2022-12-22 | 39020 | 39.02 | 7.42 | 7.54 | 155 | 25 | 368 | 40 | 327 | 38 | NA | 500 | 0.3 | 23.4 | 1100000
2022-12-23 | 39340 | 39.34 | 7.4 | 7.51 | 160 | 24 | 360 | 36 | 336 | 35 | NA | 600 | 0.3 | 23.7 | 1200000
2022-12-24 | 38610 | 38.61 | 7.36 | 7.48 | 165 | 26 | 356 | 40 | 318 | 34 | NA | 500 | 0.2 | 24 | 1400000
2022-12-25 | 39860 | 39.86 | 7.32 | 7.45 | 155 | 25 | 364 | 48 | 315 | 45 | NA | 700 | 0.3 | 24.5 | 1300000
2022-12-26 | 40870 | 40.87 | 7.35 | 7.5 | 165 | 26 | 360 | 44 | 324 | 42 | NA | 800 | 0.3 | 23.8 | 1200000
2022-12-27 | 40730 | 40.73 | 7.34 | 7.55 | 155 | 24 | 352 | 40 | 318 | 41 | NA | 600 | 0.3 | 24.4 | 1400000
2022-12-28 | 42120 | 42.12 | 7.39 | 7.52 | 150 | 23 | 348 | 36 | 326 | 31 | NA | 500 | 0.2 | 24.7 | 1700000
2022-12-29 | 37170 | 37.17 | 7.4 | 7.49 | 155 | 25 | 356 | 40 | 317 | 33 | NA | 700 | 0.3 | 23.6 | 1300000
2022-12-30 | 37520 | 37.52 | 7.33 | 7.58 | 160 | 26 | 340 | 44 | 330 | 35 | NA | 600 | 0.2 | 24.3 | 1100000
2022-12-31 | 37670 | 37.67 | 7.41 | 7.51 | 155 | 27 | 360 | 40 | 298 | 36 | NA | 500 | 0.3 | 24.8 | 1200000
Average | 38011.6129 | 38.0116 | 7.3552 | 7.4935 | 158.5484 | 24.7097 | 354.7097 | 41.4516 | 314.3871 | 36.1935 | NA | 619.3548 | 0.25806 | 24.471 | 1332258.0645
1178.36
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 33720 | 33.72 | 7.27 | 7.38 | 150 | 22 | 340 | 36 | 288 | 26 |  | 400 | 0.2 | 23.4 | 1100000
Max | 44710 | 44.71 | 7.51 | 7.63 | 165 | 27 | 368 | 48 | 338 | 45 |  | 800 | 0.3 | 25.3 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-12-01 | 28340 | 28.34 | 7.29 | 7.49 | 140 | 14 | 320 | 36 | 289 | 20 | NA | 700 | 0.4 | 23.65 | 1400000
2022-12-02 | 27900 | 27.9 | 7.18 | 7.38 | 135 | 15 | 308 | 40 | 278 | 22 | NA | 500 | 0.5 | 23.29 | 1700000
2022-12-03 | 25230 | 25.23 | 7.38 | 7.43 | 140 | 12 | 316 | 32 | 293 | 18 | NA | 600 | 0.4 | 23.56 | 1300000
2022-12-04 | 28710 | 28.71 | 7.46 | 7.55 | 130 | 13 | 300 | 36 | 286 | 21 | NA | 800 | 0.3 | 24.17 | 1400000
2022-12-05 | 27440 | 27.44 | 7.54 | 7.68 | 135 | 14 | 312 | 40 | 272 | 19 | NA | 700 | 0.4 | 24.42 | 1700000
2022-12-06 | 26820 | 26.82 | 7.59 | 7.65 | 140 | 13 | 324 | 36 | 301 | 22 | NA | 600 | 0.5 | 23.85 | 1300000
2022-12-07 | 27130 | 27.13 | 7.41 | 7.58 | 140 | 15 | 316 | 40 | 293 | 18 | NA | 800 | 0.4 | 23.53 | 1700000
2022-12-08 | 28690 | 28.69 | 7.08 | 7.19 | 145 | 12 | 304 | 36 | 282 | 20 | NA | 700 | 0.5 | 24.27 | 1400000
2022-12-09 | 28970 | 28.97 | 6.94 | 7.09 | 150 | 11 | 312 | 32 | 297 | 23 | NA | 400 | 0.4 | 24.09 | 1700000
2022-12-10 | 28760 | 28.76 | 7.24 | 7.16 | 140 | 13 | 308 | 40 | 288 | 20 | NA | 700 | 0.5 | 23.77 | 1400000
2022-12-11 | 29350 | 29.35 | 7.23 | 7.15 | 135 | 14 | 312 | 36 | 290 | 22 | NA | 500 | 0.4 | 24.37 | 1300000
2022-12-12 | 28160 | 28.16 | 7.28 | 7.2 | 145 | 15 | 360 | 40 | 240 | 19 | NA | 600 | 0.3 | 23.57 | 1700000
2022-12-13 | 26720 | 26.72 | 7.23 | 7.27 | 140 | 12 | 316 | 40 | 287 | 20 | NA | 500 | 0.4 | 23.97 | 1400000
2022-12-14 | 27870 | 27.87 | 7.31 | 7.21 | 150 | 14 | 324 | 36 | 281 | 19 | NA | 700 | 0.5 | 24.02 | 1700000
2022-12-15 | 27110 | 27.11 | 7.14 | 7.17 | 135 | 15 | 312 | 44 | 272 | 22 | NA | 600 | 0.4 | 23.87 | 1300000
2022-12-16 | 27490 | 27.49 | 7.29 | 7.2 | 130 | 16 | 308 | 40 | 265 | 21 | NA | 500 | 0.4 | 24.21 | 1400000
2022-12-17 | 28030 | 28.03 | 7.27 | 7.18 | 140 | 13 | 316 | 44 | 280 | 20 | NA | 600 | 0.5 | 23.45 | 1700000
2022-12-18 | 27670 | 27.67 | 7.24 | 7.21 | 145 | 14 | 320 | 36 | 271 | 22 | NA | 700 | 0.4 | 24.15 | 1300000
2022-12-19 | 26850 | 26.85 | 7.26 | 7.17 | 135 | 12 | 312 | 36 | 268 | 20 | NA | 500 | 0.5 | 24.07 | 1400000
2022-12-20 | 26240 | 26.24 | 7.21 | 7.15 | 140 | 13 | 324 | 40 | 276 | 21 | NA | 700 | 0.5 | 23.85 | 1300000
2022-12-21 | 27470 | 27.47 | 7.18 | 7.11 | 145 | 14 | 308 | 44 | 282 | 22 | NA | 600 | 0.4 | 23.51 | 1700000
2022-12-22 | 26820 | 26.82 | 7.22 | 7.13 | 150 | 12 | 316 | 44 | 273 | 24 | NA | 700 | 0.5 | 24.27 | 1400000
2022-12-23 | 25740 | 25.74 | 7.17 | 7.11 | 140 | 14 | 304 | 36 | 261 | 19 | NA | 500 | 0.5 | 23.48 | 1300000
2022-12-24 | 26660 | 26.66 | 7.23 | 7.15 | 145 | 15 | 312 | 40 | 292 | 22 | NA | 700 | 0.4 | 23.92 | 1700000
2022-12-25 | 28180 | 28.18 | 7.26 | 7.23 | 135 | 13 | 320 | 36 | 297 | 23 | NA | 500 | 0.5 | 24.15 | 1300000
2022-12-26 | 26890 | 26.89 | 7.25 | 7.15 | 130 | 15 | 316 | 44 | 273 | 24 | NA | 800 | 0.5 | 24.09 | 1700000
2022-12-27 | 26310 | 26.31 | 7.18 | 7.14 | 140 | 14 | 308 | 36 | 268 | 25 | NA | 600 | 0.4 | 23.53 | 1400000
2022-12-28 | 28460 | 28.46 | 7.19 | 7.28 | 145 | 13 | 316 | 44 | 276 | 24 | NA | 700 | 0.5 | 23.51 | 1300000
2022-12-29 | 26820 | 26.82 | 7.21 | 7.51 | 140 | 12 | 312 | 32 | 266 | 20 | NA | 500 | 0.4 | 23.85 | 1400000
2022-12-30 | 28510 | 28.51 | 7.23 | 7.49 | 150 | 13 | 324 | 40 | 280 | 21 | NA | 400 | 0.5 | 24.17 | 1700000
2022-12-31 | 28770 | 28.77 | 7.26 | 7.54 | 145 | 14 | 308 | 36 | 271 | 22 | NA | 600 | 0.5 | 24.36 | 1300000
Average | 27551.9355 | 27.5519 | 7.2565 | 7.2887 | 140.4839 | 13.5161 | 315.0968 | 38.4516 | 278.9677 | 21.129 | NA | 612.9032 | 0.44194 | 23.9023 | 1474193.5484
854.11
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 25230 | 25.23 | 6.94 | 7.09 | 130 | 11 | 300 | 32 | 240 | 18 |  | 400 | 0.3 | 23.29 | 1300000
Max | 29350 | 29.35 | 7.59 | 7.68 | 150 | 16 | 360 | 44 | 301 | 25 |  | 800 | 0.5 | 24.42 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-12-01 | 14150 | 14.15 | 7.32 | 7.6 | 135 | 15 | 308 | 40 | 294 | 21 | NA | 600 | 0.3 | 23.79 | 1400000
2022-12-02 | 12850 | 12.85 | 7.24 | 7.49 | 145 | 17 | 320 | 44 | 286 | 24 | NA | 800 | 0.4 | 23.45 | 1700000
2022-12-03 | 12330 | 12.33 | 7.29 | 7.41 | 140 | 16 | 312 | 48 | 278 | 23 | NA | 500 | 0.3 | 24.12 | 1200000
2022-12-04 | 13390 | 13.39 | 7.18 | 7.58 | 135 | 15 | 324 | 40 | 293 | 24 | NA | 700 | 0.4 | 23.58 | 1400000
2022-12-05 | 13480 | 13.48 | 7.36 | 7.46 | 140 | 17 | 316 | 44 | 274 | 22 | NA | 600 | 0.3 | 23.21 | 1300000
2022-12-06 | 13450 | 13.45 | 7.44 | 7.35 | 136 | 18 | 332 | 40 | 312 | 25 | NA | 800 | 0.4 | 23.43 | 1700000
2022-12-07 | 11980 | 11.98 | 7.37 | 7.48 | 150 | 17 | 324 | 48 | 288 | 24 | NA | 500 | 0.3 | 23.89 | 1400000
2022-12-08 | 14240 | 14.24 | 6.74 | 6.75 | 140 | 18 | 316 | 44 | 296 | 27 | NA | 400 | 0.4 | 24.28 | 1400000
2022-12-09 | 13290 | 13.29 | 6.81 | 6.68 | 145 | 17 | 328 | 44 | 304 | 26 | NA | 600 | 0.3 | 23.64 | 1700000
2022-12-10 | 13580 | 13.58 | 7.19 | 7.08 | 140 | 16 | 324 | 48 | 280 | 27 | NA | 500 | 0.4 | 23.8 | 1300000
2022-12-11 | 13890 | 13.89 | 7.12 | 7.26 | 145 | 17 | 308 | 44 | 294 | 26 | NA | 400 | 0.3 | 24.35 | 1700000
2022-12-12 | 13910 | 13.91 | 7.24 | 7.44 | 150 | 18 | 312 | 44 | 310 | 26 | NA | 700 | 0.4 | 23.4 | 1400000
2022-12-13 | 14250 | 14.25 | 7.27 | 7.43 | 145 | 19 | 316 | 48 | 302 | 28 | NA | 600 | 0.3 | 24.3 | 1300000
2022-12-14 | 14480 | 14.48 | 7.32 | 7.23 | 140 | 18 | 320 | 44 | 308 | 28 | NA | 500 | 0.4 | 23.87 | 1700000
2022-12-15 | 13930 | 13.93 | 7.29 | 7.38 | 145 | 17 | 312 | 48 | 305 | 25 | NA | 400 | 0.3 | 24.04 | 1400000
2022-12-16 | 13720 | 13.72 | 7.38 | 7.4 | 140 | 18 | 324 | 40 | 297 | 26 | NA | 600 | 0.4 | 23.87 | 1300000
2022-12-17 | 14090 | 14.09 | 7.27 | 7.31 | 150 | 16 | 316 | 44 | 301 | 24 | NA | 700 | 0.3 | 24.28 | 1700000
2022-12-18 | 13850 | 13.85 | 7.24 | 7.34 | 145 | 17 | 312 | 48 | 285 | 28 | NA | 500 | 0.4 | 23.77 | 1700000
2022-12-19 | 14010 | 14.01 | 7.29 | 7.37 | 150 | 16 | 304 | 40 | 299 | 25 | NA | 600 | 0.3 | 23.24 | 1300000
2022-12-20 | 12970 | 12.97 | 7.26 | 7.29 | 140 | 14 | 308 | 44 | 291 | 26 | NA | 400 | 0.4 | 24.13 | 1200000
2022-12-21 | 13860 | 13.86 | 7.14 | 7.25 | 135 | 18 | 316 | 40 | 286 | 24 | NA | 700 | 0.3 | 23.43 | 1400000
2022-12-22 | 12850 | 12.85 | 7.21 | 7.33 | 145 | 14 | 324 | 48 | 279 | 26 | NA | 500 | 0.4 | 24.08 | 1300000
2022-12-23 | 12160 | 12.6 | 7.19 | 7.28 | 140 | 17 | 312 | 40 | 294 | 23 | NA | 600 | 0.3 | 23.75 | 1700000
2022-12-24 | 12120 | 12.12 | 7.13 | 7.35 | 155 | 18 | 308 | 44 | 288 | 25 | NA | 400 | 0.4 | 24.27 | 1400000
2022-12-25 | 13120 | 13.21 | 7.23 | 7.51 | 135 | 14 | 320 | 40 | 276 | 22 | NA | 600 | 0.3 | 23.86 | 1700000
2022-12-26 | 12910 | 12.91 | 7.35 | 7.45 | 145 | 18 | 304 | 40 | 271 | 28 | NA | 500 | 0.4 | 24.11 | 1300000
2022-12-27 | 12330 | 12.33 | 7.02 | 7.39 | 150 | 19 | 300 | 48 | 283 | 21 | NA | 700 | 0.3 | 23.98 | 1200000
2022-12-28 | 12540 | 12.54 | 7.21 | 7.41 | 140 | 15 | 320 | 40 | 272 | 25 | NA | 600 | 0.4 | 24.27 | 1400000
2022-12-29 | 12680 | 12.68 | 7.31 | 7.37 | 135 | 18 | 312 | 40 | 288 | 21 | NA | 400 | 0.3 | 23.39 | 1700000
2022-12-30 | 12800 | 12.8 | 7.28 | 7.42 | 145 | 19 | 308 | 48 | 296 | 26 | NA | 700 | 0.4 | 24.91 | 1300000
2022-12-31 | 12440 | 12.44 | 7.07 | 7.36 | 140 | 16 | 316 | 40 | 279 | 27 | NA | 600 | 0.3 | 23.44 | 1700000
Average | 13279.0323 | 13.2961 | 7.2181 | 7.3371 | 142.6129 | 16.8387 | 315.3548 | 43.6129 | 290.6129 | 24.9355 | NA | 570.9677 | 0.34839 | 23.8687 | 1461290.3226
412.18
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11980 | 11.98 | 6.74 | 6.68 | 135 | 14 | 300 | 40 | 271 | 21 |  | 400 | 0.3 | 23.21 | 1200000
Max | 14480 | 14.48 | 7.44 | 7.6 | 155 | 19 | 332 | 48 | 312 | 28 |  | 800 | 0.4 | 24.91 | 1700000