## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-12-01 | 56470 | 56.47 | 7.16 | 7.8 | 140 | 16 | 316 | 44 | 282 | 24 | NA | 500 | 0.3 | 24.2 | 1700000
2023-12-02 | 52080 | 52.08 | 7.22 | 7.84 | 145 | 17 | 304 | 40 | 268 | 22 | NA | 400 | 0.3 | 23.33 | 1200000
2023-12-03 | 59800 | 59.8 | 7.12 | 7.78 | 130 | 14 | 320 | 36 | 255 | 24 | NA | 500 | 0.2 | 23.5 | 1400000
2023-12-04 | 58580 | 58.58 | 7.06 | 7.77 | 135 | 16 | 300 | 44 | 260 | 23 | NA | 700 | 0.3 | 24.52 | 1300000
2023-12-05 | 57410 | 57.41 | 7.1 | 7.76 | 130 | 14 | 312 | 40 | 272 | 23 | NA | 400 | 0.3 | 23.69 | 1100000
2023-12-06 | 58590 | 58.59 | 7.29 | 7.82 | 145 | 15 | 304 | 36 | 276 | 22 | NA | 600 | 0.2 | 23.94 | 1200000
2023-12-07 | 59220 | 59.22 | 7.18 | 7.79 | 140 | 16 | 316 | 44 | 268 | 24 | NA | 500 | 0.3 | 23.31 | 1400000
2023-12-08 | 60800 | 60.8 | 7.23 | 7.86 | 135 | 15 | 324 | 44 | 274 | 23 | NA | 700 | 0.3 | 24.4 | 1400000
2023-12-09 | 58170 | 58.17 | 7.25 | 7.81 | 145 | 18 | 308 | 40 | 284 | 24 | NA | 600 | 0.2 | 22.99 | 1300000
2023-12-10 | 57880 | 57.88 | 7.22 | 7.78 | 145 | 17 | 316 | 40 | 267 | 22 | NA | 400 | 0.3 | 24.5 | 1100000
2023-12-11 | 58850 | 58.85 | 7.25 | 7.83 | 130 | 16 | 328 | 44 | 278 | 24 | NA | 700 | 0.3 | 23.28 | 1200000
2023-12-12 | 58600 | 58.6 | 7.2 | 7.87 | 135 | 14 | 340 | 36 | 286 | 21 | NA | 600 | 0.2 | 23.61 | 1700000
2023-12-13 | 57850 | 57.85 | 7.22 | 7.81 | 135 | 15 | 324 | 40 | 287 | 20 | NA | 400 | 0.3 | 24.08 | 1400000
2023-12-14 | 57650 | 57.65 | 7.41 | 7.9 | 145 | 15 | 320 | 44 | 253 | 23 | NA | 400 | 0.3 | 23.09 | 1200000
2023-12-15 | 58970 | 58.97 | 7.36 | 7.89 | 145 | 17 | 316 | 40 | 266 | 24 | NA | 600 | 0.2 | 23.12 | 1100000
2023-12-16 | 60400 | 60.4 | 7.37 | 7.93 | 130 | 16 | 300 | 44 | 265 | 23 | NA | 500 | 0.3 | 23.26 | 1700000
2023-12-17 | 58700 | 58.7 | 7.4 | 7.86 | 135 | 16 | 316 | 44 | 288 | 21 | NA | 700 | 0.3 | 24.06 | 1400000
2023-12-18 | 60140 | 60.14 | 7.36 | 7.82 | 125 | 14 | 324 | 40 | 292 | 25 | NA | 400 | 0.2 | 23.1 | 1200000
2023-12-19 | 58420 | 58.42 | 7.41 | 7.84 | 140 | 17 | 304 | 44 | 286 | 27 | NA | 600 | 0.3 | 24.22 | 1700000
2023-12-20 | 57610 | 57.61 | 7.33 | 7.86 | 145 | 18 | 296 | 40 | 256 | 25 | NA | 400 | 0.3 | 23.12 | 1300000
2023-12-21 | 60000 | 60 | 7.34 | 7.87 | 130 | 17 | 312 | 40 | 264 | 24 | NA | 700 | 0.2 | 22.77 | 1200000
2023-12-22 | 59780 | 59.78 | 7.36 | 7.9 | 135 | 16 | 312 | 44 | 252 | 25 | NA | 600 | 0.3 | 23.84 | 1400000
2023-12-23 | 60300 | 60.3 | 7.31 | 7.88 | 130 | 14 | 320 | 36 | 260 | 26 | NA | 400 | 0.3 | 24.06 | 1100000
2023-12-24 | 58650 | 58.65 | 7.27 | 7.9 | 135 | 16 | 316 | 40 | 248 | 22 | NA | 600 | 0.3 | 23.88 | 1200000
2023-12-25 | 60000 | 60 | 7.3 | 7.92 | 145 | 18 | 324 | 44 | 276 | 26 | NA | 700 | 0.2 | 23.81 | 1400000
2023-12-26 | 57020 | 57.02 | 7.29 | 7.93 | 140 | 16 | 308 | 40 | 270 | 24 | NA | 400 | 0.3 | 22.04 | 1200000
2023-12-27 | 60150 | 60.15 | 7.34 | 7.91 | 130 | 14 | 316 | 36 | 284 | 26 | NA | 700 | 0.3 | 23.4 | 1400000
2023-12-28 | 56900 | 56.9 | 7.22 | 7.94 | 135 | 16 | 324 | 40 | 289 | 27 | NA | 500 | 0.2 | 24.18 | 1100000
2023-12-29 | 32150 | 32.15 | 7.21 | 7.92 | 125 | 14 | 304 | 36 | 266 | 23 | NA | 600 | 0.3 | 23.26 | 1400000 | Ghagharnalla MPS was shutdown from 4:00 PM on 29.12.2023 to 12:00 PM on 30.12.2023 for rectification of leakge in rising main from Ghagharnalla MPS to Numayadahi STP. Subsequently, Numayadahi STP and Sasur Kadheri SPS were also shutdown.
2023-12-30 | 28620 | 28.62 | 7.19 | 7.94 | 135 | 13 | 312 | 40 | 290 | 25 | NA | 400 | 0.3 | 24.1 | 1300000
2023-12-31 | 60700 | 60.7 | 7.19 | 7.99 | 140 | 16 | 320 | 36 | 280 | 26 | NA | 600 | 0.2 | 23.05 | 1700000
Average | 56789.0323 | 56.789 | 7.2632 | 7.8619 | 136.6129 | 15.6774 | 314.7097 | 40.5161 | 272.3226 | 23.8065 |  | 541.9355 | 0.26774 | 23.6035 | 1335483.871
1760.46
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 28620 | 28.62 | 7.06 | 7.76 | 125 | 13 | 296 | 36 | 248 | 20 |  | 400 | 0.2 | 22.04 | 1100000
Max | 60800 | 60.8 | 7.41 | 7.99 | 145 | 18 | 340 | 44 | 292 | 27 |  | 700 | 0.3 | 24.52 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | 22 |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-12-01 | 42860 | 42.86 | 7.74 | 7.78 | 165 | 27 | 352 | 44 | 326 | 34 | NA | 400 | 0.3 | 21.9 | 1400000
2023-12-02 | 43440 | 43.44 | 7.72 | 7.75 | 170 | 29 | 364 | 48 | 346 | 37 | NA | 500 | 0.3 | 22.6 | 1300000
2023-12-03 | 44010 | 44.01 | 7.48 | 7.74 | 165 | 28 | 368 | 48 | 354 | 38 | NA | 700 | 0.2 | 23.2 | 1700000
2023-12-04 | 41110 | 41.11 | 7.52 | 7.61 | 155 | 24 | 360 | 40 | 356 | 36 | NA | 600 | 0.3 | 23.9 | 1200000
2023-12-05 | 40430 | 40.43 | 7.5 | 7.62 | 160 | 27 | 364 | 44 | 355 | 35 | NA | 400 | 0.3 | 23.1 | 1400000
2023-12-06 | 45200 | 45.2 | 7.55 | 7.67 | 165 | 29 | 352 | 44 | 328 | 37 | NA | 500 | 0.3 | 23.5 | 1700000
2023-12-07 | 41300 | 41.3 | 7.48 | 7.56 | 160 | 28 | 344 | 48 | 296 | 40 | NA | 700 | 0.2 | 22.9 | 1300000
2023-12-08 | 44290 | 44.29 | 7.52 | 7.68 | 155 | 23 | 348 | 44 | 323 | 43 | NA | 500 | 0.3 | 23.6 | 1400000
2023-12-09 | 43260 | 43.26 | 7.56 | 7.63 | 150 | 21 | 352 | 44 | 332 | 41 | NA | 600 | 0.2 | 23.9 | 1300000
2023-12-10 | 43540 | 43.54 | 7.55 | 7.68 | 155 | 22 | 360 | 40 | 338 | 39 | NA | 400 | 0.3 | 23.2 | 1200000
2023-12-11 | 39180 | 39.18 | 7.51 | 7.57 | 160 | 24 | 372 | 48 | 354 | 42 | NA | 700 | 0.3 | 24 | 1400000
2023-12-12 | 42540 | 42.54 | 7.49 | 7.72 | 160 | 22 | 364 | 44 | 348 | 43 | NA | 500 | 0.2 | 24.6 | 1700000
2023-12-13 | 42510 | 42.51 | 7.58 | 7.73 | 155 | 23 | 348 | 48 | 335 | 40 | NA | 600 | 0.3 | 23.9 | 1300000
2023-12-14 | 39260 | 39.26 | 7.58 | 7.76 | 165 | 26 | 352 | 44 | 340 | 45 | NA | 400 | 0.2 | 23.5 | 1100000
2023-12-15 | 35430 | 35.43 | 7.62 | 7.71 | 150 | 21 | 344 | 40 | 312 | 40 | NA | 600 | 0.3 | 24.78 | 1400000
2023-12-16 | 38620 | 38.62 | 7.59 | 7.62 | 155 | 20 | 340 | 36 | 288 | 33 | NA | 500 | 0.3 | 24.7 | 1300000
2023-12-17 | 38680 | 38.68 | 7.61 | 7.64 | 160 | 21 | 348 | 36 | 311 | 31 | NA | 700 | 0.2 | 18.41 | 1700000
2023-12-18 | 35910 | 35.91 | 7.57 | 7.62 | 165 | 22 | 360 | 48 | 280 | 32 | NA | 500 | 0.3 | 23.07 | 1400000
2023-12-19 | 36530 | 36.53 | 7.65 | 7.57 | 160 | 23 | 340 | 36 | 298 | 34 | NA | 600 | 0.2 | 23.24 | 1100000
2023-12-20 | 35020 | 35.02 | 7.63 | 7.54 | 155 | 21 | 348 | 40 | 306 | 37 | NA | 400 | 0.3 | 22.74 | 1300000
2023-12-21 | 35430 | 35.43 | 7.66 | 7.51 | 160 | 22 | 360 | 36 | 357 | 35 | NA | 500 | 0.3 | 23.09 | 1700000
2023-12-22 | 35770 | 35.77 | 7.63 | 7.52 | 155 | 21 | 344 | 40 | 312 | 36 | NA | 700 | 0.2 | 23.18 | 1400000
2023-12-23 | 36030 | 36.03 | 7.58 | 7.54 | 165 | 24 | 360 | 40 | 342 | 35 | NA | 600 | 0.3 | 23.47 | 1300000
2023-12-24 | 40270 | 40.27 | 7.64 | 7.45 | 160 | 22 | 364 | 44 | 327 | 37 | NA | 700 | 0.3 | 22.77 | 1400000
2023-12-25 | 41120 | 41.12 | 7.58 | 7.47 | 165 | 26 | 352 | 40 | 313 | 36 | NA | 500 | 0.3 | 23.28 | 1700000
2023-12-26 | 46070 | 46.07 | 7.62 | 7.49 | 160 | 25 | 348 | 44 | 330 | 38 | NA | 400 | 0.2 | 23.67 | 1200000
2023-12-27 | 44510 | 44.51 | 7.58 | 7.46 | 170 | 24 | 360 | 48 | 318 | 36 | NA | 600 | 0.2 | 24.33 | 1400000
2023-12-28 | 40600 | 40.6 | 7.63 | 7.35 | 165 | 25 | 364 | 44 | 344 | 37 | NA | 500 | 0.3 | 22.18 | 1100000
2023-12-29 | 39640 | 39.64 | 7.59 | 7.46 | 155 | 22 | 348 | 40 | 332 | 34 | NA | 700 | 0.2 | 23.81 | 1700000
2023-12-30 | 38060 | 38.06 | 7.61 | 7.38 | 165 | 25 | 344 | 40 | 321 | 37 | NA | 600 | 0.3 | 22.23 | 1400000
2023-12-31 | 38340 | 38.34 | 7.64 | 7.41 | 160 | 27 | 360 | 44 | 343 | 35 | NA | 500 | 0.3 | 23.24 | 1300000
Average | 40289.0323 | 40.289 | 7.5874 | 7.5884 | 160.1613 | 24 | 354.3226 | 42.7097 | 327.9032 | 37.1935 |  | 551.6129 | 0.26452 | 23.2255 | 1393548.3871
1248.96
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 35020 | 35.02 | 7.48 | 7.35 | 150 | 20 | 340 | 36 | 280 | 31 |  | 400 | 0.2 | 18.41 | 1100000
Max | 46070 | 46.07 | 7.74 | 7.78 | 170 | 29 | 372 | 48 | 357 | 45 |  | 700 | 0.3 | 24.78 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-12-01 | 29050 | 29.05 | 7.34 | 7.42 | 130 | 15 | 324 | 44 | 296 | 23 | NA | 500 | 0.3 | 23.6 | 1400000
2023-12-02 | 29490 | 29.49 | 7.03 | 7.51 | 140 | 11 | 336 | 36 | 308 | 26 | NA | 400 | 0.2 | 23.38 | 1700000
2023-12-03 | 30090 | 30.09 | 7.16 | 7.48 | 135 | 14 | 320 | 40 | 291 | 25 | NA | 500 | 0.2 | 23.5 | 1300000
2023-12-04 | 28880 | 28.88 | 7.22 | 7.46 | 130 | 15 | 340 | 44 | 314 | 23 | NA | 600 | 0.3 | 23.14 | 1100000
2023-12-05 | 28310 | 28.31 | 7.41 | 7.49 | 120 | 10 | 360 | 32 | 342 | 24 | NA | 400 | 0.2 | 22.88 | 1400000
2023-12-06 | 29530 | 29.53 | 7.14 | 7.43 | 125 | 11 | 364 | 36 | 353 | 25 | NA | 600 | 0.2 | 23.47 | 1300000
2023-12-07 | 31800 | 31.8 | 6.94 | 7.42 | 120 | 11 | 380 | 32 | 375 | 23 | NA | 700 | 0.2 | 23.71 | 1200000
2023-12-08 | 30760 | 30.76 | 7.02 | 7.38 | 125 | 12 | 388 | 36 | 392 | 24 | NA | 600 | 0.3 | 24.21 | 1700000
2023-12-09 | 30300 | 30.3 | 7.13 | 7.37 | 130 | 11 | 372 | 36 | 351 | 23 | NA | 400 | 0.3 | 23.29 | 1400000
2023-12-10 | 29900 | 29.9 | 7.08 | 7.38 | 125 | 12 | 324 | 40 | 318 | 24 | NA | 500 | 0.2 | 22.99 | 1100000
2023-12-11 | 29990 | 29.99 | 7.21 | 7.39 | 130 | 13 | 320 | 36 | 307 | 26 | NA | 700 | 0.2 | 23.22 | 1300000
2023-12-12 | 28510 | 28.51 | 7.17 | 7.41 | 125 | 11 | 332 | 32 | 322 | 24 | NA | 400 | 0.2 | 23.74 | 1200000
2023-12-13 | 27750 | 27.75 | 7.24 | 7.36 | 135 | 10 | 328 | 36 | 308 | 22 | NA | 700 | 0.2 | 22.96 | 1400000
2023-12-14 | 29020 | 29.02 | 7.27 | 7.35 | 130 | 11 | 340 | 32 | 301 | 21 | NA | 500 | 0.2 | 23.38 | 1100000
2023-12-15 | 29570 | 29.57 | 7.24 | 7.36 | 135 | 12 | 352 | 36 | 318 | 23 | NA | 400 | 0.3 | 24.35 | 1400000
2023-12-16 | 29980 | 29.98 | 7.27 | 7.35 | 130 | 11 | 344 | 36 | 326 | 24 | NA | 500 | 0.3 | 23.43 | 1300000
2023-12-17 | 30650 | 30.65 | 7.28 | 7.36 | 125 | 12 | 332 | 32 | 313 | 23 | NA | 400 | 0.3 | 24.07 | 1100000
2023-12-18 | 29230 | 29.23 | 7.29 | 7.35 | 125 | 12 | 340 | 36 | 318 | 25 | NA | 700 | 0.2 | 23.39 | 1700000
2023-12-19 | 29840 | 29.84 | 7.24 | 7.37 | 135 | 11 | 352 | 36 | 322 | 22 | NA | 600 | 0.3 | 22.86 | 1400000
2023-12-20 | 29480 | 29.48 | 7.27 | 7.36 | 135 | 12 | 320 | 40 | 295 | 21 | NA | 400 | 0.3 | 23.52 | 1100000
2023-12-21 | 28560 | 28.56 | 7.3 | 7.34 | 120 | 13 | 312 | 36 | 286 | 23 | NA | 700 | 0.2 | 24.17 | 1700000
2023-12-22 | 29470 | 29.47 | 7.39 | 7.32 | 130 | 12 | 348 | 40 | 341 | 24 | NA | 500 | 0.3 | 23.49 | 1200000
2023-12-23 | 28830 | 28.83 | 7.4 | 7.3 | 125 | 13 | 312 | 37 | 290 | 25 | NA | 600 | 0.3 | 23.82 | 1400000
2023-12-24 | 30610 | 30.61 | 7.19 | 7.36 | 130 | 14 | 320 | 40 | 303 | 26 | NA | 500 | 0.3 | 24.29 | 1100000
2023-12-25 | 28060 | 28.06 | 7.17 | 7.38 | 125 | 12 | 316 | 40 | 292 | 20 | NA | 400 | 0.2 | 24.46 | 1300000
2023-12-26 | 28400 | 28.4 | 7.22 | 7.4 | 120 | 13 | 308 | 36 | 288 | 23 | NA | 600 | 0.3 | 24.67 | 1200000
2023-12-27 | 28420 | 28.42 | 7.26 | 7.37 | 130 | 11 | 324 | 32 | 297 | 22 | NA | 500 | 0.2 | 23.81 | 1400000
2023-12-28 | 28550 | 28.55 | 7.24 | 7.4 | 125 | 10 | 332 | 36 | 306 | 23 | NA | 400 | 0.3 | 23.43 | 1300000
2023-12-29 | 27920 | 27.92 | 7.28 | 7.39 | 130 | 11 | 316 | 32 | 301 | 24 | NA | 700 | 0.2 | 24.14 | 1200000
2023-12-30 | 28810 | 28.81 | 7.28 | 7.37 | 125 | 12 | 312 | 36 | 295 | 25 | NA | 400 | 0.3 | 22.58 | 1100000
2023-12-31 | 28460 | 28.46 | 7.22 | 7.34 | 135 | 11 | 332 | 32 | 305 | 21 | NA | 600 | 0.2 | 23.45 | 1400000
Average | 29297.4194 | 29.2974 | 7.2226 | 7.3861 | 128.3871 | 11.9032 | 335.4839 | 36.2903 | 315.2903 | 23.4516 |  | 529.0323 | 0.24839 | 23.5935 | 1319354.8387
908.22
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 27750 | 27.75 | 6.94 | 7.3 | 120 | 10 | 308 | 32 | 286 | 20 |  | 400 | 0.2 | 22.58 | 1100000
Max | 31800 | 31.8 | 7.41 | 7.51 | 140 | 15 | 388 | 44 | 392 | 26 |  | 700 | 0.3 | 24.67 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-12-01 | 12050 | 12.05 | 6.72 | 7.54 | 130 | 15 | 300 | 32 | 234 | 27 | NA | 500 | 0.3 | 24.12 | 1200000
2023-12-02 | 12540 | 12.54 | 7.06 | 7.69 | 140 | 16 | 292 | 36 | 226 | 26 | NA | 700 | 0.2 | 23.74 | 1400000
2023-12-03 | 12140 | 12.14 | 7.28 | 7.72 | 135 | 15 | 288 | 36 | 218 | 25 | NA | 600 | 0.3 | 23.46 | 1300000
2023-12-04 | 11560 | 11.56 | 7.18 | 7.7 | 130 | 16 | 296 | 32 | 224 | 27 | NA | 400 | 0.2 | 23.8 | 1700000
2023-12-05 | 12300 | 12.3 | 7.23 | 7.68 | 140 | 15 | 300 | 40 | 228 | 29 | NA | 500 | 0.3 | 24.09 | 1500000
2023-12-06 | 11560 | 11.56 | 7.19 | 7.73 | 135 | 17 | 304 | 36 | 232 | 23 | NA | 700 | 0.2 | 23.94 | 1200000
2023-12-07 | 11660 | 11.66 | 7.17 | 7.67 | 130 | 16 | 312 | 40 | 238 | 24 | NA | 600 | 0.3 | 24.12 | 1300000
2023-12-08 | 12330 | 12.33 | 7.23 | 7.52 | 125 | 15 | 292 | 36 | 223 | 23 | NA | 400 | 0.2 | 23.62 | 1700000
2023-12-09 | 12410 | 12.41 | 7.26 | 7.51 | 135 | 16 | 296 | 32 | 226 | 24 | NA | 700 | 0.3 | 24.36 | 1400000
2023-12-10 | 13240 | 13.24 | 7.18 | 7.66 | 130 | 15 | 312 | 36 | 242 | 25 | NA | 500 | 0.2 | 23.16 | 1200000
2023-12-11 | 14030 | 14.03 | 7.14 | 7.73 | 130 | 17 | 308 | 36 | 238 | 26 | NA | 600 | 0.3 | 23.96 | 1300000
2023-12-12 | 13600 | 13.6 | 7.22 | 7.78 | 135 | 16 | 292 | 32 | 220 | 25 | NA | 400 | 0.2 | 23.46 | 1100000
2023-12-13 | 12820 | 12.82 | 7.32 | 7.58 | 130 | 14 | 288 | 36 | 215 | 24 | NA | 700 | 0.2 | 23.72 | 1200000
2023-12-14 | 12360 | 12.36 | 7.11 | 7.67 | 140 | 16 | 284 | 36 | 205 | 25 | NA | 500 | 0.3 | 24.08 | 1300000
2023-12-15 | 12510 | 12.51 | 7.09 | 7.72 | 130 | 15 | 300 | 40 | 230 | 23 | NA | 600 | 0.2 | 24.16 | 1700000
2023-12-16 | 11800 | 11.8 | 7.15 | 7.58 | 140 | 16 | 312 | 36 | 235 | 22 | NA | 400 | 0.3 | 24.3 | 1400000
2023-12-17 | 13580 | 13.58 | 7.16 | 7.69 | 135 | 14 | 292 | 32 | 223 | 23 | NA | 700 | 0.2 | 23.36 | 1100000
2023-12-18 | 13610 | 13.61 | 7.22 | 7.62 | 130 | 16 | 296 | 36 | 229 | 27 | NA | 500 | 0.2 | 24.08 | 1200000
2023-12-19 | 13940 | 13.94 | 7.26 | 7.64 | 135 | 15 | 304 | 32 | 237 | 26 | NA | 600 | 0.3 | 23.78 | 1700000
2023-12-20 | 13730 | 13.73 | 7.18 | 7.62 | 140 | 16 | 292 | 36 | 221 | 27 | NA | 400 | 0.2 | 24.24 | 1300000
2023-12-21 | 13360 | 13.36 | 7.08 | 7.67 | 130 | 15 | 296 | 32 | 228 | 24 | NA | 700 | 0.3 | 24.56 | 1400000
2023-12-22 | 12120 | 12.12 | 7.19 | 7.57 | 140 | 16 | 304 | 36 | 235 | 26 | NA | 600 | 0.2 | 23.92 | 1200000
2023-12-23 | 12460 | 12.46 | 7.24 | 7.61 | 135 | 14 | 288 | 32 | 219 | 25 | NA | 500 | 0.3 | 24.13 | 1700000
2023-12-24 | 12980 | 12.98 | 7.18 | 7.63 | 140 | 16 | 300 | 36 | 232 | 24 | NA | 400 | 0.2 | 23.87 | 1100000
2023-12-25 | 11650 | 11.65 | 7.2 | 7.66 | 135 | 17 | 312 | 40 | 242 | 26 | NA | 600 | 0.3 | 24.18 | 1300000
2023-12-26 | 13150 | 13.15 | 7.16 | 7.7 | 130 | 16 | 292 | 36 | 221 | 25 | NA | 700 | 0.2 | 23.98 | 1400000
2023-12-27 | 13110 | 13.11 | 7.27 | 7.64 | 135 | 15 | 308 | 40 | 243 | 26 | NA | 400 | 0.3 | 24.07 | 1200000
2023-12-28 | 12690 | 12.69 | 7.24 | 7.65 | 140 | 16 | 312 | 32 | 239 | 23 | NA | 500 | 0.2 | 23.46 | 1700000
2023-12-29 | 11580 | 11.58 | 7.32 | 7.63 | 135 | 15 | 304 | 36 | 244 | 24 | NA | 600 | 0.3 | 23.89 | 1300000
2023-12-30 | 12420 | 12.42 | 7.25 | 7.58 | 130 | 16 | 308 | 32 | 236 | 26 | NA | 400 | 0.2 | 23.82 | 1400000
2023-12-31 | 13290 | 13.29 | 6.94 | 7.6 | 140 | 15 | 312 | 36 | 245 | 25 | NA | 700 | 0.3 | 24.15 | 1200000
Average | 12663.871 | 12.6639 | 7.1748 | 7.6448 | 134.3548 | 15.5484 | 299.871 | 35.3548 | 229.9355 | 25 |  | 551.6129 | 0.24839 | 23.9219 | 1358064.5161
392.58
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11560 | 11.56 | 6.72 | 7.51 | 125 | 14 | 284 | 32 | 205 | 22 |  | 400 | 0.2 | 23.16 | 1100000
Max | 14030 | 14.03 | 7.32 | 7.78 | 140 | 17 | 312 | 40 | 245 | 29 |  | 700 | 0.3 | 24.56 | 1700000