## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-12-01 | 54050 | 54.05 | 7.19 | 7.72 | 135 | 16 | 312 | 36 | 256 | 26 | NA | 800 | 0.3 | 23.96 | 1400000 | Retaining wall of Nalla at Sasur Kadheri SPS is broken hence raw sewage is going directly into the river.
2021-12-02 | 51200 | 51.2 | 7.27 | 7.64 | 150 | 13 | 304 | 32 | 236 | 26 | NA | 400 | 0.2 | 23.91 | 1300000 | Construction of retaining wall of Nalla at Sasur Kadheri SPS is in progress.
2021-12-03 | 49800 | 49.8 | 7.22 | 7.84 | 145 | 13 | 324 | 40 | 264 | 24 | NA | 700 | 0.2 | 23.53 | 1400000
2021-12-04 | 55840 | 55.84 | 7.14 | 7.71 | 135 | 17 | 300 | 36 | 264 | 28 | NA | 400 | 0.3 | 25 | 1300000
2021-12-05 | 56350 | 56.35 | 7.14 | 7.79 | 140 | 14 | 316 | 40 | 236 | 26 | NA | 500 | 0.3 | 23.53 | 1700000
2021-12-06 | 52100 | 52.1 | 7.22 | 7.84 | 130 | 12 | 304 | 36 | 244 | 28 | NA | 700 | 0.2 | 22.15 | 1400000
2021-12-07 | 51800 | 51.8 | 7.26 | 7.84 | 145 | 13 | 320 | 32 | 256 | 24 | NA | 400 | 0.2 | 22.22 | 1400000
2021-12-08 | 52900 | 52.9 | 7.17 | 7.9 | 150 | 16 | 324 | 40 | 238 | 26 | NA | 800 | 0.3 | 22.61 | 1400000
2021-12-09 | 53980 | 53.98 | 7.28 | 7.64 | 140 | 16 | 328 | 32 | 238 | 28 | NA | 500 | 0.3 | 23.13 | 1700000
2021-12-10 | 52920 | 52.92 | 7.32 | 7.74 | 130 | 13 | 296 | 40 | 256 | 24 | NA | 400 | 0.2 | 24.04 | 1400000
2021-12-11 | 50680 | 50.68 | 7.15 | 7.84 | 145 | 15 | 328 | 40 | 252 | 24 | NA | 500 | 0.3 | 24.33 | 1300000
2021-12-12 | 50910 | 50.91 | 7.24 | 7.9 | 150 | 16 | 304 | 36 | 250 | 26 | NA | 800 | 0.2 | 22.41 | 1400000
2021-12-13 | 50940 | 50.94 | 7.17 | 7.84 | 140 | 14 | 320 | 32 | 284 | 24 | NA | 400 | 0.2 | 23.92 | 1300000
2021-12-14 | 50880 | 50.88 | 7.18 | 7.64 | 135 | 13 | 304 | 36 | 248 | 26 | NA | 600 | 0.3 | 22.17 | 1700000
2021-12-15 | 50110 | 50.11 | 7.26 | 7.84 | 140 | 12 | 324 | 40 | 222 | 26 | NA | 400 | 0.3 | 23.9 | 1400000
2021-12-16 | 51300 | 51.3 | 7.21 | 7.94 | 145 | 11 | 312 | 36 | 250 | 24 | NA | 700 | 0.2 | 22.93 | 1300000
2021-12-17 | 52160 | 52.16 | 7.14 | 7.8 | 140 | 15 | 312 | 40 | 272 | 24 | NA | 400 | 0.2 | 24.12 | 1400000
2021-12-18 | 53840 | 53.84 | 7.3 | 7.84 | 150 | 12 | 300 | 36 | 248 | 26 | NA | 600 | 0.3 | 24.96 | 1300000
2021-12-19 | 52050 | 52.05 | 7.21 | 7.8 | 140 | 12 | 328 | 40 | 240 | 28 | NA | 400 | 0.3 | 23.43 | 1400000
2021-12-20 | 50030 | 50.03 | 7.71 | 7.72 | 135 | 14 | 312 | 36 | 234 | 26 | NA | 800 | 0.2 | 22.41 | 1400000
2021-12-21 | 51520 | 51.52 | 7.14 | 7.8 | 145 | 15 | 340 | 40 | 296 | 26 | NA | 500 | 0.4 | 24.29 | 1300000
2021-12-22 | 54050 | 54.05 | 7.24 | 7.78 | 140 | 14 | 324 | 36 | 264 | 24 | NA | 400 | 0.2 | 23.96 | 1400000 | Construction of retaining wall of Nalla at Sasur Kadheri SPS is completed.
2021-12-23 | 54900 | 54.9 | 7.16 | 7.88 | 145 | 15 | 336 | 44 | 296 | 28 | NA | 600 | 0.3 | 23.92 | 1700000
2021-12-24 | 59020 | 59.02 | 7.26 | 7.78 | 150 | 12 | 332 | 40 | 256 | 26 | NA | 400 | 0.3 | 23.37 | 1300000
2021-12-25 | 60020 | 60.02 | 7.18 | 7.8 | 135 | 13 | 324 | 40 | 240 | 28 | NA | 500 | 0.2 | 21.67 | 1700000
2021-12-26 | 57650 | 57.65 | 7.21 | 7.64 | 145 | 13 | 328 | 36 | 272 | 24 | NA | 600 | 0.3 | 23.42 | 1400000
2021-12-27 | 56900 | 56.9 | 7.24 | 7.74 | 140 | 14 | 320 | 36 | 240 | 24 | NA | 400 | 0.3 | 24.34 | 1300000
2021-12-28 | 55420 | 55.42 | 7.26 | 7.8 | 135 | 15 | 324 | 40 | 246 | 26 | NA | 800 | 0.3 | 23.39 | 1400000
2021-12-29 | 50740 | 50.74 | 7.22 | 7.88 | 135 | 17 | 316 | 36 | 246 | 28 | NA | 500 | 0.2 | 23.27 | 1700000
2021-12-30 | 63100 | 63.1 | 7.28 | 7.68 | 150 | 18 | 304 | 32 | 266 | 24 | NA | 600 | 0.3 | 24.06 | 1300000
2021-12-31 | 60650 | 60.65 | 7.21 | 7.77 | 145 | 16 | 320 | 40 | 272 | 28 | NA | 500 | 0.3 | 24.5 | 1300000
Average | 53800.3226 | 53.8003 | 7.2316 | 7.7861 | 141.4516 | 14.1613 | 317.4194 | 37.2903 | 254.2581 | 25.8065 | NA | 548.3871 | 0.26129 | 23.5113 | 1422580.6452
1667.81
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 49800 | 49.8 | 7.14 | 7.64 | 130 | 11 | 296 | 32 | 222 | 24 |  | 400 | 0.2 | 21.67 | 1300000
Max | 63100 | 63.1 | 7.71 | 7.94 | 150 | 18 | 340 | 44 | 296 | 28 |  | 800 | 0.4 | 25 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-12-01 | 30630 | 30.63 | 7.43 | 7.6 | 153 | 21 | 344 | 32 | 305 | 42 | NA | 600 | 0.3 | 25.1 | 1100000
2021-12-02 | 31290 | 31.29 | 7.31 | 7.48 | 160 | 24 | 352 | 36 | 300 | 39 | NA | 700 | 0.2 | 24.7 | 1200000
2021-12-03 | 32600 | 32.6 | 7.36 | 7.54 | 163 | 26 | 356 | 44 | 323 | 41 | NA | 600 | 0.2 | 24.2 | 1300000
2021-12-04 | 31890 | 31.89 | 7.33 | 7.5 | 157 | 25 | 348 | 40 | 317 | 34 | NA | 800 | 0.3 | 24.5 | 1700000
2021-12-05 | 32460 | 32.46 | 7.28 | 7.55 | 160 | 24 | 352 | 32 | 310 | 38 | NA | 500 | 0.2 | 23.8 | 1400000
2021-12-06 | 31000 | 31 | 7.35 | 7.49 | 153 | 22 | 356 | 40 | 303 | 36 | NA | 700 | 0.2 | 25 | 1300000
2021-12-07 | 32570 | 32.57 | 7.38 | 7.53 | 147 | 23 | 364 | 44 | 319 | 43 | NA | 600 | 0.3 | 24.6 | 1100000
2021-12-08 | 36880 | 36.88 | 7.4 | 7.56 | 163 | 28 | 260 | 36 | 325 | 37 | NA | 500 | 0.2 | 24.1 | 1700000
2021-12-09 | 32420 | 32.42 | 7.33 | 7.61 | 157 | 26 | 352 | 48 | 316 | 44 | NA | 400 | 0.3 | 22.9 | 1400000
2021-12-10 | 32870 | 32.87 | 7.27 | 7.46 | 160 | 20 | 356 | 40 | 309 | 41 | NA | 800 | 0.2 | 23.2 | 1100000
2021-12-11 | 33830 | 33.83 | 7.36 | 7.52 | 153 | 23 | 364 | 44 | 322 | 45 | NA | 700 | 0.2 | 24.4 | 1200000
2021-12-12 | 38250 | 38.25 | 7.34 | 7.49 | 160 | 27 | 368 | 48 | 312 | 40 | NA | 600 | 0.3 | 23.7 | 1300000
2021-12-13 | 35420 | 35.42 | 7.39 | 7.51 | 157 | 25 | 360 | 36 | 328 | 38 | NA | 500 | 0.2 | 23 | 1100000
2021-12-14 | 35210 | 35.21 | 7.29 | 7.55 | 150 | 24 | 352 | 40 | 296 | 33 | NA | 600 | 0.2 | 24.8 | 1300000
2021-12-15 | 38110 | 38.11 | 7.4 | 7.58 | 163 | 26 | 364 | 48 | 315 | 39 | NA | 800 | 0.2 | 22.7 | 1400000
2021-12-16 | 35350 | 35.35 | 7.34 | 7.64 | 160 | 22 | 356 | 44 | 304 | 42 | NA | 700 | 0.2 | 25.1 | 1300000
2021-12-17 | 37150 | 37.15 | 7.3 | 7.56 | 153 | 27 | 364 | 40 | 320 | 35 | NA | 400 | 0.3 | 24.7 | 1100000
2021-12-18 | 38740 | 38.74 | 7.37 | 7.6 | 159 | 26 | 360 | 44 | 324 | 37 | NA | 600 | 0.2 | 23.6 | 1100000
2021-12-19 | 33260 | 33.26 | 7.38 | 7.59 | 156 | 23 | 368 | 48 | 302 | 41 | NA | 800 | 0.3 | 21.3 | 1300000
2021-12-20 | 34290 | 34.29 | 7.32 | 7.54 | 147 | 25 | 356 | 40 | 298 | 36 | NA | 500 | 0.2 | 23.8 | 1400000
2021-12-21 | 38640 | 38.64 | 7.35 | 7.5 | 160 | 26 | 352 | 44 | 318 | 38 | NA | 600 | 0.2 | 24.4 | 1600000
2021-12-22 | 38590 | 38.59 | 7.28 | 7.53 | 163 | 28 | 364 | 36 | 326 | 35 | NA | 700 | 0.2 | 25 | 1100000
2021-12-23 | 37290 | 37.29 | 7.36 | 7.57 | 157 | 25 | 360 | 40 | 311 | 42 | NA | 500 | 0.3 | 23.2 | 1300000
2021-12-24 | 36930 | 36.93 | 7.31 | 7.48 | 159 | 27 | 352 | 36 | 301 | 40 | NA | 600 | 0.2 | 22.9 | 1100000
2021-12-25 | 35600 | 35.6 | 7.33 | 7.52 | 146 | 22 | 360 | 44 | 316 | 43 | NA | 700 | 0.2 | 24.3 | 1200000
2021-12-26 | 35440 | 35.44 | 7.39 | 7.54 | 153 | 25 | 356 | 48 | 295 | 39 | NA | 500 | 0.3 | 23.4 | 1400000
2021-12-27 | 42200 | 42.2 | 7.42 | 7.57 | 159 | 27 | 364 | 44 | 322 | 40 | NA | 800 | 0.2 | 24 | 1300000
2021-12-28 | 38860 | 38.86 | 7.34 | 7.47 | 156 | 26 | 352 | 48 | 318 | 44 | NA | 600 | 0.2 | 23.7 | 1400000
2021-12-29 | 36220 | 36.22 | 7.37 | 7.59 | 163 | 28 | 348 | 40 | 308 | 39 | NA | 500 | 0.3 | 22.6 | 1600000
2021-12-30 | 34170 | 34.17 | 7.3 | 7.55 | 166 | 27 | 344 | 32 | 315 | 34 | NA | 700 | 0.2 | 23.4 | 1700000
2021-12-31 | 36300 | 36.3 | 7.34 | 7.53 | 160 | 25 | 356 | 36 | 312 | 38 | NA | 400 | 0.3 | 24.6 | 1400000
Average | 35305.1613 | 35.3052 | 7.3458 | 7.5403 | 157.1935 | 24.9355 | 353.5484 | 41.0323 | 312.5806 | 39.129 | NA | 612.9032 | 0.23548 | 23.8935 | 1319354.8387
1094.46
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 30630 | 30.63 | 7.27 | 7.46 | 146 | 20 | 260 | 32 | 295 | 33 |  | 400 | 0.2 | 21.3 | 1100000
Max | 42200 | 42.2 | 7.43 | 7.64 | 166 | 28 | 368 | 48 | 328 | 45 |  | 800 | 0.3 | 25.1 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-12-01 | 31910 | 31.91 | 7.34 | 7.68 | 135 | 13 | 316 | 36 | 267 | 18 | NA | 500 | 0.2 | 24 | 1200000 | 1. There is small leakage in retaining wall due to which raw sewage is bypassing to river. This leakage must be rectified. 2. Strengthening of retaining wall is required so that it does not break down during rains & flood.
2021-12-02 | 31580 | 31.58 | 7.42 | 7.59 | 141 | 15 | 328 | 32 | 272 | 17 | NA | 600 | 0.3 | 24.1 | 1300000
2021-12-03 | 30430 | 30.43 | 7.31 | 7.54 | 147 | 14 | 320 | 36 | 262 | 19 | NA | 400 | 0.2 | 23.9 | 1400000
2021-12-04 | 32370 | 32.37 | 7.38 | 7.63 | 156 | 16 | 332 | 40 | 267 | 21 | NA | 700 | 0.3 | 23.7 | 1300000
2021-12-05 | 30600 | 30.6 | 7.25 | 7.72 | 144 | 15 | 324 | 44 | 279 | 20 | NA | 500 | 0.2 | 24.2 | 1200000
2021-12-06 | 31430 | 31.43 | 7.36 | 7.61 | 150 | 14 | 336 | 40 | 288 | 18 | NA | 400 | 0.2 | 23.8 | 1300000
2021-12-07 | 31590 | 31.59 | 7.43 | 7.58 | 141 | 16 | 328 | 44 | 264 | 19 | NA | 700 | 0.3 | 24.3 | 1400000
2021-12-08 | 30970 | 30.97 | 7.37 | 7.64 | 147 | 15 | 316 | 36 | 273 | 17 | NA | 600 | 0.2 | 23.9 | 1200000
2021-12-09 | 31440 | 31.44 | 7.3 | 7.68 | 138 | 13 | 324 | 40 | 259 | 19 | NA | 500 | 0.3 | 24.1 | 1300000
2021-12-10 | 31890 | 31.89 | 7.42 | 7.76 | 145 | 14 | 332 | 36 | 268 | 18 | NA | 400 | 0.2 | 23.8 | 1200000
2021-12-11 | 31730 | 31.73 | 7.35 | 7.64 | 150 | 13 | 320 | 32 | 278 | 16 | NA | 600 | 0.2 | 24.3 | 1400000
2021-12-12 | 31870 | 31.87 | 7.41 | 7.59 | 155 | 15 | 328 | 40 | 265 | 17 | NA | 700 | 0.3 | 23.7 | 1300000
2021-12-13 | 31560 | 31.56 | 7.32 | 7.66 | 144 | 13 | 316 | 36 | 259 | 19 | NA | 500 | 0.2 | 24.2 | 1400000
2021-12-14 | 32110 | 32.11 | 7.39 | 7.54 | 148 | 14 | 324 | 40 | 268 | 18 | NA | 400 | 0.3 | 24 | 1600000
2021-12-15 | 32150 | 32.15 | 7.24 | 7.74 | 142 | 14 | 312 | 34 | 276 | 20 | NA | 600 | 0.2 | 23.6 | 1300000
2021-12-16 | 31450 | 31.45 | 7.31 | 7.61 | 147 | 12 | 308 | 38 | 265 | 17 | NA | 700 | 0.3 | 24.1 | 1400000
2021-12-17 | 32650 | 32.65 | 7.15 | 7.52 | 141 | 13 | 304 | 36 | 248 | 19 | NA | 500 | 0.2 | 22.8 | 1200000
2021-12-18 | 31230 | 31.23 | 7.42 | 7.59 | 153 | 14 | 316 | 40 | 262 | 17 | NA | 600 | 0.2 | 23.7 | 1300000
2021-12-19 | 31960 | 31.96 | 7.37 | 7.64 | 144 | 12 | 324 | 34 | 256 | 16 | NA | 400 | 0.2 | 24.3 | 1600000
2021-12-20 | 31780 | 31.78 | 7.45 | 7.59 | 147 | 14 | 312 | 40 | 268 | 18 | NA | 700 | 0.3 | 24.1 | 1400000
2021-12-21 | 33750 | 33.75 | 7.34 | 7.67 | 141 | 13 | 328 | 36 | 259 | 17 | NA | 500 | 0.2 | 23.8 | 1200000
2021-12-22 | 32860 | 32.86 | 7.42 | 7.61 | 147 | 14 | 320 | 32 | 273 | 20 | NA | 600 | 0.3 | 23.6 | 1300000
2021-12-23 | 32680 | 32.68 | 7.31 | 7.71 | 144 | 12 | 332 | 36 | 261 | 19 | NA | 500 | 0.2 | 23.5 | 1200000
2021-12-24 | 33890 | 33.89 | 7.39 | 7.67 | 153 | 13 | 324 | 40 | 269 | 18 | NA | 700 | 0.3 | 24 | 1400000
2021-12-25 | 31660 | 31.66 | 7.27 | 7.54 | 147 | 14 | 316 | 32 | 276 | 17 | NA | 500 | 0.2 | 23.8 | 1200000
2021-12-26 | 32790 | 32.79 | 7.34 | 7.59 | 141 | 12 | 328 | 36 | 262 | 16 | NA | 600 | 0.3 | 23.4 | 1300000
2021-12-27 | 31010 | 31.01 | 7.43 | 7.64 | 144 | 14 | 320 | 40 | 271 | 17 | NA | 400 | 0.3 | 23.7 | 1400000
2021-12-28 | 33220 | 33.22 | 7.38 | 7.73 | 153 | 13 | 324 | 32 | 259 | 15 | NA | 500 | 0.2 | 23.3 | 1200000
2021-12-29 | 31500 | 31.5 | 7.31 | 7.57 | 147 | 12 | 332 | 40 | 268 | 16 | NA | 700 | 0.3 | 23.9 | 1400000
2021-12-30 | 32770 | 32.77 | 7.42 | 7.64 | 141 | 13 | 320 | 36 | 261 | 15 | NA | 600 | 0.2 | 23.5 | 1300000
2021-12-31 | 33320 | 33.32 | 7.35 | 7.59 | 153 | 14 | 328 | 32 | 274 | 16 | NA | 500 | 0.3 | 23.8 | 1200000
Average | 32004.8387 | 32.0048 | 7.3532 | 7.6294 | 146 | 13.6452 | 322.3226 | 36.9677 | 267 | 17.7097 | NA | 551.6129 | 0.24516 | 23.8355 | 1316129.0323
992.15
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 30430 | 30.43 | 7.15 | 7.52 | 135 | 12 | 304 | 32 | 248 | 15 |  | 400 | 0.2 | 22.8 | 1200000
Max | 33890 | 33.89 | 7.45 | 7.76 | 156 | 16 | 336 | 44 | 288 | 21 |  | 700 | 0.3 | 24.3 | 1600000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2021-12-01 | 11220 | 11.22 | 7.45 | 7.73 | 145 | 19 | 328 | 40 | 263 | 20 | NA | 500 | 0.2 | 23.4 | 1600000
2021-12-02 | 10920 | 10.92 | 7.37 | 7.64 | 140 | 18 | 320 | 38 | 255 | 22 | NA | 700 | 0.3 | 23.1 | 1700000
2021-12-03 | 10000 | 10 | 7.28 | 7.54 | 135 | 17 | 312 | 42 | 248 | 24 | NA | 600 | 0.2 | 22.29 | 1400000
2021-12-04 | 9770 | 9.77 | 7.15 | 7.61 | 130 | 19 | 304 | 48 | 260 | 27 | NA | 500 | 0.2 | 21.46 | 1600000
2021-12-05 | 10630 | 10.63 | 7.24 | 7.48 | 138 | 18 | 316 | 46 | 268 | 25 | NA | 700 | 0.2 | 23.12 | 1300000
2021-12-06 | 11550 | 11.55 | 7.18 | 7.36 | 145 | 17 | 324 | 44 | 276 | 28 | NA | 600 | 0.2 | 22.54 | 1700000
2021-12-07 | 11270 | 11.27 | 7.23 | 7.33 | 140 | 18 | 310 | 48 | 265 | 26 | NA | 500 | 0.3 | 21.36 | 1400000
2021-12-08 | 10210 | 10.21 | 7.16 | 7.41 | 150 | 17 | 320 | 46 | 270 | 29 | NA | 700 | 0.2 | 20.73 | 1600000 | Aeration tank no. 1 is taken in shutdown on 08/12/2021 for maintenance purpose.
2021-12-09 | 9640 | 9.64 | 7.21 | 7.38 | 142 | 18 | 312 | 44 | 250 | 27 | NA | 600 | 0.2 | 21.67 | 1300000 | Aeration tank no. 1 is in maintenance.
2021-12-10 | 10390 | 10.39 | 7.29 | 7.56 | 138 | 19 | 304 | 48 | 267 | 26 | NA | 500 | 0.2 | 22.33 | 1400000
2021-12-11 | 9870 | 9.87 | 7.14 | 7.43 | 140 | 18 | 308 | 46 | 256 | 28 | NA | 600 | 0.3 | 23.16 | 1600000 | 1. Maintenance of Aerartion tank no. 1 is completed on 11/12/2021 and hence taken into operation. 2. Aeration tank no. 2 is taken in shutdown on 12/12/2021 for maintenance purpose.
2021-12-12 | 9770 | 9.77 | 7.22 | 7.51 | 145 | 17 | 320 | 44 | 266 | 25 | NA | 500 | 0.2 | 22.26 | 1300000 | Aeration tank no. 2 is in maintenance.
2021-12-13 | 9590 | 9.59 | 7.19 | 7.47 | 135 | 18 | 310 | 48 | 259 | 27 | NA | 700 | 0.2 | 20.64 | 1200000
2021-12-14 | 10860 | 10.86 | 7.15 | 7.34 | 138 | 16 | 316 | 42 | 247 | 24 | NA | 500 | 0.3 | 21.72 | 1400000 | Maintenance of Aerartion tank no. 2 is completed on 14/12/2021 and hence taken into operation.
2021-12-15 | 11890 | 11.89 | 7.25 | 7.66 | 144 | 17 | 324 | 44 | 269 | 23 | NA | 600 | 0.2 | 22.52 | 1600000
2021-12-16 | 11340 | 11.34 | 7.17 | 7.59 | 141 | 16 | 300 | 40 | 258 | 21 | NA | 400 | 0.3 | 21.44 | 1300000
2021-12-17 | 11130 | 11.13 | 7.13 | 7.71 | 145 | 14 | 312 | 36 | 265 | 20 | NA | 600 | 0.2 | 22.76 | 1200000
2021-12-18 | 11320 | 11.32 | 7.22 | 7.68 | 141 | 15 | 328 | 32 | 253 | 18 | NA | 700 | 0.2 | 20.55 | 1400000
2021-12-19 | 11910 | 11.91 | 7.15 | 7.76 | 147 | 14 | 316 | 34 | 260 | 22 | NA | 600 | 0.2 | 23.17 | 1200000
2021-12-20 | 11840 | 11.84 | 7.31 | 7.59 | 138 | 16 | 324 | 40 | 272 | 20 | NA | 500 | 0.3 | 23.49 | 1600000
2021-12-21 | 12200 | 12.2 | 7.37 | 7.64 | 144 | 15 | 310 | 36 | 258 | 21 | NA | 600 | 0.2 | 22.93 | 1400000
2021-12-22 | 12110 | 12.11 | 7.18 | 7.73 | 153 | 16 | 328 | 34 | 276 | 19 | NA | 700 | 0.3 | 22.16 | 1300000
2021-12-23 | 12270 | 12.27 | 7.29 | 7.69 | 145 | 15 | 320 | 40 | 263 | 21 | NA | 500 | 0.2 | 23.63 | 1200000
2021-12-24 | 12050 | 12.05 | 7.34 | 7.61 | 140 | 14 | 312 | 32 | 255 | 23 | NA | 600 | 0.3 | 23.3 | 1300000
2021-12-25 | 12980 | 12.98 | 7.41 | 7.58 | 146 | 15 | 324 | 36 | 274 | 22 | NA | 700 | 0.2 | 22.84 | 1400000
2021-12-26 | 12580 | 12.58 | 7.32 | 7.67 | 138 | 13 | 316 | 32 | 266 | 23 | NA | 600 | 0.3 | 23.92 | 1600000
2021-12-27 | 12430 | 12.43 | 7.26 | 7.53 | 150 | 16 | 324 | 40 | 253 | 21 | NA | 500 | 0.2 | 23.65 | 1400000
2021-12-28 | 12280 | 12.28 | 7.17 | 7.62 | 145 | 15 | 320 | 36 | 265 | 20 | NA | 400 | 0.2 | 22.31 | 1300000
2021-12-29 | 12020 | 12.02 | 7.22 | 7.56 | 140 | 13 | 312 | 32 | 256 | 18 | NA | 600 | 0.3 | 21.46 | 1400000
2021-12-30 | 11930 | 11.93 | 7.27 | 7.69 | 136 | 15 | 308 | 38 | 270 | 22 | NA | 500 | 0.2 | 21.96 | 1200000
2021-12-31 | 12260 | 12.26 | 7.36 | 7.51 | 142 | 14 | 322 | 36 | 278 | 19 | NA | 600 | 0.2 | 22.14 | 1400000
Average | 11297.7419 | 11.2977 | 7.2477 | 7.5681 | 141.8065 | 16.1935 | 316.2581 | 40.0645 | 262.6129 | 22.9355 | NA | 577.4194 | 0.23226 | 22.3874 | 1409677.4194
350.23
Source: | Logbook of Labarotory at Sewage Treament Plant
Min. | 9590 | 9.59 | 7.13 | 7.33 | 130 | 13 | 300 | 32 | 247 | 18 |  | 400 | 0.2 | 20.55 | 1200000
Max | 12980 | 12.98 | 7.45 | 7.76 | 153 | 19 | 328 | 48 | 278 | 29 |  | 700 | 0.3 | 23.92 | 1700000