## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-02-01 | 61250 | 61.25 | 7.24 | 7.73 | 140 | 17 | 312 | 44 | 286 | 24 | NA | 700 | 0.3 | 24.47 | 1300000
2023-02-02 | 61330 | 61.33 | 7.26 | 7.69 | 135 | 15 | 328 | 40 | 291 | 22 | NA | 500 | 0.4 | 23.89 | 1700000
2023-02-03 | 58310 | 58.31 | 7.27 | 7.62 | 145 | 17 | 300 | 36 | 278 | 24 | NA | 700 | 0.4 | 23.5 | 1400000
2023-02-04 | 61190 | 61.19 | 7.22 | 7.73 | 150 | 18 | 304 | 44 | 284 | 22 | NA | 600 | 0.3 | 24.26 | 1300000
2023-02-05 | 61870 | 61.87 | 7.26 | 7.66 | 135 | 16 | 320 | 40 | 297 | 25 | NA | 400 | 0.3 | 23.69 | 1700000
2023-02-06 | 61730 | 61.73 | 7.22 | 7.74 | 145 | 17 | 308 | 36 | 279 | 23 | NA | 500 | 0.2 | 24.37 | 1400000
2023-02-07 | 59050 | 59.05 | 7.28 | 7.76 | 130 | 15 | 312 | 44 | 288 | 22 | NA | 700 | 0.2 | 23.56 | 1300000
2023-02-08 | 61820 | 61.82 | 7.19 | 7.69 | 145 | 18 | 304 | 40 | 293 | 24 | NA | 600 | 0.3 | 23.64 | 1700000
2023-02-09 | 61750 | 61.75 | 7.24 | 7.73 | 135 | 17 | 300 | 36 | 296 | 22 | NA | 400 | 0.2 | 23.22 | 1400000
2023-02-10 | 59440 | 59.44 | 7.28 | 7.71 | 130 | 16 | 328 | 40 | 289 | 21 | NA | 500 | 0.3 | 24.98 | 1700000
2023-02-11 | 59380 | 59.38 | 7.22 | 7.67 | 140 | 15 | 316 | 44 | 291 | 23 | NA | 700 | 0.3 | 23.69 | 1400000
2023-02-12 | 54650 | 54.65 | 7.24 | 7.74 | 145 | 17 | 324 | 44 | 295 | 22 | NA | 600 | 0.2 | 23.66 | 1300000
2023-02-13 | 57820 | 57.82 | 7.26 | 7.68 | 135 | 18 | 328 | 40 | 298 | 24 | NA | 400 | 0.3 | 23.78 | 1700000
2023-02-14 | 59760 | 59.76 | 7.28 | 7.74 | 150 | 15 | 308 | 36 | 286 | 23 | NA | 600 | 0.2 | 23.57 | 1400000
2023-02-15 | 58320 | 58.32 | 7.21 | 7.72 | 145 | 14 | 300 | 40 | 278 | 21 | NA | 700 | 0.2 | 24.25 | 1300000
2023-02-16 | 56260 | 56.26 | 7.28 | 7.73 | 150 | 18 | 308 | 44 | 294 | 24 | NA | 400 | 0.3 | 23.45 | 1400000
2023-02-17 | 58780 | 58.78 | 7.26 | 7.68 | 140 | 18 | 324 | 40 | 298 | 26 | NA | 500 | 0.2 | 23.5 | 1700000
2023-02-18 | 61350 | 61.35 | 7.18 | 7.72 | 145 | 16 | 360 | 44 | 258 | 25 | NA | 700 | 0.3 | 25.05 | 1300000
2023-02-19 | 60040 | 60.04 | 7.12 | 7.68 | 135 | 18 | 356 | 44 | 262 | 24 | NA | 700 | 0.2 | 23.58 | 1300000
1900-02-19 | 59080 | 59.08 | 7.18 | 7.6 | 140 | 17 | 336 | 40 | 248 | 26 | NA | 400 | 0.3 | 24.04 | 1400000
2023-02-21 | 60130 | 60.13 | 7.1 | 7.64 | 130 | 18 | 320 | 40 | 284 | 26 | NA | 600 | 0.3 | 23.14 | 1700000
2023-02-22 | 59290 | 59.29 | 7.18 | 7.62 | 140 | 19 | 312 | 44 | 292 | 27 | NA | 700 | 0.2 | 23.21 | 1300000
2023-02-23 | 62470 | 62.47 | 7.18 | 7.72 | 130 | 16 | 328 | 40 | 280 | 22 | NA | 400 | 0.2 | 22.17 | 1700000
2023-02-24 | 61300 | 61.3 | 7.19 | 7.84 | 145 | 17 | 316 | 44 | 286 | 25 | NA | 600 | 0.3 | 23.55 | 1400000
2023-02-25 | 57880 | 57.88 | 7.21 | 7.74 | 140 | 18 | 328 | 44 | 291 | 23 | NA | 500 | 0.3 | 24.23 | 1300000
2023-02-26 | 59480 | 59.48 | 7.26 | 7.68 | 135 | 17 | 304 | 40 | 296 | 22 | NA | 700 | 0.2 | 23.64 | 1400000
2023-02-27 | 58920 | 58.92 | 7.22 | 7.73 | 140 | 16 | 320 | 44 | 293 | 25 | NA | 600 | 0.3 | 24.82 | 1700000
2023-02-28 | 53520 | 53.52 | 7.24 | 7.7 | 145 | 17 | 312 | 40 | 297 | 26 | NA | 700 | 0.2 | 23.22 | 1700000
Average | 59506.0714 | 59.5061 | 7.2239 | 7.7032 | 140 | 16.7857 | 318.4286 | 41.1429 | 286 | 23.6786 | NA | 575 | 0.26429 | 23.7904 | 1475000
1666.17
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 53520 | 53.52 | 7.1 | 7.6 | 130 | 14 | 300 | 36 | 248 | 21 |  | 400 | 0.2 | 22.17 | 1300000
Max | 62470 | 62.47 | 7.28 | 7.84 | 150 | 19 | 360 | 44 | 298 | 27 |  | 700 | 0.4 | 25.05 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-02-01 | 41070 | 41.07 | 7.39 | 7.52 | 165 | 28 | 360 | 44 | 297 | 39 | NA | 600 | 0.3 | 24.7 | 1400000
2023-02-02 | 46460 | 46.46 | 7.37 | 7.61 | 170 | 31 | 364 | 48 | 315 | 41 | NA | 700 | 0.2 | 24.6 | 1700000
2023-02-03 | 45430 | 45.43 | 7.42 | 7.59 | 155 | 30 | 372 | 44 | 322 | 38 | NA | 500 | 0.3 | 24.9 | 1300000
2023-02-04 | 43520 | 43.52 | 7.4 | 7.55 | 160 | 31 | 368 | 48 | 320 | 37 | NA | 600 | 0.3 | 25.3 | 1400000
2023-02-05 | 41850 | 41.85 | 7.38 | 7.5 | 155 | 32 | 372 | 48 | 328 | 38 | NA | 800 | 0.2 | 25.1 | 1700000
2023-02-06 | 39880 | 39.88 | 7.35 | 7.4 | 160 | 23 | 360 | 40 | 345 | 37 | NA | 900 | 0.3 | 24.8 | 1700000
2023-02-07 | 38680 | 38.68 | 7.31 | 7.36 | 165 | 24 | 340 | 40 | 307 | 34 | NA | 700 | 0.2 | 24.7 | 1300000
2023-02-08 | 39390 | 39.39 | 7.3 | 7.35 | 160 | 24 | 364 | 36 | 319 | 36 | NA | 800 | 0.2 | 25 | 1400000
2023-02-09 | 38160 | 38.16 | 7.34 | 7.4 | 155 | 23 | 356 | 44 | 330 | 39 | NA | 600 | 0.3 | 25.4 | 1100000
2023-02-10 | 35610 | 35.61 | 7.36 | 7.38 | 150 | 25 | 364 | 44 | 340 | 40 | NA | 700 | 0.3 | 25.5 | 1200000
2023-02-11 | 36520 | 36.52 | 7.33 | 7.39 | 160 | 27 | 368 | 40 | 322 | 37 | NA | 800 | 0.2 | 24.1 | 1400000
2023-02-12 | 35770 | 35.77 | 7.28 | 7.35 | 165 | 26 | 364 | 40 | 309 | 35 | NA | 800 | 0.2 | 24.6 | 1700000
2023-02-13 | 37200 | 37.2 | 7.29 | 7.34 | 170 | 28 | 360 | 44 | 290 | 36 | NA | 600 | 0.3 | 24.9 | 1300000
2023-02-14 | 39330 | 39.33 | 7.12 | 7.28 | 160 | 27 | 364 | 44 | 298 | 35 | NA | 700 | 0.2 | 25.1 | 1400000
2023-02-15 | 41900 | 41.9 | 7.15 | 7.26 | 165 | 29 | 356 | 40 | 308 | 37 | NA | 800 | 0.3 | 25.3 | 1700000
2023-02-16 | 39500 | 39.5 | 7.25 | 7.33 | 160 | 28 | 360 | 44 | 317 | 36 | NA | 500 | 0.3 | 24.2 | 1300000
2023-02-17 | 39950 | 39.95 | 7.31 | 7.37 | 155 | 29 | 352 | 44 | 312 | 35 | NA | 700 | 0.2 | 24.7 | 1700000
2023-02-18 | 38690 | 38.69 | 7.29 | 7.3 | 160 | 27 | 364 | 40 | 316 | 36 | NA | 700 | 0.3 | 25.3 | 1400000
2023-02-19 | 37920 | 37.92 | 7.45 | 7.28 | 165 | 28 | 368 | 44 | 320 | 36 | NA | 600 | 0.2 | 24.9 | 1100000
1900-02-19 | 34020 | 34.02 | 7.46 | 7.26 | 160 | 29 | 360 | 48 | 329 | 38 | NA | 800 | 0.3 | 25 | 1700000
2023-02-21 | 34480 | 34.48 | 7.57 | 7.4 | 155 | 27 | 356 | 44 | 318 | 36 | NA | 700 | 0.2 | 24.5 | 1400000
2023-02-22 | 35750 | 35.75 | 7.63 | 7.38 | 165 | 25 | 364 | 40 | 321 | 35 | NA | 500 | 0.2 | 24.7 | 1300000
2023-02-23 | 36710 | 36.71 | 7.58 | 7.37 | 160 | 24 | 352 | 36 | 316 | 34 | NA | 800 | 0.3 | 24.8 | 1400000
2023-02-24 | 37940 | 37.94 | 7.56 | 7.39 | 170 | 24 | 356 | 40 | 319 | 35 | NA | 600 | 0.2 | 25.1 | 1200000
2023-02-25 | 39470 | 39.47 | 7.51 | 7.36 | 165 | 25 | 364 | 40 | 320 | 34 | NA | 700 | 0.3 | 25.3 | 1400000
2023-02-26 | 39420 | 39.42 | 7.5 | 7.2 | 155 | 26 | 360 | 36 | 314 | 35 | NA | 900 | 0.3 | 24.7 | 1700000
2023-02-27 | 38550 | 38.55 | 7.48 | 7.15 | 170 | 27 | 368 | 44 | 318 | 33 | NA | 800 | 0.2 | 24.9 | 1300000
2023-02-28 | 35710 | 35.71 | 7.46 | 7.14 | 165 | 27 | 364 | 40 | 316 | 34 | NA | 700 | 0.3 | 24.6 | 1400000
Average | 38888.5714 | 38.8886 | 7.3871 | 7.3646 | 161.4286 | 26.9286 | 361.4286 | 42.2857 | 317.3571 | 36.2857 | NA | 700 | 0.25357 | 24.8821 | 1428571.4286
1088.88
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 34020 | 34.02 | 7.12 | 7.14 | 150 | 23 | 340 | 36 | 290 | 33 |  | 500 | 0.2 | 24.1 | 1100000
Max | 46460 | 46.46 | 7.63 | 7.61 | 170 | 32 | 372 | 48 | 345 | 41 |  | 900 | 0.3 | 25.5 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-02-01 | 28480 | 28.48 | 7.24 | 7.52 | 150 | 14 | 312 | 40 | 291 | 21 | NA | 600 | 0.5 | 24.27 | 1400000
2023-02-02 | 26960 | 26.96 | 7.21 | 7.44 | 140 | 15 | 320 | 44 | 280 | 20 | NA | 700 | 0.4 | 23.38 | 1700000
2023-02-03 | 30130 | 30.13 | 7.26 | 7.48 | 135 | 16 | 308 | 40 | 273 | 21 | NA | 500 | 0.5 | 23.46 | 1300000
2023-02-04 | 29990 | 29.99 | 7.23 | 7.53 | 145 | 13 | 316 | 36 | 268 | 22 | NA | 400 | 0.5 | 24.41 | 1200000
2023-02-05 | 31870 | 31.87 | 7.18 | 7.56 | 150 | 12 | 324 | 36 | 270 | 21 | NA | 600 | 0.3 | 24.07 | 1400000
2023-02-06 | 29490 | 29.49 | 7.22 | 7.49 | 145 | 14 | 312 | 40 | 263 | 19 | NA | 700 | 0.2 | 24.18 | 1300000
2023-02-07 | 31370 | 31.37 | 7.24 | 7.45 | 150 | 15 | 316 | 44 | 271 | 18 | NA | 500 | 0.3 | 24.02 | 1700000
2023-02-08 | 29990 | 29.99 | 7.18 | 7.47 | 140 | 14 | 308 | 40 | 267 | 21 | NA | 600 | 0.2 | 24.27 | 1400000
2023-02-09 | 29940 | 29.94 | 7.2 | 7.38 | 135 | 11 | 312 | 36 | 276 | 22 | NA | 500 | 0.3 | 23.81 | 1300000
2023-02-10 | 30380 | 30.38 | 7.25 | 7.5 | 145 | 13 | 320 | 40 | 281 | 19 | NA | 400 | 0.2 | 24.12 | 1700000
2023-02-11 | 29740 | 29.74 | 7.28 | 7.56 | 150 | 15 | 304 | 44 | 265 | 18 | NA | 600 | 0.3 | 24.35 | 1400000
2023-02-12 | 30530 | 30.53 | 7.24 | 7.51 | 155 | 13 | 316 | 40 | 273 | 20 | NA | 700 | 0.3 | 23.56 | 1300000
2023-02-13 | 29810 | 29.81 | 7.3 | 7.57 | 145 | 12 | 308 | 36 | 268 | 21 | NA | 500 | 0.2 | 24.17 | 1400000
2023-02-14 | 29750 | 29.75 | 7.18 | 7.48 | 140 | 14 | 312 | 40 | 280 | 20 | NA | 600 | 0.2 | 24.45 | 1700000
2023-02-15 | 29240 | 29.24 | 7.16 | 7.43 | 150 | 15 | 320 | 44 | 277 | 19 | NA | 400 | 0.3 | 23.91 | 1400000
2023-02-16 | 28500 | 28.5 | 7.22 | 7.55 | 155 | 13 | 328 | 40 | 266 | 21 | NA | 500 | 0.3 | 24.28 | 1300000
2023-02-17 | 31170 | 31.17 | 7.19 | 7.52 | 135 | 12 | 316 | 36 | 279 | 20 | NA | 700 | 0.2 | 23.61 | 1700000
2023-02-18 | 31860 | 31.86 | 7.24 | 7.49 | 140 | 11 | 304 | 36 | 270 | 19 | NA | 600 | 0.2 | 24.15 | 1400000
2023-02-19 | 32950 | 32.95 | 7.21 | 7.45 | 145 | 14 | 312 | 40 | 281 | 18 | NA | 500 | 0.3 | 23.59 | 1200000
1900-02-19 | 29300 | 29.3 | 7.26 | 7.51 | 155 | 16 | 324 | 44 | 269 | 17 | NA | 400 | 0.2 | 24.26 | 1300000
2023-02-21 | 29640 | 29.64 | 7.2 | 7.43 | 150 | 14 | 308 | 36 | 276 | 20 | NA | 600 | 0.2 | 24.11 | 1400000
2023-02-22 | 2918 | 29.18 | 7.23 | 7.44 | 140 | 13 | 316 | 40 | 265 | 20 | NA | 700 | 0.3 | 23.45 | 1200000
2023-02-23 | 29340 | 29.34 | 7.18 | 7.5 | 145 | 16 | 320 | 44 | 280 | 17 | NA | 500 | 0.2 | 23.51 | 1700000
2023-02-24 | 29760 | 29.76 | 7.22 | 7.47 | 155 | 14 | 328 | 40 | 277 | 20 | NA | 600 | 0.3 | 24.34 | 1400000
2023-02-25 | 28790 | 28.79 | 7.25 | 7.43 | 140 | 13 | 312 | 36 | 284 | 19 | NA | 500 | 0.2 | 24.19 | 1300000
2023-02-26 | 29710 | 29.71 | 7.28 | 7.52 | 135 | 15 | 308 | 40 | 269 | 20 | NA | 400 | 0.2 | 24.54 | 1200000
2023-02-27 | 29160 | 29.16 | 7.24 | 7.48 | 130 | 14 | 300 | 44 | 266 | 18 | NA | 600 | 0.3 | 23.39 | 1700000
2023-02-28 | 30520 | 30.52 | 7.2 | 7.51 | 140 | 12 | 316 | 36 | 271 | 19 | NA | 500 | 0.2 | 24.17 | 1400000
Average | 28974.5714 | 29.9125 | 7.2246 | 7.4882 | 144.2857 | 13.6786 | 314.2857 | 39.7143 | 273.4286 | 19.6429 | NA | 550 | 0.27857 | 24.0007 | 1421428.5714
837.55
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 2918 | 26.96 | 7.16 | 7.38 | 130 | 11 | 300 | 36 | 263 | 17 |  | 400 | 0.2 | 23.38 | 1200000
Max | 32950 | 32.95 | 7.3 | 7.57 | 155 | 16 | 328 | 44 | 291 | 22 |  | 700 | 0.5 | 24.54 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-02-01 | 12600 | 12.6 | 7.29 | 7.4 | 145 | 17 | 304 | 40 | 286 | 26 | NA | 500 | 0.3 | 23.31 | 1300000
2023-02-02 | 12020 | 12.02 | 7.3 | 7.42 | 140 | 16 | 312 | 44 | 294 | 27 | NA | 600 | 0.3 | 23.23 | 1700000
2023-02-03 | 11710 | 11.71 | 7.26 | 7.41 | 130 | 17 | 302 | 48 | 278 | 26 | NA | 500 | 0.4 | 22.9 | 1200000
2023-02-04 | 12640 | 12.64 | 7.3 | 7.44 | 150 | 15 | 304 | 40 | 296 | 24 | NA | 400 | 0.3 | 22.86 | 1300000
2023-02-05 | 13320 | 13.32 | 7.25 | 7.38 | 145 | 17 | 310 | 48 | 279 | 26 | NA | 600 | 0.3 | 23.61 | 1400000
2023-02-06 | 12450 | 12.45 | 7.29 | 7.4 | 140 | 15 | 298 | 44 | 284 | 27 | NA | 500 | 0.3 | 23.42 | 1700000
2023-02-07 | 12000 | 12 | 7.3 | 7.42 | 150 | 16 | 312 | 40 | 292 | 26 | NA | 400 | 0.3 | 22.99 | 1300000
2023-02-08 | 12560 | 12.56 | 7.32 | 7.44 | 130 | 15 | 309 | 48 | 285 | 29 | NA | 500 | 0.3 | 23.62 | 1500000
2023-02-09 | 12890 | 12.89 | 7.4 | 7.42 | 145 | 16 | 305 | 44 | 289 | 27 | NA | 600 | 0.3 | 23.22 | 1700000
2023-02-10 | 12010 | 12.01 | 7.3 | 7.45 | 135 | 17 | 312 | 40 | 267 | 25 | NA | 400 | 0.2 | 25.13 | 1400000
2023-02-11 | 12490 | 12.49 | 7.36 | 7.51 | 140 | 15 | 308 | 44 | 272 | 26 | NA | 700 | 0.3 | 24.17 | 1200000
2023-02-12 | 13520 | 13.52 | 7.27 | 7.38 | 145 | 18 | 300 | 48 | 286 | 24 | NA | 500 | 0.2 | 23.05 | 1700000
2023-02-13 | 12700 | 12.7 | 7.17 | 7.31 | 150 | 16 | 304 | 44 | 269 | 21 | NA | 400 | 0.3 | 24.07 | 1400000
2023-02-14 | 11280 | 11.28 | 7.15 | 7.29 | 130 | 17 | 312 | 40 | 275 | 19 | NA | 600 | 0.2 | 23.69 | 1300000
2023-02-15 | 11200 | 11.2 | 7.29 | 7.46 | 145 | 16 | 302 | 44 | 282 | 22 | NA | 700 | 0.3 | 23.86 | 1400000
2023-02-16 | 11500 | 11.85 | 7.26 | 7.32 | 130 | 18 | 304 | 48 | 290 | 28 | NA | 500 | 0.3 | 24.14 | 1200000
2023-02-17 | 12600 | 12.6 | 7.28 | 7.4 | 150 | 16 | 310 | 44 | 284 | 24 | NA | 400 | 0.3 | 24.01 | 1300000
2023-02-18 | 14180 | 14.18 | 7.24 | 7.35 | 135 | 17 | 300 | 40 | 292 | 21 | NA | 400 | 0.3 | 23.64 | 1400000
2023-02-19 | 12500 | 12.5 | 7.27 | 7.41 | 145 | 16 | 305 | 44 | 273 | 19 | NA | 500 | 0.3 | 22.9 | 1700000
2023-02-20 | 11870 | 11.87 | 7.23 | 7.4 | 130 | 15 | 302 | 48 | 287 | 20 | NA | 600 | 0.3 | 23.63 | 1500000
2023-02-21 | 12530 | 12.53 | 7.29 | 7.42 | 150 | 16 | 295 | 44 | 296 | 22 | NA | 500 | 0.3 | 22.72 | 1400000
2023-02-22 | 12060 | 12.06 | 7.3 | 7.41 | 135 | 17 | 304 | 48 | 292 | 21 | NA | 400 | 0.3 | 24.01 | 1200000
2023-02-23 | 11530 | 11.53 | 7.28 | 7.44 | 150 | 18 | 312 | 44 | 268 | 24 | NA | 400 | 0.2 | 22.48 | 1400000
2023-02-24 | 13120 | 13.12 | 7.3 | 7.43 | 140 | 15 | 310 | 48 | 298 | 25 | NA | 600 | 0.3 | 24.22 | 1300000
2023-02-25 | 12990 | 12.99 | 7.29 | 7.4 | 135 | 16 | 308 | 40 | 287 | 26 | NA | 500 | 0.3 | 23.49 | 1200000
2023-02-26 | 13600 | 13.6 | 7.25 | 7.43 | 130 | 17 | 304 | 48 | 295 | 27 | NA | 600 | 0.2 | 22.8 | 1400000
2023-02-27 | 12680 | 12.68 | 7.3 | 7.4 | 150 | 16 | 302 | 44 | 298 | 28 | NA | 400 | 0.3 | 22.57 | 1500000
2023-02-28 | 13680 | 13.68 | 7.24 | 7.37 | 145 | 15 | 310 | 48 | 282 | 27 | NA | 500 | 0.3 | 23.86 | 1700000
Average | 12508.2143 | 12.5207 | 7.2779 | 7.4039 | 140.8929 | 16.25 | 305.7143 | 44.4286 | 284.8571 | 24.5357 | NA | 507.1429 | 0.28571 | 23.4857 | 1417857.1429
350.58
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11200 | 11.2 | 7.15 | 7.29 | 130 | 15 | 295 | 40 | 267 | 19 |  | 400 | 0.2 | 22.48 | 1200000
Max | 14180 | 14.18 | 7.4 | 7.51 | 150 | 18 | 312 | 48 | 298 | 29 |  | 700 | 0.4 | 25.13 | 1700000