## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-02-01 | 62100 | 62.1 | 7.22 | 7.75 | 135 | 16 | 316 | 40 | 278 | 24 | NA | 500 | 0.3 | 23.27 | 1400000
2024-02-02 | 61900 | 61.9 | 7.26 | 7.78 | 130 | 15 | 324 | 44 | 281 | 26 | NA | 400 | 0.2 | 24.6 | 1200000
2024-02-03 | 60950 | 60.95 | 7.25 | 7.7 | 140 | 17 | 320 | 40 | 296 | 25 | NA | 600 | 0.3 | 23.08 | 1300000
2024-02-04 | 59960 | 59.96 | 7.28 | 7.76 | 145 | 16 | 312 | 40 | 288 | 27 | NA | 700 | 0.3 | 22.35 | 1700000
2024-02-05 | 56060 | 56.06 | 7.24 | 7.6 | 140 | 17 | 328 | 44 | 294 | 26 | NA | 400 | 0.3 | 23.4 | 1300000
2024-02-06 | 62100 | 62.1 | 7.31 | 7.69 | 130 | 15 | 316 | 40 | 284 | 28 | NA | 600 | 0.3 | 23.36 | 1400000
2024-02-07 | 59850 | 59.85 | 7.25 | 7.8 | 140 | 16 | 324 | 44 | 268 | 24 | NA | 400 | 0.2 | 22.04 | 1100000
2024-02-08 | 59620 | 59.62 | 7.28 | 7.77 | 130 | 17 | 328 | 40 | 294 | 26 | NA | 500 | 0.3 | 23.21 | 1400000
2024-02-09 | 60040 | 60.04 | 7.25 | 7.76 | 135 | 15 | 320 | 40 | 281 | 25 | NA | 700 | 0.2 | 24.12 | 1300000
2024-02-10 | 59450 | 59.45 | 7.2 | 7.8 | 135 | 16 | 324 | 44 | 278 | 24 | NA | 400 | 0.3 | 23.5 | 1200000
2024-02-11 | 59250 | 59.25 | 7.18 | 7.77 | 145 | 18 | 316 | 40 | 269 | 26 | NA | 500 | 0.3 | 24.11 | 1200000
2024-02-12 | 58900 | 58.9 | 7.1 | 7.68 | 130 | 15 | 324 | 44 | 274 | 27 | NA | 700 | 0.2 | 23.65 | 1700000
2024-02-13 | 60980 | 60.98 | 7.15 | 7.78 | 135 | 14 | 320 | 40 | 290 | 26 | NA | 600 | 0.3 | 24.08 | 1300000
2024-02-14 | 61650 | 61.65 | 7.11 | 7.68 | 145 | 17 | 328 | 44 | 283 | 24 | NA | 400 | 0.3 | 23.71 | 1400000
2024-02-15 | 58200 | 58.2 | 7.05 | 7.74 | 140 | 18 | 320 | 40 | 276 | 28 | NA | 600 | 0.2 | 23.05 | 1200000
2024-02-16 | 60500 | 60.5 | 7.12 | 7.67 | 135 | 16 | 324 | 36 | 291 | 27 | NA | 400 | 0.3 | 22.2 | 1100000
2024-02-17 | 59670 | 59.67 | 7.06 | 7.7 | 130 | 15 | 316 | 40 | 267 | 24 | NA | 700 | 0.2 | 23.66 | 1300000
2024-02-18 | 59700 | 59.7 | 7.16 | 7.74 | 145 | 17 | 328 | 44 | 281 | 27 | NA | 500 | 0.3 | 24.06 | 1100000
2024-02-19 | 58010 | 58.01 | 7.38 | 7.67 | 140 | 17 | 312 | 40 | 274 | 29 | NA | 400 | 0.2 | 23.32 | 1200000
2024-02-20 | 58970 | 58.97 | 7.57 | 7.7 | 135 | 16 | 304 | 40 | 268 | 27 | NA | 600 | 0.3 | 23.41 | 1400000
2024-02-21 | 59630 | 59.63 | 7.64 | 7.72 | 130 | 16 | 316 | 44 | 276 | 28 | NA | 400 | 0.3 | 24.55 | 1100000
2024-02-22 | 59740 | 59.74 | 7.6 | 7.71 | 145 | 18 | 324 | 40 | 288 | 26 | NA | 700 | 0.3 | 23.67 | 1400000
2024-02-23 | 61270 | 61.27 | 7.54 | 7.69 | 135 | 15 | 304 | 40 | 261 | 24 | NA | 500 | 0.2 | 23.77 | 1100000
2024-02-24 | 58820 | 58.82 | 7.61 | 7.7 | 130 | 16 | 316 | 44 | 274 | 26 | NA | 600 | 0.3 | 24.67 | 1300000
2024-02-25 | 59520 | 59.52 | 7.54 | 7.66 | 140 | 15 | 308 | 40 | 288 | 27 | NA | 400 | 0.2 | 23.41 | 1200000
2024-02-26 | 60180 | 60.18 | 7.36 | 7.72 | 135 | 16 | 324 | 44 | 279 | 25 | NA | 500 | 0.3 | 23.5 | 1400000
2024-02-27 | 62020 | 62.02 | 7.32 | 7.64 | 140 | 18 | 316 | 40 | 281 | 26 | NA | 700 | 0.2 | 22.21 | 1700000
2024-02-28 | 58890 | 58.89 | 7.28 | 7.62 | 130 | 16 | 308 | 36 | 298 | 28 | NA | 400 | 0.3 | 23.67 | 1300000
2024-02-29 | 58920 | 58.92 | 7.18 | 7.5 | 140 | 15 | 320 | 40 | 302 | 26 | NA | 600 | 0.3 | 23.84 | 1100000
Average | 59891.3793 | 59.8914 | 7.2928 | 7.7069 | 136.7241 | 16.1379 | 318.6207 | 41.1034 | 281.4483 | 26.069 |  | 531.0345 | 0.26552 | 23.499 | 1303448.2759
1736.85
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 56060 | 56.06 | 7.05 | 7.5 | 130 | 14 | 304 | 36 | 261 | 24 |  | 400 | 0.2 | 22.04 | 1100000
Max | 62100 | 62.1 | 7.64 | 7.8 | 145 | 18 | 328 | 44 | 302 | 29 |  | 700 | 0.3 | 24.67 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-02-01 | 39130 | 39.13 | 7.56 | 7.22 | 165 | 26 | 352 | 40 | 327 | 32 | NA | 700 | 0.3 | 23.72 | 1400000
2024-02-02 | 40470 | 40.47 | 7.49 | 7.25 | 160 | 24 | 360 | 44 | 321 | 34 | NA | 400 | 0.3 | 24.32 | 1200000
2024-02-03 | 39750 | 39.75 | 7.52 | 7.36 | 155 | 27 | 364 | 48 | 334 | 39 | NA | 600 | 0.3 | 22.92 | 1700000
2024-02-04 | 38980 | 38.98 | 7.56 | 7.28 | 160 | 24 | 360 | 44 | 330 | 42 | NA | 500 | 0.2 | 23.54 | 1400000
2024-02-05 | 43080 | 43.08 | 7.51 | 7.26 | 150 | 21 | 352 | 48 | 358 | 48 | NA | 500 | 0.3 | 24.26 | 1100000
2024-02-06 | 43520 | 43.52 | 7.54 | 7.41 | 155 | 23 | 244 | 76 | 348 | 44 | NA | 700 | 0.3 | 24.52 | 1300000
2024-02-07 | 41360 | 41.36 | 7.58 | 7.35 | 160 | 24 | 360 | 44 | 334 | 35 | NA | 600 | 0.2 | 24.05 | 1700000
2024-02-08 | 41680 | 41.68 | 7.55 | 7.38 | 165 | 26 | 356 | 40 | 328 | 32 | NA | 400 | 0.3 | 22.99 | 1400000
2024-02-09 | 41470 | 41.47 | 7.59 | 7.32 | 155 | 26 | 356 | 44 | 321 | 37 | NA | 600 | 0.3 | 24.33 | 1200000
2024-02-10 | 40030 | 40.03 | 7.64 | 7.29 | 160 | 25 | 352 | 40 | 330 | 33 | NA | 500 | 0.3 | 24.89 | 1300000
2024-02-11 | 41340 | 41.34 | 7.61 | 7.26 | 155 | 24 | 360 | 40 | 340 | 36 | NA | 700 | 0.3 | 24.79 | 1700000
2024-02-12 | 40160 | 40.16 | 7.43 | 7.22 | 160 | 24 | 364 | 48 | 336 | 40 | NA | 400 | 0.2 | 23.9 | 1400000
2024-02-13 | 41840 | 41.84 | 7.44 | 7.24 | 165 | 27 | 340 | 40 | 343 | 42 | NA | 600 | 0.3 | 24.24 | 1100000
2024-02-14 | 43890 | 43.89 | 7.46 | 7.32 | 155 | 26 | 352 | 48 | 347 | 41 | NA | 500 | 0.3 | 23.29 | 1200000
2024-02-15 | 41680 | 41.68 | 7.42 | 7.27 | 150 | 22 | 360 | 44 | 328 | 38 | NA | 400 | 0.3 | 24.77 | 1700000
2024-02-16 | 43050 | 43.05 | 7.45 | 7.3 | 160 | 25 | 364 | 44 | 334 | 37 | NA | 600 | 0.3 | 24.22 | 1400000
2024-02-17 | 39400 | 39.4 | 7.53 | 7.33 | 155 | 24 | 356 | 40 | 325 | 34 | NA | 500 | 0.3 | 24.78 | 1100000
2024-02-18 | 42910 | 42.91 | 7.45 | 7.36 | 165 | 27 | 364 | 48 | 342 | 38 | NA | 700 | 0.2 | 24.91 | 1300000
2024-02-19 | 38670 | 38.67 | 7.44 | 7.32 | 160 | 26 | 360 | 44 | 356 | 34 | NA | 600 | 0.2 | 24.09 | 1700000
2024-02-20 | 38450 | 38.45 | 7.48 | 7.35 | 155 | 23 | 380 | 36 | 430 | 29 | NA | 700 | 0.3 | 24.59 | 1400000
2024-02-21 | 41220 | 41.22 | 7.52 | 7.4 | 160 | 23 | 364 | 40 | 358 | 36 | NA | 500 | 0.3 | 24.71 | 1200000
2024-02-22 | 41930 | 41.93 | 7.43 | 7.38 | 165 | 24 | 360 | 44 | 355 | 38 | NA | 400 | 0.2 | 25.51 | 1100000
2024-02-23 | 41280 | 41.28 | 7.41 | 7.32 | 160 | 23 | 356 | 40 | 344 | 36 | NA | 600 | 0.3 | 25.26 | 1700000
2024-02-24 | 38300 | 38.3 | 7.36 | 7.45 | 155 | 27 | 352 | 40 | 336 | 37 | NA | 700 | 0.3 | 24.63 | - | On 24.02.2024, sample for testing fecal coliform of sludge was not found in lab. Hence, no value is written for that day.
2024-02-25 | 39100 | 39.1 | 7.41 | 7.32 | 150 | 26 | 356 | 44 | 327 | 36 | NA | 500 | 0.3 | 24.6 | 1300000
2024-02-26 | 39580 | 39.58 | 7.3 | 7.43 | 155 | 27 | 360 | 40 | 340 | 33 | NA | 600 | 0.2 | 25.61 | 1100000
2024-02-27 | 41720 | 41.72 | 7.35 | 7.45 | 160 | 28 | 364 | 44 | 347 | 36 | NA | 400 | 0.3 | 23.35 | 1400000
2024-02-28 | 41310 | 41.31 | 7.41 | 7.46 | 165 | 25 | 356 | 40 | 342 | 33 | NA | 700 | 0.3 | 24.05 | 1200000
2024-02-29 | 37280 | 37.28 | 7.37 | 7.48 | 155 | 24 | 352 | 40 | 358 | 37 | NA | 500 | 0.2 | 24.08 | 1300000
Average | 40778.6207 | 40.7786 | 7.4762 | 7.3372 | 158.2759 | 24.8621 | 354.3448 | 43.8621 | 342.0345 | 36.7931 |  | 555.1724 | 0.27241 | 24.3076 | 1357142.8571
1182.58
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 37280 | 37.28 | 7.3 | 7.22 | 150 | 21 | 244 | 36 | 321 | 29 |  | 400 | 0.2 | 22.92 | 1100000
Max | 43890 | 43.89 | 7.64 | 7.48 | 165 | 28 | 380 | 76 | 430 | 48 |  | 700 | 0.3 | 25.61 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-02-01 | 27440 | 27.44 | 7.19 | 7.34 | 135 | 15 | 284 | 44 | 263 | 18 | NA | 400 | 0.3 | 23.62 | 1400000
2024-02-02 | 28180 | 28.18 | 7.15 | 7.36 | 125 | 16 | 276 | 40 | 253 | 17 | NA | 600 | 0.2 | 22.89 | 1100000
2024-02-03 | 27330 | 27.33 | 7.18 | 7.47 | 130 | 13 | 312 | 36 | 287 | 19 | NA | 400 | 0.3 | 23.11 | 1200000
2024-02-04 | 27680 | 27.68 | 7.26 | 7.39 | 120 | 14 | 272 | 40 | 255 | 18 | NA | 500 | 0.3 | 22.36 | 1700000
2024-02-05 | 34590 | 34.59 | 7.19 | 7.33 | 125 | 15 | 286 | 44 | 273 | 20 | NA | 700 | 0.3 | 22.57 | 1200000
2024-02-06 | 27560 | 27.56 | 7.22 | 7.3 | 135 | 13 | 300 | 36 | 287 | 19 | NA | 500 | 0.2 | 24.24 | 1700000
2024-02-07 | 28740 | 28.74 | 7.2 | 7.32 | 130 | 14 | 292 | 40 | 272 | 18 | NA | 400 | 0.2 | 24.28 | 1100000
2024-02-08 | 27480 | 27.48 | 7.11 | 7.21 | 135 | 13 | 288 | 36 | 267 | 17 | NA | 400 | 0.2 | 23.05 | 1200000
2024-02-09 | 29100 | 29.1 | 7.14 | 7.29 | 140 | 12 | 308 | 40 | 296 | 18 | NA | 600 | 0.3 | 22.48 | 1400000
2024-02-10 | 25210 | 25.21 | 7.1 | 7.21 | 135 | 12 | 320 | 36 | 298 | 16 | NA | 800 | 0.2 | 23.01 | 1700000
2024-02-11 | 26340 | 26.34 | 7.09 | 7.25 | 130 | 16 | 304 | 44 | 265 | 18 | NA | 700 | 0.3 | 24.08 | 1400000
2024-02-12 | 26100 | 26.1 | 7.04 | 7.32 | 125 | 12 | 296 | 36 | 278 | 17 | NA | 400 | 0.2 | 22.62 | 1300000
2024-02-13 | 28780 | 28.78 | 7.02 | 7.29 | 135 | 13 | 292 | 40 | 259 | 19 | NA | 600 | 0.2 | 24.31 | 1400000
2024-02-14 | 28910 | 28.91 | 7.05 | 7.33 | 140 | 12 | 320 | 36 | 270 | 18 | NA | 700 | 0.3 | 23.33 | 1700000
2024-02-15 | 28330 | 28.33 | 7.23 | 7.15 | 150 | 14 | 328 | 40 | 280 | 16 | NA | 500 | 0.3 | 22.62 | 1200000
2024-02-16 | 28350 | 28.35 | 7.12 | 7.25 | 145 | 13 | 320 | 36 | 300 | 17 | NA | 600 | 0.3 | 24.3 | 1300000
2024-02-17 | 29230 | 29.23 | 7.2 | 7.24 | 135 | 15 | 304 | 40 | 285 | 18 | NA | 400 | 0.2 | 22.43 | 1700000
2024-02-18 | 29660 | 29.66 | 7.27 | 7.31 | 140 | 14 | 296 | 44 | 263 | 17 | NA | 600 | 0.3 | 24.66 | 1100000
2024-02-19 | 27840 | 27.84 | 7.19 | 7.27 | 130 | 12 | 308 | 40 | 268 | 17 | NA | 400 | 0.2 | 22.65 | 1400000
2024-02-20 | 27890 | 27.89 | 7.22 | 7.29 | 135 | 15 | 316 | 44 | 279 | 20 | NA | 700 | 0.2 | 23.2 | 1300000
2024-02-21 | 26450 | 26.45 | 7.15 | 7.23 | 140 | 13 | 324 | 40 | 286 | 18 | NA | 500 | 0.3 | 23.54 | 1100000
2024-02-22 | 28130 | 28.13 | 7.11 | 7.2 | 135 | 15 | 312 | 36 | 265 | 17 | NA | 600 | 0.2 | 22.94 | 1700000
2024-02-23 | 27930 | 27.93 | 7.13 | 7.24 | 130 | 13 | 304 | 40 | 271 | 18 | NA | 700 | 0.2 | 23.56 | 1300000
2024-02-24 | 27970 | 27.97 | 7.15 | 7.2 | 135 | 14 | 300 | 44 | 260 | 17 | NA | 500 | 0.3 | 23.06 | 1200000
2024-02-25 | 29690 | 29.69 | 7.28 | 7.21 | 130 | 13 | 292 | 36 | 257 | 18 | NA | 600 | 0.3 | 22.78 | 1700000
2024-02-26 | 28080 | 28.08 | 7.2 | 7.27 | 140 | 12 | 304 | 40 | 280 | 16 | NA | 400 | 0.3 | 22.39 | 1300000
2024-02-27 | 31890 | 31.89 | 7.36 | 7.29 | 135 | 14 | 212 | 32 | 255 | 14 | NA | 600 | 0.2 | 26.73 | 1400000
2024-02-28 | 28630 | 28.63 | 7.23 | 7.27 | 140 | 16 | 316 | 44 | 285 | 16 | NA | 400 | 0.3 | 23.88 | 1100000
2024-02-29 | 28750 | 28.75 | 7.31 | 7.48 | 130 | 12 | 308 | 36 | 274 | 17 | NA | 700 | 0.3 | 23.31 | 1400000
Average | 28353.7931 | 28.3538 | 7.1755 | 7.2866 | 134.1379 | 13.6207 | 299.7931 | 39.3103 | 273.4828 | 17.5172 |  | 548.2759 | 0.25517 | 23.3793 | 1368965.5172
822.26
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 25210 | 25.21 | 7.02 | 7.15 | 120 | 12 | 212 | 32 | 253 | 14 |  | 400 | 0.2 | 22.36 | 1100000
Max | 34590 | 34.59 | 7.36 | 7.48 | 150 | 16 | 328 | 44 | 300 | 20 |  | 800 | 0.3 | 26.73 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-02-01 | 12590 | 12.59 | 7.23 | 7.53 | 130 | 15 | 308 | 40 | 242 | 25 | NA | 600 | 0.3 | 23.98 | 1400000
2024-02-02 | 12120 | 12.12 | 7.26 | 7.54 | 125 | 16 | 304 | 36 | 229 | 24 | NA | 500 | 0.2 | 24.18 | 1700000
2024-02-03 | 12490 | 12.49 | 7.21 | 7.55 | 140 | 17 | 296 | 36 | 227 | 25 | NA | 400 | 0.3 | 23.94 | 1200000
2024-02-04 | 12080 | 12.08 | 7.23 | 7.52 | 145 | 15 | 316 | 32 | 234 | 23 | NA | 700 | 0.2 | 23.69 | 1300000
2024-02-05 | 12510 | 12.51 | 7.29 | 7.46 | 140 | 16 | 292 | 40 | 225 | 24 | NA | 500 | 0.3 | 24.29 | 1400000
2024-02-06 | 10990 | 10.99 | 7.31 | 7.51 | 145 | 15 | 312 | 36 | 242 | 27 | NA | 400 | 0.2 | 23.54 | 1700000
2024-02-07 | 12970 | 12.97 | 7.27 | 7.54 | 125 | 17 | 296 | 36 | 226 | 26 | NA | 600 | 0.3 | 23.89 | 1400000
2024-02-08 | 11470 | 11.47 | 7.34 | 7.56 | 135 | 16 | 304 | 40 | 231 | 25 | NA | 700 | 0.2 | 23.14 | 1200000
2024-02-09 | 11990 | 11.99 | 7.23 | 7.53 | 130 | 17 | 300 | 36 | 224 | 24 | NA | 500 | 0.3 | 23.42 | 1300000
2024-02-10 | 10850 | 10.85 | 7.2 | 7.47 | 135 | 15 | 284 | 40 | 212 | 21 | NA | 600 | 0.2 | 24.03 | 1100000
2024-02-11 | 12530 | 12.53 | 7.09 | 7.51 | 130 | 17 | 292 | 36 | 219 | 23 | NA | 400 | 0.3 | 23.82 | 1400000
2024-02-12 | 13690 | 13.69 | 6.98 | 7.45 | 140 | 16 | 280 | 32 | 209 | 22 | NA | 500 | 0.3 | 22.67 | 1200000
2024-02-13 | 12260 | 12.26 | 6.92 | 7.49 | 145 | 17 | 316 | 36 | 229 | 24 | NA | 700 | 0.2 | 23.04 | 1300000
2024-02-14 | 12580 | 12.58 | 6.8 | 7.52 | 145 | 16 | 312 | 40 | 234 | 25 | NA | 400 | 0.3 | 23.47 | 1700000
2024-02-15 | 12510 | 12.51 | 6.72 | 7.53 | 125 | 17 | 304 | 40 | 237 | 32 | NA | 600 | 0.3 | 22.62 | 1400000
2024-02-16 | 10960 | 10.96 | 6.68 | 7.54 | 135 | 16 | 300 | 32 | 231 | 22 | NA | 700 | 0.2 | 23.01 | 1200000
2024-02-17 | 12630 | 12.63 | 6.84 | 7.52 | 140 | 16 | 296 | 36 | 227 | 25 | NA | 500 | 0.3 | 23.42 | 1300000
2024-02-18 | 12310 | 12.31 | 6.94 | 7.58 | 130 | 15 | 304 | 32 | 225 | 24 | NA | 600 | 0.2 | 22.96 | 1400000
2024-02-19 | 11540 | 11.54 | 6.83 | 7.56 | 135 | 16 | 300 | 36 | 221 | 23 | NA | 400 | 0.3 | 23.1 | 1700000
2024-02-20 | 10730 | 10.73 | 6.85 | 7.54 | 145 | 17 | 308 | 40 | 232 | 25 | NA | 700 | 0.3 | 23.17 | 1200000
2024-02-21 | 10980 | 10.98 | 6.88 | 7.34 | 135 | 18 | 312 | 40 | 246 | 29 | NA | 600 | 0.3 | 23.58 | 1300000
2024-02-22 | 11720 | 11.72 | 6.92 | 7.55 | 130 | 17 | 280 | 44 | 215 | 19 | NA | 500 | 0.2 | 22.54 | 1400000
2024-02-23 | 10610 | 10.61 | 7.13 | 7.61 | 140 | 16 | 304 | 40 | 242 | 21 | NA | 400 | 0.3 | 22.91 | 1100000
2024-02-24 | 10730 | 10.73 | 7.08 | 7.63 | 125 | 15 | 292 | 36 | 222 | 28 | NA | 500 | 0.2 | 23.03 | 1400000
2024-02-25 | 11790 | 11.79 | 7.11 | 7.49 | 130 | 16 | 288 | 36 | 226 | 27 | NA | 700 | 0.3 | 23.16 | 1700000
2024-02-26 | 13080 | 13.08 | 7.19 | 7.46 | 145 | 17 | 292 | 40 | 240 | 28 | NA | 500 | 0.2 | 23.03 | 1400000
2024-02-27 | 12930 | 12.93 | 7.03 | 7.51 | 140 | 18 | 280 | 44 | 215 | 19 | NA | 400 | 0.3 | 22.54 | 1100000
2024-02-28 | 13480 | 13.48 | 7.24 | 7.4 | 145 | 16 | 304 | 36 | 231 | 25 | NA | 500 | 0.2 | 24.49 | 1200000
2024-02-29 | 13170 | 13.17 | 7.21 | 7.46 | 125 | 17 | 332 | 40 | 275 | 29 | NA | 600 | 0.3 | 23.89 | 1300000
Average | 12078.9655 | 12.079 | 7.0693 | 7.5138 | 135.6897 | 16.2759 | 300.2759 | 37.5172 | 229.931 | 24.6207 |  | 541.3793 | 0.25862 | 23.3983 | 1358620.6897
350.29
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 10610 | 10.61 | 6.68 | 7.34 | 125 | 15 | 280 | 32 | 209 | 19 |  | 400 | 0.2 | 22.54 | 1100000
Max | 13690 | 13.69 | 7.34 | 7.63 | 145 | 18 | 332 | 44 | 275 | 32 |  | 700 | 0.3 | 24.49 | 1700000