## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-01-01 | 64840 | 64.84 | 7.24 | 7.6 | 130 | 15 | 336 | 36 | 266 | 26 | NA | 700 | 0.2 | 23.07 | 1400000
2022-01-02 | 66540 | 66.54 | 7.2 | 7.64 | 140 | 17 | 308 | 40 | 232 | 28 | NA | 400 | 0.2 | 24.72 | 1400000
2022-01-03 | 64660 | 64.66 | 7.15 | 7.7 | 150 | 17 | 324 | 36 | 288 | 24 | NA | 500 | 0.3 | 23.19 | 1700000
2022-01-04 | 63540 | 63.54 | 7.19 | 7.69 | 135 | 15 | 340 | 40 | 246 | 28 | NA | 500 | 0.3 | 25.42 | 1300000
2022-01-05 | 61900 | 61.9 | 7.28 | 7.88 | 145 | 17 | 324 | 36 | 276 | 28 | NA | 400 | 0.3 | 23.9 | 1700000
2022-01-06 | 55670 | 55.67 | 7.18 | 7.72 | 140 | 15 | 312 | 32 | 246 | 28 | NA | 400 | 0.2 | 23.8 | 1700000
2022-01-07 | 52650 | 52.65 | 7.27 | 7.84 | 135 | 18 | 316 | 40 | 272 | 26 | NA | 600 | 0.3 | 24.72 | 1400000
2022-01-08 | 56740 | 56.74 | 7.2 | 7.74 | 130 | 16 | 324 | 36 | 230 | 24 | NA | 500 | 0.2 | 25.2 | 1300000
2022-01-09 | 59560 | 59.56 | 7.18 | 7.84 | 150 | 17 | 336 | 40 | 238 | 26 | NA | 700 | 0.3 | 22.92 | 1400000
2022-01-10 | 58760 | 58.76 | 7.34 | 7.89 | 135 | 16 | 328 | 36 | 248 | 28 | NA | 500 | 0.2 | 23.92 | 1300000
2022-01-11 | 61900 | 61.9 | 7.17 | 7.61 | 150 | 17 | 316 | 40 | 228 | 24 | NA | 600 | 0.3 | 23.52 | 1400000
2022-01-12 | 63110 | 63.11 | 7.21 | 7.84 | 135 | 16 | 304 | 36 | 256 | 26 | NA | 400 | 0.3 | 24.9 | 1300000
2022-01-13 | 62850 | 62.85 | 7.31 | 7.6 | 145 | 15 | 336 | 36 | 260 | 24 | NA | 800 | 0.2 | 23.07 | 1400000
2022-01-14 | 62400 | 62.4 | 7.19 | 7.72 | 140 | 16 | 316 | 40 | 240 | 28 | NA | 700 | 0.3 | 24.5 | 1300000
2022-01-15 | 65480 | 65.48 | 7.3 | 7.78 | 135 | 17 | 280 | 44 | 272 | 24 | NA | 400 | 0.3 | 24.34 | 1400000
2022-01-16 | 65120 | 65.12 | 7.38 | 7.84 | 135 | 13 | 296 | 40 | 232 | 26 | NA | 500 | 0.3 | 23.53 | 1400000
2022-01-17 | 61260 | 61.26 | 7.28 | 7.69 | 145 | 15 | 288 | 36 | 250 | 28 | NA | 400 | 0.2 | 23.8 | 1300000
2022-01-18 | 62840 | 62.84 | 7.18 | 7.72 | 140 | 16 | 328 | 40 | 236 | 24 | NA | 500 | 0.3 | 23.13 | 1700000
2022-01-19 | 63090 | 63.09 | 7.26 | 7.8 | 135 | 15 | 308 | 40 | 230 | 26 | NA | 400 | 0.2 | 23.92 | 1300000
2022-01-20 | 63020 | 63.02 | 7.24 | 7.84 | 150 | 13 | 324 | 36 | 250 | 28 | NA | 600 | 0.3 | 24.09 | 1300000
2022-01-21 | 63800 | 63.8 | 7.2 | 7.64 | 135 | 13 | 328 | 40 | 264 | 26 | NA | 500 | 0.3 | 24.12 | 1700000
2022-01-22 | 62120 | 62.12 | 7.16 | 7.21 | 145 | 17 | 336 | 36 | 272 | 28 | NA | 400 | 0.3 | 23.53 | 1400000
2022-01-23 | 63500 | 63.5 | 7.22 | 7.74 | 135 | 14 | 325 | 36 | 270 | 28 | NA | 500 | 0.2 | 23.48 | 1300000
2022-01-24 | 65450 | 65.45 | 7.32 | 7.58 | 140 | 15 | 336 | 32 | 264 | 24 | NA | 600 | 0.2 | 24.47 | 1400000
2022-01-25 | 64560 | 64.56 | 7.24 | 7.64 | 130 | 16 | 336 | 40 | 240 | 28 | NA | 500 | 0.3 | 24.84 | 1300000
2022-01-26 | 63840 | 63.84 | 7.16 | 7.7 | 145 | 17 | 332 | 36 | 236 | 26 | NA | 700 | 0.3 | 23.45 | 1700000
2022-01-27 | 63540 | 63.54 | 7.28 | 7.64 | 140 | 13 | 320 | 36 | 246 | 28 | NA | 500 | 0.2 | 24.73 | 1300000
2022-01-28 | 65660 | 65.66 | 7.22 | 7.69 | 145 | 17 | 328 | 32 | 228 | 24 | NA | 400 | 0.3 | 23.18 | 1400000
2022-01-29 | 60400 | 60.4 | 7.26 | 7.7 | 140 | 15 | 336 | 40 | 256 | 22 | NA | 700 | 0.2 | 22.15 | 1700000
2022-01-30 | 62260 | 62.26 | 7.3 | 7.84 | 135 | 16 | 316 | 36 | 236 | 24 | NA | 400 | 0.3 | 22.53 | 1400000
2022-01-31 | 63080 | 63.08 | 7.37 | 7.9 | 130 | 14 | 324 | 44 | 240 | 26 | NA | 500 | 0.3 | 23.85 | 1300000
Average | 62391.6129 | 62.3916 | 7.2413 | 7.7181 | 139.3548 | 15.5806 | 321.3226 | 37.6774 | 249.9355 | 26.0645 | NA | 522.5806 | 0.26129 | 23.8706 | 1429032.2581
1934.14
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 52650 | 52.65 | 7.15 | 7.21 | 130 | 13 | 280 | 32 | 228 | 22 |  | 400 | 0.2 | 22.15 | 1300000
Max | 66540 | 66.54 | 7.38 | 7.9 | 150 | 18 | 340 | 44 | 288 | 28 |  | 800 | 0.3 | 25.42 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-01-01 | 37890 | 37.89 | 7.32 | 7.5 | 153 | 24 | 360 | 44 | 319 | 41 | NA | 500 | 0.2 | 23.8 | 1300000
2022-01-02 | 36890 | 36.89 | 7.29 | 7.47 | 157 | 26 | 348 | 40 | 324 | 42 | NA | 700 | 0.2 | 24.9 | 1200000
2022-01-03 | 34370 | 34.37 | 7.37 | 7.54 | 153 | 23 | 344 | 44 | 313 | 38 | NA | 500 | 0.3 | 23.4 | 1100000
2022-01-04 | 41430 | 41.43 | 7.38 | 7.49 | 160 | 25 | 360 | 48 | 325 | 43 | NA | 800 | 0.2 | 25 | 1300000
2022-01-05 | 39770 | 39.77 | 7.31 | 7.53 | 149 | 22 | 352 | 40 | 318 | 37 | NA | 600 | 0.2 | 22.5 | 1100000
2022-01-06 | 40620 | 40.62 | 7.36 | 7.57 | 144 | 26 | 340 | 36 | 332 | 40 | NA | 400 | 0.3 | 23.1 | 1600000
2022-01-07 | 40950 | 40.95 | 7.39 | 7.55 | 146 | 24 | 336 | 40 | 313 | 35 | NA | 700 | 0.2 | 22.9 | 1300000
2022-01-08 | 43540 | 43.54 | 7.31 | 7.58 | 153 | 27 | 348 | 36 | 302 | 39 | NA | 500 | 0.2 | 22.2 | 1400000
2022-01-09 | 44390 | 44.39 | 7.37 | 7.6 | 160 | 25 | 360 | 44 | 321 | 41 | NA | 600 | 0.3 | 21.6 | 1100000
2022-01-10 | 45210 | 45.21 | 7.4 | 7.52 | 166 | 28 | 364 | 48 | 334 | 38 | NA | 800 | 0.2 | 23.3 | 1200000
2022-01-11 | 44420 | 44.42 | 7.35 | 7.56 | 159 | 26 | 368 | 44 | 329 | 42 | NA | 500 | 0.2 | 24 | 1100000
2022-01-12 | 37870 | 37.87 | 7.39 | 7.52 | 153 | 23 | 356 | 40 | 309 | 36 | NA | 400 | 0.2 | 24.7 | 1400000
2022-01-13 | 43210 | 43.21 | 7.33 | 7.48 | 157 | 25 | 360 | 36 | 318 | 37 | NA | 700 | 0.3 | 25.1 | 1700000
2022-01-14 | 41210 | 41.21 | 7.28 | 7.53 | 160 | 28 | 364 | 40 | 323 | 34 | NA | 600 | 0.2 | 23.5 | 1300000
2022-01-15 | 38990 | 38.99 | 7.32 | 7.59 | 153 | 26 | 352 | 36 | 312 | 33 | NA | 500 | 0.3 | 22.8 | 1200000
2022-01-16 | 39320 | 39.32 | 7.36 | 7.54 | 159 | 27 | 356 | 44 | 298 | 36 | NA | 700 | 0.2 | 24.2 | 1400000
2022-01-17 | 37260 | 37.26 | 7.31 | 7.46 | 156 | 24 | 348 | 40 | 305 | 35 | NA | 500 | 0.3 | 22 | 1100000
2022-01-18 | 39350 | 39.35 | 7.28 | 7.42 | 163 | 26 | 352 | 36 | 314 | 37 | NA | 800 | 0.2 | 23.2 | 1200000
2022-01-19 | 34100 | 34.1 | 7.25 | 7.48 | 153 | 23 | 344 | 32 | 302 | 31 | NA | 600 | 0.2 | 24.6 | 1400000
2022-01-20 | 33390 | 33.39 | 7.34 | 7.51 | 147 | 25 | 348 | 36 | 295 | 33 | NA | 500 | 0.3 | 25.4 | 1300000
2022-01-21 | 34300 | 34.3 | 7.29 | 7.49 | 156 | 24 | 356 | 40 | 310 | 38 | NA | 700 | 0.3 | 23.9 | 1100000
2022-01-22 | 34350 | 34.35 | 7.31 | 7.54 | 160 | 26 | 352 | 44 | 318 | 37 | NA | 500 | 0.2 | 22.6 | 1400000
2022-01-23 | 36290 | 36.29 | 7.36 | 7.53 | 153 | 22 | 356 | 40 | 309 | 35 | NA | 600 | 0.3 | 24.3 | 1300000
2022-01-24 | 36840 | 36.84 | 7.37 | 7.56 | 157 | 24 | 364 | 36 | 322 | 32 | NA | 700 | 0.2 | 23.2 | 1200000
2022-01-25 | 41450 | 41.45 | 7.3 | 7.61 | 163 | 26 | 360 | 44 | 315 | 38 | NA | 500 | 0.3 | 22.4 | 1100000
2022-01-26 | 42560 | 42.56 | 7.38 | 7.52 | 159 | 27 | 364 | 48 | 325 | 40 | NA | 400 | 0.3 | 23.7 | 1200000
2022-01-27 | 41630 | 41.63 | 7.4 | 7.55 | 166 | 25 | 368 | 40 | 312 | 39 | NA | 600 | 0.2 | 24.6 | 1400000
2022-01-28 | 42560 | 42.56 | 7.42 | 7.64 | 147 | 23 | 360 | 44 | 305 | 37 | NA | 800 | 0.3 | 22.2 | 1300000
2022-01-29 | 35310 | 35.31 | 7.35 | 7.58 | 157 | 22 | 356 | 40 | 319 | 34 | NA | 500 | 0.2 | 22.9 | 1100000
2022-01-30 | 38630 | 38.63 | 7.32 | 7.49 | 153 | 24 | 364 | 36 | 323 | 33 | NA | 700 | 0.3 | 24.2 | 1600000
2022-01-31 | 35940 | 35.94 | 7.36 | 7.52 | 156 | 25 | 352 | 40 | 318 | 36 | NA | 600 | 0.3 | 25.3 | 1200000
Average | 39162.5806 | 39.1626 | 7.341 | 7.5313 | 155.7419 | 24.871 | 355.2258 | 40.5161 | 315.5484 | 37 | NA | 596.7742 | 0.24516 | 23.5968 | 1277419.3548
1214.04
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 33390 | 33.39 | 7.25 | 7.42 | 144 | 22 | 336 | 32 | 295 | 31 |  | 400 | 0.2 | 21.6 | 1100000
Max | 45210 | 45.21 | 7.42 | 7.64 | 166 | 28 | 368 | 48 | 334 | 43 |  | 800 | 0.3 | 25.4 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-01-01 | 31860 | 31.86 | 7.39 | 7.68 | 147 | 13 | 316 | 36 | 265 | 17 | NA | 400 | 0.2 | 23.9 | 1400000 | 1. There is small leakage in retaining wall due to which raw sewage is bypassing to river. This leakage must be rectified. 2. Strengthening of retaining wall is required so that it does not break down during rains & flood.
2022-01-02 | 32360 | 32.36 | 7.29 | 7.51 | 141 | 12 | 324 | 40 | 258 | 16 | NA | 500 | 0.3 | 24.1 | 1200000
2022-01-03 | 32020 | 32.02 | 7.18 | 7.56 | 144 | 14 | 308 | 32 | 267 | 18 | NA | 700 | 0.2 | 23.6 | 1300000
2022-01-04 | 33350 | 33.35 | 7.25 | 7.59 | 153 | 13 | 320 | 36 | 272 | 17 | NA | 600 | 0.3 | 23.9 | 1400000
2022-01-05 | 32540 | 32.54 | 7.37 | 7.64 | 147 | 14 | 328 | 40 | 255 | 16 | NA | 700 | 0.3 | 23.66 | 1600000
2022-01-06 | 35830 | 35.83 | 7.29 | 7.68 | 138 | 16 | 316 | 44 | 278 | 21 | NA | 500 | 0.2 | 23.3 | 1300000
2022-01-07 | 36590 | 36.59 | 7.31 | 7.73 | 132 | 17 | 304 | 48 | 284 | 24 | NA | 600 | 0.3 | 23.89 | 1600000
2022-01-08 | 32100 | 32.1 | 7.37 | 7.69 | 141 | 15 | 296 | 44 | 275 | 23 | NA | 700 | 0.2 | 24.17 | 1400000
2022-01-09 | 35620 | 35.62 | 7.27 | 7.61 | 135 | 14 | 292 | 48 | 279 | 22 | NA | 500 | 0.3 | 23.64 | 1300000
2022-01-10 | 31570 | 31.57 | 7.34 | 7.67 | 144 | 13 | 300 | 40 | 272 | 20 | NA | 600 | 0.2 | 23.88 | 1400000
2022-01-11 | 30340 | 30.34 | 7.41 | 7.78 | 141 | 14 | 308 | 44 | 265 | 18 | NA | 500 | 0.3 | 24.09 | 1200000
2022-01-12 | 30730 | 30.73 | 7.32 | 7.72 | 147 | 12 | 312 | 40 | 275 | 21 | NA | 700 | 0.2 | 23.77 | 1300000
2022-01-13 | 31220 | 31.22 | 7.36 | 7.66 | 138 | 13 | 320 | 36 | 262 | 19 | NA | 600 | 0.3 | 24.26 | 1400000
2022-01-14 | 31760 | 31.76 | 7.39 | 7.61 | 144 | 14 | 316 | 32 | 271 | 17 | NA | 500 | 0.2 | 23.31 | 1300000
2022-01-15 | 29540 | 29.54 | 7.28 | 7.57 | 150 | 15 | 324 | 40 | 259 | 16 | NA | 400 | 0.3 | 24.11 | 1200000
2022-01-16 | 31260 | 31.26 | 7.41 | 7.68 | 141 | 13 | 316 | 36 | 266 | 17 | NA | 700 | 0.2 | 22.83 | 1400000
2022-01-17 | 29690 | 29.69 | 7.32 | 7.63 | 153 | 14 | 320 | 32 | 256 | 15 | NA | 600 | 0.3 | 23.41 | 1300000
2022-01-18 | 29570 | 29.57 | 7.37 | 7.59 | 147 | 12 | 328 | 40 | 263 | 16 | NA | 500 | 0.2 | 22.9 | 1600000
2022-01-19 | 29160 | 29.16 | 7.31 | 7.67 | 144 | 13 | 316 | 36 | 269 | 17 | NA | 700 | 0.2 | 23.33 | 1400000
2022-01-20 | 29710 | 29.71 | 7.18 | 7.54 | 138 | 12 | 308 | 32 | 258 | 18 | NA | 600 | 0.3 | 22.46 | 1200000
2022-01-21 | 28980 | 28.98 | 7.26 | 7.59 | 150 | 14 | 320 | 40 | 263 | 16 | NA | 500 | 0.2 | 22.86 | 1300000
2022-01-22 | 30350 | 30.35 | 7.31 | 7.67 | 144 | 13 | 312 | 36 | 274 | 17 | NA | 400 | 0.3 | 23.75 | 1200000
2022-01-23 | 31570 | 31.57 | 7.21 | 7.74 | 156 | 14 | 324 | 32 | 265 | 18 | NA | 600 | 0.2 | 23.18 | 1300000
2022-01-24 | 29890 | 29.89 | 7.34 | 7.62 | 147 | 15 | 316 | 40 | 259 | 16 | NA | 500 | 0.3 | 22.93 | 1400000
2022-01-25 | 28520 | 28.52 | 7.27 | 7.66 | 141 | 13 | 320 | 36 | 271 | 17 | NA | 700 | 0.2 | 23.21 | 1300000
2022-01-26 | 29610 | 29.61 | 7.22 | 7.56 | 144 | 12 | 308 | 32 | 264 | 18 | NA | 400 | 0.3 | 22.84 | 1200000
2022-01-27 | 27450 | 27.45 | 7.36 | 7.67 | 138 | 14 | 324 | 36 | 258 | 17 | NA | 500 | 0.2 | 23.14 | 1300000
2022-01-28 | 28560 | 28.56 | 7.3 | 7.59 | 153 | 13 | 316 | 40 | 268 | 19 | NA | 600 | 0.3 | 23.27 | 1400000
2022-01-29 | 29390 | 29.39 | 7.28 | 7.63 | 147 | 12 | 312 | 36 | 261 | 22 | NA | 500 | 0.2 | 22.63 | 1200000
2022-01-30 | 28780 | 28.78 | 7.34 | 7.67 | 156 | 13 | 320 | 40 | 254 | 20 | NA | 700 | 0.3 | 22.95 | 1300000
2022-01-31 | 27890 | 27.89 | 7.25 | 7.72 | 144 | 11 | 308 | 32 | 272 | 19 | NA | 400 | 0.2 | 23.27 | 1400000
Average | 30897.0968 | 30.8971 | 7.3081 | 7.6429 | 144.6774 | 13.4516 | 314.5806 | 37.9355 | 266.3871 | 18.2903 | NA | 561.2903 | 0.24839 | 23.4368 | 1338709.6774
957.81
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 27450 | 27.45 | 7.18 | 7.51 | 132 | 11 | 292 | 32 | 254 | 15 |  | 400 | 0.2 | 22.46 | 1200000
Max | 36590 | 36.59 | 7.41 | 7.78 | 156 | 17 | 328 | 48 | 284 | 24 |  | 700 | 0.3 | 24.26 | 1600000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - < 20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - < 30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-01-01 | 13220 | 13.22 | 7.2 | 7.48 | 138 | 15 | 316 | 40 | 260 | 21 | NA | 500 | 0.3 | 20.76 | 1600000
2022-01-02 | 13150 | 13.15 | 7.31 | 7.57 | 130 | 17 | 304 | 44 | 268 | 23 | NA | 400 | 0.2 | 21.6 | 1300000
1912-07-25 | 12240 | 12.24 | 7.15 | 7.68 | 135 | 16 | 320 | 38 | 280 | 22 | NA | 500 | 0.2 | 21.33 | 1700000
2022-01-04 | 12350 | 12.35 | 7.24 | 7.51 | 145 | 14 | 328 | 32 | 265 | 20 | NA | 600 | 0.2 | 22.55 | 1400000
2022-01-05 | 12140 | 12.14 | 7.16 | 7.46 | 140 | 15 | 308 | 36 | 273 | 23 | NA | 500 | 0.3 | 22.13 | 1300000
2022-01-06 | 12450 | 12.45 | 7.29 | 7.73 | 136 | 14 | 300 | 40 | 282 | 25 | NA | 700 | 0.2 | 21.46 | 1700000
2022-01-07 | 15890 | 15.89 | 7.46 | 7.81 | 130 | 13 | 292 | 36 | 276 | 22 | NA | 600 | 0.2 | 20.38 | 1400000
2022-01-08 | 15490 | 15.49 | 7.33 | 7.69 | 132 | 15 | 296 | 40 | 266 | 24 | NA | 500 | 0.3 | 21.18 | 1600000
2022-01-09 | 14980 | 14.98 | 7.17 | 7.38 | 140 | 13 | 312 | 32 | 255 | 21 | NA | 400 | 0.2 | 22.27 | 1400000
2022-01-10 | 14510 | 14.51 | 7.26 | 7.56 | 135 | 14 | 304 | 36 | 263 | 19 | NA | 600 | 0.2 | 21.53 | 1300000
2022-01-11 | 13970 | 13.97 | 7.19 | 7.41 | 142 | 13 | 316 | 32 | 258 | 20 | NA | 500 | 0.3 | 22.63 | 1600000
2022-01-12 | 13910 | 13.91 | 7.28 | 7.64 | 150 | 15 | 324 | 36 | 270 | 18 | NA | 600 | 0.2 | 20.31 | 1200000
2022-01-13 | 13720 | 13.72 | 7.21 | 7.53 | 145 | 14 | 308 | 40 | 261 | 21 | NA | 400 | 0.3 | 21.18 | 1400000
2022-01-14 | 13610 | 13.61 | 7.31 | 7.76 | 152 | 13 | 320 | 36 | 248 | 23 | NA | 500 | 0.2 | 20.58 | 1600000
2022-01-15 | 13880 | 13.88 | 7.18 | 7.66 | 146 | 15 | 312 | 42 | 257 | 22 | NA | 400 | 0.3 | 22.41 | 1300000
2022-01-16 | 13460 | 13.46 | 7.14 | 7.48 | 155 | 13 | 328 | 32 | 262 | 20 | NA | 600 | 0.2 | 21.75 | 1400000
2022-01-17 | 13210 | 13.21 | 7.27 | 7.54 | 148 | 14 | 316 | 36 | 272 | 18 | NA | 500 | 0.3 | 22.25 | 1600000
2022-01-18 | 12620 | 12.62 | 7.22 | 7.61 | 144 | 15 | 304 | 40 | 246 | 21 | NA | 700 | 0.3 | 23.12 | 1400000
2022-01-19 | 12360 | 12.36 | 7.34 | 7.79 | 140 | 14 | 310 | 36 | 256 | 19 | NA | 500 | 0.2 | 21.68 | 1200000
2022-01-20 | 12450 | 12.45 | 7.17 | 7.58 | 150 | 13 | 324 | 32 | 243 | 22 | NA | 600 | 0.3 | 22.4 | 1400000
2022-01-21 | 12690 | 12.69 | 7.13 | 7.47 | 145 | 14 | 312 | 36 | 268 | 20 | NA | 700 | 0.2 | 22.17 | 1300000
2022-01-22 | 12180 | 12.18 | 7.26 | 7.63 | 142 | 13 | 316 | 32 | 276 | 21 | NA | 600 | 0.2 | 21.32 | 1600000
2022-01-23 | 12590 | 12.59 | 7.31 | 7.69 | 148 | 15 | 324 | 40 | 262 | 22 | NA | 500 | 0.3 | 22.89 | 1400000
2022-01-24 | 12200 | 12.2 | 7.11 | 7.56 | 144 | 14 | 308 | 36 | 254 | 20 | NA | 600 | 0.2 | 20.34 | 1300000
2022-01-25 | 12080 | 12.08 | 7.21 | 7.51 | 140 | 15 | 300 | 40 | 247 | 23 | NA | 500 | 0.2 | 21.52 | 1600000
2022-01-26 | 11870 | 11.87 | 7.38 | 7.72 | 146 | 16 | 310 | 44 | 260 | 21 | NA | 400 | 0.3 | 22.15 | 1400000
2022-01-27 | 12230 | 12.23 | 7.28 | 7.66 | 150 | 14 | 320 | 36 | 255 | 19 | NA | 700 | 0.2 | 22.78 | 1300000
2022-01-28 | 11920 | 11.92 | 7.16 | 7.41 | 145 | 13 | 304 | 32 | 271 | 22 | NA | 500 | 0.2 | 21.66 | 1200000
2022-01-29 | 12690 | 12.69 | 7.31 | 7.56 | 148 | 15 | 316 | 40 | 264 | 23 | NA | 400 | 0.3 | 22.87 | 1400000
2022-01-30 | 12520 | 12.52 | 7.18 | 7.61 | 155 | 14 | 324 | 36 | 250 | 21 | NA | 600 | 0.2 | 20.43 | 1600000
2022-01-31 | 12140 | 12.14 | 7.27 | 7.48 | 142 | 15 | 308 | 40 | 277 | 20 | NA | 500 | 0.3 | 21.7 | 1300000
Average | 13055.4839 | 13.0555 | 7.2413 | 7.5861 | 143.1613 | 14.2903 | 312.3871 | 37.0323 | 262.7419 | 21.1613 | NA | 535.4839 | 0.24194 | 21.7203 | 1425806.4516
404.72
Source: | Logbook of Labarotory at Sewage Treament Plant
Min | 11870 | 11.87 | 7.11 | 7.38 | 130 | 13 | 292 | 32 | 243 | 18 |  | 400 | 0.2 | 20.31 | 1200000
Max | 15890 | 15.89 | 7.46 | 7.81 | 155 | 17 | 328 | 44 | 282 | 25 |  | 700 | 0.3 | 23.12 | 1700000