## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-01-01 | 60100 | 60.1 | 7.31 | 7.84 | 130 | 15 | 316 | 40 | 254 | 24 | NA | 400 | 0.3 | 24.27 | 1200000
2024-01-02 | 58360 | 58.36 | 7.3 | 7.88 | 145 | 16 | 320 | 40 | 262 | 26 | NA | 700 | 0.3 | 23.17 | 1400000
2024-01-03 | 55250 | 55.25 | 7.2 | 7.9 | 135 | 15 | 328 | 44 | 272 | 27 | NA | 400 | 0.2 | 23.81 | 1300000
2024-01-04 | 59110 | 59.11 | 7.11 | 7.88 | 145 | 17 | 316 | 40 | 298 | 26 | NA | 500 | 0.3 | 24.06 | 1100000
2024-01-05 | 62750 | 62.75 | 7.16 | 7.84 | 140 | 16 | 308 | 44 | 258 | 23 | NA | 600 | 0.2 | 22.87 | 1400000
2024-01-06 | 59300 | 59.3 | 7.1 | 7.86 | 135 | 17 | 312 | 40 | 268 | 25 | NA | 400 | 0.3 | 23.25 | 1200000
2024-01-07 | 57100 | 57.1 | 7.04 | 7.93 | 130 | 14 | 320 | 36 | 280 | 26 | NA | 600 | 0.2 | 24.08 | 1700000
2024-01-08 | 61220 | 61.22 | 7.26 | 7.95 | 125 | 15 | 328 | 40 | 286 | 24 | NA | 500 | 0.3 | 22.1 | 1400000
2024-01-09 | 59800 | 59.8 | 7.28 | 7.75 | 135 | 15 | 296 | 40 | 262 | 24 | NA | 700 | 0.3 | 23.89 | 1300000
2024-01-10 | 62270 | 62.27 | 7.18 | 7.77 | 145 | 17 | 316 | 44 | 281 | 25 | NA | 600 | 0.3 | 23.41 | 1400000
2024-01-11 | 61190 | 61.19 | 7.3 | 7.81 | 125 | 16 | 304 | 40 | 286 | 23 | NA | 400 | 0.2 | 24.11 | 1700000
2024-01-12 | 62280 | 62.28 | 7.28 | 7.76 | 130 | 14 | 312 | 36 | 264 | 27 | NA | 700 | 0.3 | 22.8 | 1200000
2024-01-13 | 60190 | 60.19 | 7.24 | 7.76 | 150 | 15 | 320 | 44 | 284 | 26 | NA | 500 | 0.3 | 23.08 | 1400000
2024-01-14 | 61290 | 61.29 | 7.32 | 7.83 | 145 | 17 | 308 | 40 | 288 | 28 | NA | 400 | 0.2 | 23.31 | 1200000
2024-01-15 | 60120 | 60.12 | 7.42 | 7.76 | 135 | 14 | 316 | 44 | 281 | 26 | NA | 600 | 0.2 | 24.2 | 1400000
2024-01-16 | 58820 | 58.82 | 7.38 | 7.78 | 140 | 16 | 340 | 40 | 298 | 25 | NA | 700 | 0.3 | 23.98 | 1200000
2024-01-17 | 59250 | 59.25 | 7.4 | 7.84 | 145 | 17 | 320 | 44 | 280 | 24 | NA | 400 | 0.2 | 24.13 | 1100000
2024-01-18 | 57880 | 57.88 | 7.38 | 7.82 | 135 | 15 | 312 | 40 | 255 | 23 | NA | 500 | 0.3 | 24.01 | 1700000
2024-01-19 | 59900 | 59.9 | 7.3 | 7.78 | 145 | 15 | 316 | 36 | 294 | 25 | NA | 700 | 0.3 | 23.87 | 1400000
2024-01-20 | 59610 | 59.61 | 7.32 | 7.84 | 135 | 14 | 300 | 36 | 278 | 23 | NA | 400 | 0.2 | 23.27 | 1300000
2024-01-21 | 60350 | 60.35 | 7.22 | 7.8 | 145 | 16 | 304 | 40 | 268 | 25 | NA | 600 | 0.3 | 24.18 | 1700000
2024-01-22 | 59850 | 59.85 | 7.3 | 7.82 | 130 | 15 | 320 | 44 | 283 | 24 | NA | 500 | 0.3 | 23.29 | 1100000
2024-01-23 | 59990 | 59.99 | 7.26 | 7.81 | 140 | 14 | 312 | 40 | 287 | 26 | NA | 700 | 0.3 | 22.88 | 1300000
2024-01-24 | 58940 | 58.94 | 7.28 | 7.86 | 130 | 16 | 304 | 36 | 266 | 23 | NA | 400 | 0.2 | 23.27 | 1200000
2024-01-25 | 58750 | 58.75 | 7.4 | 7.82 | 140 | 15 | 316 | 40 | 271 | 26 | NA | 600 | 0.3 | 24.66 | 1100000
2024-01-26 | 61000 | 61 | 7.37 | 7.78 | 130 | 16 | 320 | 40 | 281 | 24 | NA | 500 | 0.2 | 22.07 | 1100000
2024-01-27 | 60270 | 60.27 | 7.25 | 7.74 | 145 | 18 | 328 | 44 | 290 | 25 | NA | 700 | 0.3 | 23.87 | 1400000
2024-01-28 | 59650 | 59.65 | 7.32 | 7.79 | 135 | 15 | 320 | 40 | 265 | 24 | NA | 400 | 0.2 | 24.01 | 1300000
2024-01-29 | 57300 | 57.3 | 7.16 | 7.82 | 140 | 17 | 336 | 44 | 295 | 26 | NA | 600 | 0.3 | 23.98 | 1400000
2024-01-30 | 61000 | 61 | 7.21 | 7.78 | 145 | 16 | 324 | 40 | 263 | 24 | NA | 500 | 0.3 | 23.77 | 1700000
2024-01-31 | 61050 | 61.05 | 7.26 | 7.72 | 135 | 17 | 304 | 44 | 278 | 26 | NA | 700 | 0.2 | 24.07 | 1400000
Average | 59804.5161 | 59.8045 | 7.2681 | 7.8168 | 137.5806 | 15.6452 | 316 | 40.6452 | 276.6452 | 24.9355 | NA | 545.1613 | 0.26129 | 23.6039 | 1345161.2903
1853.94
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 55250 | 55.25 | 7.04 | 7.72 | 125 | 14 | 296 | 36 | 254 | 23 |  | 400 | 0.2 | 22.07 | 1100000
Max | 62750 | 62.75 | 7.42 | 7.95 | 150 | 18 | 340 | 44 | 298 | 28 |  | 700 | 0.3 | 24.66 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-01-01 | 37900 | 37.9 | 7.58 | 7.39 | 165 | 27 | 336 | 40 | 311 | 34 | NA | 700 | 0.3 | 24.07 | 1400000
2024-01-02 | 36400 | 36.4 | 7.61 | 7.36 | 155 | 22 | 340 | 36 | 318 | 35 | NA | 500 | 0.27 | 23.69 | 1700000
2024-01-03 | 38460 | 38.46 | 7.63 | 7.03 | 155 | 21 | 332 | 36 | 312 | 34 | NA | 600 | 0.26 | 22.73 | 1400000
2024-01-04 | 34900 | 34.9 | 7.57 | 7.07 | 160 | 23 | 344 | 40 | 350 | 31 | NA | 500 | 0.28 | 23.71 | 1300000
2024-01-05 | 36530 | 36.53 | 7.52 | 7.23 | 155 | 24 | 352 | 48 | 365 | 37 | NA | 600 | 0.3 | 23.1 | 1400000
2024-01-06 | 36920 | 36.92 | 7.58 | 7.28 | 165 | 25 | 340 | 44 | 336 | 45 | NA | 400 | 0.31 | 24.2 | 1200000
2024-01-07 | 39200 | 39.2 | 7.53 | 7.24 | 160 | 23 | 364 | 48 | 355 | 46 | NA | 700 | 0.3 | 23.86 | 1400000
2024-01-08 | 37020 | 37.02 | 7.55 | 7.27 | 155 | 24 | 356 | 44 | 346 | 42 | NA | 500 | 0.27 | 24.38 | 1300000
2024-01-09 | 38450 | 38.45 | 7.63 | 7.21 | 155 | 26 | 344 | 48 | 312 | 40 | NA | 500 | 0.3 | 23.23 | 1400000
2024-01-10 | 34530 | 34.53 | 7.61 | 7.25 | 160 | 22 | 308 | 48 | 328 | 37 | NA | 700 | 0.29 | 22.62 | 1700000
2024-01-11 | 36010 | 36.01 | 7.6 | 7.22 | 165 | 25 | 328 | 44 | 320 | 39 | NA | 700 | 0.3 | 24.72 | 1400000
2024-01-12 | 37240 | 37.24 | 7.56 | 7.19 | 160 | 23 | 336 | 40 | 313 | 36 | NA | 600 | 0.28 | 24.88 | 1700000
2024-01-13 | 38760 | 38.76 | 7.54 | 7.25 | 165 | 26 | 340 | 44 | 295 | 37 | NA | 500 | 0.31 | 23.35 | 1400000
2024-01-14 | 39110 | 39.11 | 7.57 | 7.18 | 165 | 25 | 344 | 40 | 328 | 35 | NA | 700 | 0.31 | 23.67 | 1100000
2024-01-15 | 40600 | 40.6 | 7.61 | 7.22 | 160 | 23 | 316 | 44 | 307 | 38 | NA | 400 | 0.29 | 23.08 | 1400000 | Sample collection for 15.01.2024 was not correct as samples from 6AM to 12 PM were not collected for influent. In this case influent testing cannot be deemed as accurate.
2024-01-16 | 38860 | 38.86 | 7.64 | 7.23 | 155 | 21 | 340 | 40 | 335 | 37 | NA | 700 | 0.3 | 23.09 | 1700000
2024-01-17 | 37900 | 37.9 | 7.62 | 7.21 | 160 | 24 | 360 | 44 | 326 | 39 | NA | 400 | 0.3 | 24.44 | 1400000
2024-01-18 | 35790 | 35.79 | 7.58 | 7.26 | 165 | 26 | 364 | 40 | 348 | 38 | NA | 600 | 0.3 | 22.47 | 1100000
2024-01-19 | 38460 | 38.46 | 7.65 | 7.21 | 155 | 22 | 360 | 40 | 331 | 35 | NA | 700 | 0.2 | 23.49 | 1700000
2024-01-20 | 36440 | 36.44 | 7.62 | 7.23 | 170 | 23 | 352 | 36 | 318 | 36 | NA | 500 | 0.3 | 22.6 | 1300000
2024-01-21 | 38570 | 38.57 | 7.66 | 7.28 | 160 | 22 | 356 | 40 | 310 | 34 | NA | 600 | 0.3 | 23.17 | 1700000
2024-01-22 | 39520 | 39.52 | 7.68 | 7.22 | 165 | 24 | 348 | 36 | 315 | 33 | NA | 400 | 0.2 | 23.87 | 1200000
2024-01-23 | 36480 | 36.48 | 7.65 | 7.24 | 160 | 25 | 344 | 40 | 348 | 35 | NA | 700 | 0.3 | 23.77 | 1400000
2024-01-24 | 37100 | 37.1 | 7.68 | 7.27 | 155 | 24 | 352 | 44 | 327 | 32 | NA | 500 | 0.3 | 23.58 | 1100000
2024-01-25 | 36680 | 36.68 | 7.64 | 7.21 | 165 | 26 | 364 | 40 | 336 | 37 | NA | 700 | 0.3 | 24.42 | 1300000
2024-01-26 | 36730 | 36.73 | 7.72 | 7.28 | 160 | 25 | 356 | 44 | 347 | 34 | NA | 600 | 0.2 | 23.98 | 1700000
2024-01-27 | 35630 | 35.63 | 7.67 | 7.32 | 155 | 27 | 364 | 40 | 370 | 39 | NA | 400 | 0.3 | 23.5 | 1400000
2024-01-28 | 36840 | 36.84 | 7.63 | 7.23 | 160 | 26 | 360 | 48 | 354 | 36 | NA | 600 | 0.3 | 23.15 | 1200000
2024-01-29 | 40520 | 40.52 | 7.65 | 7.27 | 150 | 28 | 352 | 44 | 332 | 38 | NA | 500 | 0.3 | 24.55 | 1700000
2024-01-30 | 39020 | 39.02 | 7.6 | 7.29 | 155 | 25 | 356 | 40 | 320 | 35 | NA | 400 | 0.3 | 24.38 | 1300000
2024-01-31 | 38250 | 38.25 | 7.58 | 7.35 | 160 | 26 | 360 | 44 | 332 | 37 | NA | 500 | 0.2 | 24.06 | 1100000
Average | 37574.8387 | 37.5748 | 7.6116 | 7.2416 | 159.6774 | 24.2903 | 347.3548 | 42.0645 | 330.4839 | 36.8065 |  | 561.2903 | 0.2829 | 23.6713 | 1403225.8065
1164.82
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 34530 | 34.53 | 7.52 | 7.03 | 150 | 21 | 308 | 36 | 295 | 31 |  | 400 | 0.2 | 22.47 | 1100000
Max | 40600 | 40.6 | 7.72 | 7.39 | 170 | 28 | 364 | 48 | 370 | 46 |  | 700 | 0.31 | 24.88 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-01-01 | 29170 | 29.17 | 7.33 | 7.35 | 120 | 12 | 324 | 36 | 297 | 22 | NA | 500 | 0.2 | 22.73 | 1700000
2024-01-02 | 28510 | 28.51 | 7.41 | 7.33 | 130 | 11 | 320 | 32 | 301 | 24 | NA | 400 | 0.2 | 23.92 | 1300000
2024-01-03 | 31230 | 31.23 | 7.45 | 7.26 | 125 | 14 | 340 | 36 | 314 | 26 | NA | 700 | 0.3 | 23.46 | 1400000
2024-01-04 | 28510 | 28.51 | 7.2 | 7.32 | 120 | 13 | 328 | 40 | 317 | 25 | NA | 500 | 0.3 | 22.87 | 1400000
2024-01-05 | 28450 | 28.45 | 7.13 | 7.35 | 125 | 12 | 316 | 36 | 286 | 19 | NA | 600 | 0.2 | 22.42 | 1100000
2024-01-06 | 27760 | 27.76 | 6.88 | 7.35 | 135 | 13 | 330 | 36 | 320 | 18 | NA | 500 | 0.2 | 23.16 | 1200000
2024-01-07 | 29790 | 29.79 | 7.01 | 7.38 | 130 | 14 | 324 | 40 | 308 | 16 | NA | 400 | 0.2 | 22.38 | 1700000
2024-01-08 | 29160 | 29.16 | 7.17 | 7.4 | 125 | 13 | 336 | 36 | 315 | 18 | NA | 600 | 0.3 | 23.67 | 1100000
2024-01-09 | 29340 | 29.34 | 7.21 | 7.36 | 130 | 14 | 328 | 40 | 310 | 17 | NA | 500 | 0.3 | 24.13 | 1400000
2024-01-10 | 28970 | 28.97 | 7.25 | 7.37 | 140 | 13 | 316 | 36 | 292 | 16 | NA | 700 | 0.3 | 22.79 | 1300000
2024-01-11 | 28960 | 28.96 | 7.28 | 7.38 | 120 | 14 | 348 | 40 | 329 | 18 | NA | 500 | 0.2 | 23.14 | 1200000
2024-01-12 | 27570 | 27.57 | 7.24 | 7.33 | 140 | 10 | 356 | 36 | 347 | 17 | NA | 600 | 0.2 | 22.56 | 1700000
2024-01-13 | 28780 | 28.78 | 7.16 | 7.32 | 135 | 11 | 320 | 32 | 303 | 18 | NA | 400 | 0.2 | 23.02 | 1400000
2024-01-14 | 28300 | 28.3 | 7.13 | 7.3 | 130 | 12 | 332 | 36 | 325 | 17 | NA | 700 | 0.2 | 22.63 | 1300000
2024-01-15 | 28450 | 28.45 | 7.15 | 7.29 | 120 | 11 | 324 | 32 | 316 | 18 | NA | 500 | 0.2 | 23.68 | 1100000
2024-01-16 | 27240 | 27.24 | 7.18 | 7.25 | 135 | 12 | 360 | 36 | 352 | 17 | NA | 400 | 0.2 | 23.85 | 1200000
2024-01-17 | 27770 | 27.77 | 7.27 | 7.3 | 130 | 11 | 324 | 36 | 306 | 19 | NA | 700 | 0.3 | 24.53 | 1400000
2024-01-18 | 28530 | 28.53 | 7.34 | 7.29 | 125 | 13 | 320 | 40 | 293 | 18 | NA | 400 | 0.2 | 23.34 | 1300000
2024-01-19 | 29570 | 29.57 | 7.36 | 7.28 | 130 | 12 | 332 | 36 | 315 | 19 | NA | 600 | 0.3 | 22.63 | 1700000
2024-01-20 | 27430 | 27.43 | 7.3 | 7.24 | 135 | 13 | 312 | 36 | 280 | 16 | NA | 700 | 0.2 | 22.31 | 1200000
2024-01-21 | 28130 | 28.13 | 7.15 | 7.29 | 140 | 12 | 328 | 40 | 326 | 15 | NA | 600 | 0.3 | 22.83 | 1100000
2024-01-22 | 28830 | 28.83 | 7.18 | 7.31 | 130 | 13 | 320 | 36 | 277 | 17 | NA | 400 | 0.3 | 23.5 | 1700000
2024-01-23 | 28890 | 28.89 | 7.16 | 7.27 | 135 | 12 | 332 | 40 | 317 | 16 | NA | 500 | 0.3 | 22.64 | 1300000
2024-01-24 | 27630 | 27.63 | 7.14 | 7.32 | 130 | 14 | 364 | 36 | 352 | 17 | NA | 400 | 0.2 | 23.38 | 1400000
2024-01-25 | 28150 | 28.15 | 7.18 | 7.29 | 120 | 13 | 316 | 40 | 298 | 18 | NA | 700 | 0.3 | 23.51 | 1300000
2024-01-26 | 28820 | 28.82 | 7.13 | 7.35 | 130 | 12 | 312 | 36 | 286 | 19 | NA | 600 | 0.2 | 22.53 | 1700000
2024-01-27 | 28560 | 28.56 | 7.25 | 7.3 | 135 | 11 | 332 | 40 | 320 | 17 | NA | 500 | 0.2 | 23.31 | 1200000
2024-01-28 | 28630 | 28.63 | 7.23 | 7.35 | 145 | 13 | 336 | 36 | 292 | 18 | NA | 400 | 0.3 | 24.33 | 1400000
2024-01-29 | 28050 | 28.05 | 7.2 | 7.32 | 135 | 14 | 316 | 40 | 288 | 17 | NA | 600 | 0.3 | 23.1 | 1700000
2024-01-30 | 28530 | 28.53 | 7.13 | 7.37 | 125 | 15 | 304 | 36 | 278 | 18 | NA | 500 | 0.2 | 23.4 | 1100000
2024-01-31 | 27260 | 27.26 | 7.16 | 7.42 | 130 | 13 | 296 | 40 | 269 | 19 | NA | 700 | 0.3 | 24.07 | 1300000
Average | 28547.4194 | 28.5474 | 7.2052 | 7.3239 | 130.1613 | 12.5806 | 327.2903 | 37.0323 | 307.3871 | 18.3548 |  | 541.9355 | 0.24516 | 23.22 | 1364516.129
884.97
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 27240 | 27.24 | 6.88 | 7.24 | 120 | 10 | 296 | 32 | 269 | 15 |  | 400 | 0.2 | 22.31 | 1100000
Max | 31230 | 31.23 | 7.45 | 7.42 | 145 | 15 | 364 | 40 | 352 | 26 |  | 700 | 0.3 | 24.53 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-01-01 | 12880 | 12.88 | 7.12 | 7.55 | 135 | 16 | 300 | 36 | 229 | 24 | NA | 600 | 0.2 | 24.32 | 1300000
2024-01-02 | 11410 | 11.41 | 7.09 | 7.61 | 140 | 17 | 292 | 40 | 224 | 27 | NA | 400 | 0.3 | 23.8 | 1700000
2024-01-03 | 11450 | 11.45 | 7.19 | 7.57 | 135 | 15 | 312 | 36 | 246 | 26 | NA | 500 | 0.2 | 24.03 | 1400000
2024-01-04 | 11580 | 11.58 | 7.16 | 7.59 | 140 | 16 | 288 | 36 | 225 | 27 | NA | 700 | 0.3 | 24.29 | 1200000
2024-01-05 | 11210 | 11.21 | 7.14 | 7.61 | 135 | 17 | 292 | 40 | 219 | 26 | NA | 600 | 0.2 | 23.7 | 1700000
2024-01-06 | 10180 | 10.18 | 7.26 | 7.56 | 140 | 15 | 312 | 36 | 243 | 23 | NA | 400 | 0.3 | 24.15 | 1300000
2024-01-07 | 10510 | 10.51 | 7.18 | 7.58 | 135 | 16 | 288 | 36 | 223 | 22 | NA | 500 | 0.2 | 23.98 | 1200000
2024-01-08 | 11160 | 11.16 | 7.16 | 7.54 | 140 | 15 | 296 | 40 | 227 | 24 | NA | 700 | 0.3 | 24.42 | 1700000
2024-01-09 | 12430 | 12.43 | 7.04 | 7.49 | 135 | 16 | 304 | 36 | 233 | 23 | NA | 600 | 0.2 | 23.75 | 1400000
2024-01-10 | 12650 | 12.65 | 7.08 | 7.59 | 140 | 14 | 300 | 36 | 229 | 22 | NA | 400 | 0.3 | 23.86 | 1300000
2024-01-11 | 12360 | 12.36 | 7.02 | 7.58 | 130 | 16 | 296 | 32 | 224 | 21 | NA | 500 | 0.2 | 24.11 | 1200000
2024-01-12 | 11450 | 11.45 | 7.19 | 7.6 | 135 | 15 | 308 | 36 | 239 | 20 | NA | 700 | 0.3 | 23.62 | 1700000
2024-01-13 | 12070 | 12.07 | 7.11 | 7.61 | 125 | 16 | 288 | 32 | 221 | 23 | NA | 600 | 0.2 | 23.82 | 1300000
2024-01-14 | 12690 | 12.69 | 7.07 | 7.59 | 120 | 14 | 276 | 36 | 218 | 22 | NA | 400 | 0.3 | 23.26 | 1400000
2024-01-15 | 13090 | 13.09 | 7.1 | 7.53 | 130 | 16 | 284 | 32 | 220 | 21 | NA | 500 | 0.2 | 24.29 | 1200000
2024-01-16 | 12810 | 12.81 | 7.23 | 7.57 | 140 | 15 | 296 | 36 | 225 | 20 | NA | 700 | 0.3 | 23.02 | 1700000
2024-01-17 | 12330 | 12.33 | 7.04 | 7.54 | 130 | 16 | 300 | 32 | 223 | 22 | NA | 600 | 0.2 | 24.15 | 1300000
2024-01-18 | 12990 | 12.99 | 7.06 | 7.56 | 135 | 15 | 304 | 36 | 227 | 21 | NA | 400 | 0.3 | 23.3 | 1200000
2024-01-19 | 12410 | 12.41 | 7.21 | 7.62 | 130 | 14 | 308 | 32 | 231 | 20 | NA | 500 | 0.2 | 23.94 | 1400000
2024-01-20 | 12260 | 12.26 | 7.24 | 7.58 | 140 | 17 | 312 | 40 | 252 | 25 | NA | 700 | 0.3 | 24.12 | 1700000
2024-01-21 | 12950 | 12.95 | 7.27 | 7.53 | 135 | 16 | 296 | 36 | 227 | 27 | NA | 600 | 0.2 | 24.29 | 1300000
2024-01-22 | 12160 | 12.16 | 7.29 | 7.56 | 130 | 14 | 304 | 32 | 232 | 25 | NA | 400 | 0.3 | 23.86 | 1200000
2024-01-23 | 12600 | 12.6 | 7.18 | 7.54 | 135 | 16 | 312 | 36 | 256 | 26 | NA | 500 | 0.2 | 24.03 | 1400000
2024-01-24 | 10230 | 10.23 | 7.12 | 7.53 | 130 | 15 | 300 | 32 | 224 | 20 | NA | 700 | 0.3 | 23.76 | 1700000
2024-01-25 | 12350 | 12.35 | 7.08 | 7.57 | 140 | 16 | 316 | 36 | 249 | 21 | NA | 600 | 0.3 | 23.16 | 1200000
2024-01-26 | 13080 | 13.08 | 7.14 | 7.58 | 125 | 17 | 304 | 40 | 228 | 23 | NA | 400 | 0.2 | 23.68 | 1300000
2024-01-27 | 12780 | 12.78 | 7.16 | 7.56 | 130 | 16 | 296 | 36 | 221 | 24 | NA | 500 | 0.3 | 24.19 | 1400000
2024-01-28 | 11970 | 11.97 | 7.18 | 7.58 | 140 | 14 | 312 | 32 | 242 | 23 | NA | 700 | 0.2 | 24.02 | 1200000
2024-01-29 | 12910 | 12.91 | 7.13 | 7.53 | 130 | 16 | 288 | 36 | 218 | 22 | NA | 600 | 0.3 | 23.9 | 1700000
2024-01-30 | 12710 | 12.71 | 7.17 | 7.55 | 135 | 15 | 304 | 36 | 223 | 21 | NA | 400 | 0.2 | 23.72 | 1300000
2024-01-31 | 12390 | 12.39 | 7.12 | 7.54 | 140 | 17 | 312 | 40 | 252 | 23 | NA | 500 | 0.3 | 24.11 | 1400000
Average | 12130.6452 | 12.1306 | 7.1461 | 7.5658 | 134.1935 | 15.5806 | 300 | 35.7419 | 230.6452 | 23.0323 |  | 545.1613 | 0.25161 | 23.8919 | 1400000
376.05
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 10180 | 10.18 | 7.02 | 7.49 | 120 | 14 | 276 | 32 | 218 | 20 |  | 400 | 0.2 | 23.02 | 1200000
Max | 13090 | 13.09 | 7.29 | 7.62 | 140 | 17 | 316 | 40 | 256 | 27 |  | 700 | 0.3 | 24.42 | 1700000