## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-01-01 | 59720 | 59.72 | 7.22 | 7.64 | 135 | 14 | 336 | 36 | 288 | 17 | NA | 400 | 0.4 | 24.81 | 1300000
2023-01-02 | 60180 | 60.18 | 7.19 | 7.72 | 140 | 18 | 328 | 36 | 264 | 22 | NA | 600 | 0.4 | 23.09 | 1400000
2023-01-03 | 58720 | 58.72 | 7.18 | 7.8 | 130 | 15 | 300 | 44 | 282 | 21 | NA | 600 | 0.3 | 22.81 | 1700000
2023-01-04 | 60830 | 60.83 | 7.19 | 7.64 | 150 | 17 | 324 | 44 | 240 | 20 | NA | 500 | 0.4 | 23.41 | 1200000
2023-01-05 | 57270 | 57.27 | 7.21 | 7.58 | 145 | 18 | 320 | 36 | 272 | 21 | NA | 400 | 0.3 | 22.49 | 1400000
2023-01-06 | 58930 | 58.93 | 7.16 | 7.74 | 135 | 16 | 328 | 48 | 278 | 20 | NA | 600 | 0.3 | 23.5 | 1300000
2023-01-07 | 56230 | 56.23 | 7.23 | 7.77 | 130 | 14 | 304 | 44 | 288 | 20 | NA | 400 | 0.4 | 24.37 | 1200000
2023-01-08 | 57680 | 57.68 | 7.28 | 7.59 | 140 | 15 | 312 | 40 | 296 | 28 | NA | 600 | 0.3 | 23.22 | 1400000
2023-01-09 | 58640 | 58.64 | 7.24 | 7.66 | 150 | 19 | 304 | 36 | 274 | 22 | NA | 700 | 0.4 | 24.1 | 1300000
2023-01-10 | 58310 | 58.31 | 7.26 | 7.74 | 135 | 16 | 300 | 36 | 292 | 21 | NA | 500 | 0.3 | 23.56 | 1700000
2023-01-11 | 57190 | 57.91 | 7.19 | 7.72 | 140 | 17 | 324 | 48 | 298 | 22 | NA | 600 | 0.4 | 22.58 | 1200000
2023-01-12 | 59930 | 59.93 | 7.22 | 7.64 | 145 | 16 | 304 | 36 | 286 | 22 | NA | 400 | 0.4 | 23.56 | 1400000
2023-01-13 | 58070 | 58.07 | 7.26 | 7.74 | 150 | 17 | 324 | 44 | 283 | 17 | NA | 700 | 0.3 | 23.5 | 1700000
2023-01-14 | 59440 | 59.44 | 7.18 | 7.67 | 140 | 19 | 300 | 36 | 277 | 23 | NA | 500 | 0.4 | 24.59 | 1200000
2023-01-15 | 59120 | 59.12 | 7.28 | 7.76 | 135 | 17 | 340 | 48 | 294 | 24 | NA | 400 | 0.3 | 22.85 | 1300000
2023-01-16 | 58190 | 58.19 | 7.23 | 7.66 | 145 | 19 | 312 | 44 | 292 | 21 | NA | 600 | 0.4 | 23.58 | 1400000
2023-01-17 | 60310 | 60.31 | 7.26 | 7.74 | 130 | 15 | 328 | 36 | 287 | 24 | NA | 500 | 0.4 | 23.44 | 1700000
2023-01-18 | 57990 | 57.99 | 7.19 | 7.72 | 140 | 17 | 308 | 44 | 298 | 21 | NA | 700 | 0.3 | 24.26 | 1200000
2023-01-19 | 59170 | 59.17 | 7.25 | 7.68 | 130 | 15 | 336 | 36 | 283 | 19 | NA | 600 | 0.4 | 23.78 | 1400000
1900-01-19 | 60260 | 60.26 | 7.23 | 7.73 | 140 | 18 | 316 | 44 | 288 | 20 | NA | 400 | 0.4 | 23.22 | 1700000
2023-01-21 | 63570 | 63.57 | 7.28 | 7.68 | 145 | 17 | 328 | 36 | 278 | 22 | NA | 500 | 0.4 | 23.57 | 1400000
2023-01-22 | 59050 | 59.05 | 7.24 | 7.73 | 130 | 15 | 304 | 36 | 289 | 21 | NA | 600 | 0.3 | 22.85 | 1700000
2023-01-23 | 60430 | 60.43 | 7.26 | 7.64 | 150 | 19 | 316 | 44 | 275 | 21 | NA | 400 | 0.4 | 24.23 | 1200000
2023-01-24 | 59350 | 59.35 | 7.29 | 7.66 | 140 | 18 | 324 | 40 | 293 | 20 | NA | 700 | 0.4 | 23.64 | 1400000
2023-01-25 | 55700 | 55.7 | 7.23 | 7.74 | 130 | 17 | 304 | 44 | 287 | 23 | NA | 500 | 0.3 | 23.69 | 1700000
2023-01-26 | 58770 | 58.77 | 7.27 | 7.75 | 135 | 16 | 320 | 44 | 296 | 22 | NA | 600 | 0.4 | 24.82 | 1300000
2023-01-27 | 60290 | 60.29 | 7.25 | 7.69 | 145 | 18 | 312 | 40 | 287 | 21 | NA | 400 | 0.3 | 23.76 | 1400000
2023-01-28 | 59740 | 59.74 | 7.24 | 7.73 | 140 | 17 | 304 | 44 | 294 | 24 | NA | 700 | 0.4 | 24.09 | 1300000
2023-01-29 | 60720 | 60.72 | 7.27 | 7.66 | 150 | 19 | 324 | 40 | 288 | 22 | NA | 500 | 0.3 | 23.68 | 1400000
2023-01-30 | 62450 | 62.45 | 7.21 | 7.74 | 125 | 16 | 316 | 44 | 296 | 21 | NA | 400 | 0.4 | 23.3 | 1700000
2023-01-31 | 61730 | 61.73 | 7.26 | 7.68 | 140 | 19 | 320 | 48 | 308 | 26 | NA | 600 | 0.3 | 24.26 | 1400000
Average | 59289.6774 | 59.3129 | 7.2339 | 7.6981 | 139.1935 | 16.871 | 316.7742 | 41.1613 | 285.5161 | 21.5484 | NA | 535.4839 | 0.35806 | 23.6326 | 1419354.8387
1838.7
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 55700 | 55.7 | 7.16 | 7.58 | 125 | 14 | 300 | 36 | 240 | 17 |  | 400 | 0.3 | 22.49 | 1200000
Max | 63570 | 63.57 | 7.29 | 7.8 | 150 | 19 | 340 | 48 | 308 | 28 |  | 700 | 0.4 | 24.82 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-01-01 | 42430 | 42.43 | 7.38 | 7.53 | 165 | 23 | 356 | 40 | 312 | 31 | NA | 700 | 0.3 | 25.3 | 1400000
2023-01-02 | 38330 | 38.33 | 7.41 | 7.5 | 160 | 22 | 368 | 36 | 295 | 30 | NA | 400 | 0.3 | 24.9 | 1200000
2023-01-03 | 37490 | 37.49 | 7.42 | 7.51 | 165 | 21 | 372 | 40 | 320 | 31 | NA | 600 | 0.2 | 24.5 | 1400000
2023-01-04 | 37830 | 37.83 | 7.4 | 7.52 | 160 | 22 | 372 | 40 | 330 | 32 | NA | 500 | 0.3 | 24.8 | 1400000
2023-01-05 | 36810 | 36.81 | 7.48 | 7.54 | 155 | 23 | 368 | 44 | 310 | 31 | NA | 800 | 0.3 | 24.4 | 1100000
2023-01-06 | 40380 | 40.38 | 7.49 | 7.56 | 165 | 25 | 344 | 40 | 335 | 36 | NA | 500 | 0.2 | 24.7 | 1200000
2023-01-07 | 41720 | 41.72 | 7.42 | 7.64 | 155 | 24 | 352 | 44 | 339 | 40 | NA | 800 | 0.2 | 24.5 | 1400000
2023-01-08 | 39710 | 39.71 | 7.47 | 7.55 | 160 | 26 | 360 | 40 | 323 | 38 | NA | 600 | 0.3 | 24.6 | 1400000
2023-01-09 | 40320 | 40.32 | 7.49 | 7.54 | 165 | 27 | 368 | 48 | 345 | 40 | NA | 400 | 0.3 | 25.1 | 1200000
2023-01-10 | 46340 | 46.34 | 7.43 | 7.56 | 170 | 28 | 388 | 48 | 371 | 49 | NA | 700 | 0.2 | 24.9 | 1700000
2023-01-11 | 45120 | 45.12 | 7.47 | 7.54 | 160 | 28 | 384 | 44 | 382 | 48 | NA | 800 | 0.3 | 24.7 | 1400000
2023-01-12 | 46030 | 46.03 | 7.45 | 7.52 | 165 | 29 | 372 | 48 | 358 | 45 | NA | 600 | 0.3 | 25 | 1300000
2023-01-13 | 47070 | 47.07 | 7.48 | 7.46 | 170 | 30 | 368 | 52 | 344 | 51 | NA | 500 | 0.3 | 23.6 | 1700000
2023-01-14 | 52110 | 52.11 | 7.42 | 7.51 | 160 | 31 | 360 | 52 | 339 | 50 | NA | 700 | 0.2 | 25.4 | 1400000
2023-01-15 | 51050 | 51.05 | 7.44 | 7.55 | 165 | 33 | 372 | 48 | 336 | 52 | NA | 800 | 0.3 | 24.9 | 1200000
2023-01-16 | 48980 | 48.98 | 7.41 | 7.52 | 155 | 32 | 368 | 52 | 341 | 51 | NA | 600 | 0.2 | 25.2 | 1400000
2023-01-17 | 48810 | 48.81 | 7.4 | 7.54 | 165 | 33 | 364 | 52 | 337 | 50 | NA | 700 | 0.3 | 25.3 | 1300000
2023-01-18 | 47740 | 47.74 | 7.42 | 7.49 | 155 | 30 | 372 | 48 | 329 | 45 | NA | 800 | 0.3 | 25.1 | 1100000
2023-01-19 | 44020 | 44.02 | 7.38 | 7.48 | 160 | 27 | 364 | 44 | 321 | 37 | NA | 600 | 0.2 | 24.8 | 1400000
1900-01-19 | 43880 | 43.88 | 7.43 | 7.53 | 165 | 25 | 368 | 40 | 342 | 30 | NA | 700 | 0.3 | 24.2 | 1200000
2023-01-21 | 48100 | 48.1 | 7.36 | 7.5 | 160 | 28 | 360 | 44 | 338 | 32 | NA | 600 | 0.3 | 23.7 | 1400000
2023-01-22 | 46550 | 46.55 | 7.4 | 7.51 | 155 | 27 | 364 | 44 | 330 | 31 | NA | 400 | 0.2 | 24.5 | 1300000
2023-01-23 | 47580 | 47.58 | 7.38 | 7.49 | 160 | 28 | 360 | 40 | 324 | 30 | NA | 800 | 0.3 | 24.6 | 1700000
2023-01-24 | 49020 | 49.02 | 7.42 | 7.54 | 155 | 29 | 356 | 44 | 312 | 32 | NA | 600 | 0.3 | 25.1 | 1400000
2023-01-25 | 48950 | 48.95 | 7.38 | 7.57 | 165 | 32 | 360 | 52 | 326 | 39 | NA | 500 | 0.2 | 24.9 | 1200000
2023-01-26 | 46720 | 46.72 | 7.42 | 7.54 | 160 | 33 | 368 | 48 | 310 | 36 | NA | 700 | 0.3 | 24.7 | 1700000
2023-01-27 | 45660 | 45.66 | 7.36 | 7.61 | 155 | 31 | 364 | 48 | 319 | 38 | NA | 800 | 0.2 | 23.9 | 1300000
2023-01-28 | 45530 | 45.53 | 7.34 | 7.59 | 160 | 33 | 356 | 44 | 328 | 39 | NA | 500 | 0.3 | 24.4 | 1100000
2023-01-29 | 45970 | 45.97 | 7.37 | 7.56 | 170 | 32 | 360 | 48 | 323 | 37 | NA | 600 | 0.3 | 25.5 | 1200000
2023-01-30 | 42150 | 42.15 | 7.32 | 7.6 | 165 | 31 | 352 | 44 | 326 | 36 | NA | 800 | 0.3 | 24.1 | 1400000
2023-01-31 | 41310 | 41.31 | 7.47 | 7.57 | 155 | 32 | 356 | 48 | 318 | 35 | NA | 700 | 0.2 | 24.3 | 1300000
Average | 44635.8065 | 44.6358 | 7.4165 | 7.5377 | 161.2903 | 28.2258 | 364.3871 | 45.2903 | 331.0645 | 38.7742 | NA | 638.7097 | 0.26452 | 24.6968 | 1348387.0968
1383.71
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 36810 | 36.81 | 7.32 | 7.46 | 155 | 21 | 344 | 36 | 295 | 30 |  | 400 | 0.2 | 23.6 | 1100000
Max | 52110 | 52.11 | 7.49 | 7.64 | 170 | 33 | 388 | 52 | 382 | 52 |  | 800 | 0.3 | 25.5 | 1700000

## Kodra
kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-01-01 | 27920 | 27.92 | 7.22 | 7.48 | 135 | 13 | 316 | 44 | 265 | 24 | NA | 500 | 0.5 | 23.75 | 1400000
2023-01-02 | 27470 | 27.47 | 7.25 | 7.52 | 140 | 14 | 324 | 40 | 276 | 21 | NA | 600 | 0.4 | 23.92 | 1300000
2023-01-03 | 26990 | 26.99 | 7.18 | 7.55 | 150 | 16 | 332 | 44 | 284 | 23 | NA | 400 | 0.5 | 22.86 | 1700000
2023-01-04 | 26160 | 26.16 | 7.24 | 7.41 | 145 | 13 | 320 | 36 | 268 | 21 | NA | 500 | 0.4 | 24.25 | 1400000
2023-01-05 | 25210 | 25.21 | 7.19 | 7.56 | 140 | 12 | 312 | 40 | 282 | 23 | NA | 700 | 0.5 | 24.36 | 1300000
2023-01-06 | 26620 | 26.62 | 7.23 | 7.47 | 150 | 13 | 324 | 40 | 280 | 21 | NA | 400 | 0.4 | 24.09 | 1700000
2023-01-07 | 27200 | 27.2 | 7.16 | 7.54 | 130 | 14 | 312 | 36 | 268 | 22 | NA | 800 | 0.5 | 24.26 | 1400000
2023-01-08 | 29620 | 29.62 | 7.19 | 7.52 | 135 | 13 | 308 | 40 | 297 | 23 | NA | 500 | 0.4 | 24.92 | 1300000
2023-01-09 | 26320 | 26.32 | 7.18 | 7.51 | 145 | 15 | 324 | 44 | 280 | 22 | NA | 600 | 0.5 | 23.53 | 1700000
2023-01-10 | 27760 | 27.76 | 7.22 | 7.44 | 135 | 14 | 316 | 40 | 274 | 18 | NA | 400 | 0.5 | 24.13 | 1300000
2023-01-11 | 27480 | 27.48 | 7.24 | 7.55 | 130 | 13 | 312 | 36 | 297 | 23 | NA | 500 | 0.4 | 24.17 | 1400000
2023-01-12 | 26040 | 26.04 | 7.21 | 7.52 | 140 | 14 | 324 | 40 | 280 | 22 | NA | 700 | 0.5 | 24.36 | 1700000
2023-01-13 | 27470 | 27.47 | 7.17 | 7.46 | 145 | 15 | 332 | 44 | 268 | 21 | NA | 600 | 0.5 | 24.21 | 1300000
2023-01-14 | 30860 | 30.86 | 7.28 | 7.51 | 135 | 12 | 320 | 32 | 278 | 24 | NA | 400 | 0.4 | 23.88 | 1100000
2023-01-15 | 31610 | 31.61 | 7.22 | 7.48 | 150 | 13 | 308 | 40 | 265 | 22 | NA | 500 | 0.4 | 23.46 | 1400000
2023-01-16 | 30580 | 30.58 | 7.26 | 7.56 | 155 | 12 | 312 | 36 | 282 | 23 | NA | 600 | 0.5 | 24.28 | 1700000
2023-01-17 | 29680 | 29.68 | 7.29 | 7.44 | 145 | 14 | 316 | 40 | 271 | 19 | NA | 500 | 0.4 | 23.55 | 1300000
2023-01-18 | 30150 | 30.15 | 7.23 | 7.47 | 140 | 13 | 304 | 36 | 263 | 21 | NA | 700 | 0.4 | 23.96 | 1400000
2023-01-19 | 29160 | 29.16 | 7.2 | 7.51 | 135 | 15 | 320 | 40 | 270 | 19 | NA | 600 | 0.5 | 24.51 | 1100000
1900-01-19 | 30830 | 30.83 | 7.24 | 7.49 | 150 | 14 | 328 | 44 | 283 | 22 | NA | 500 | 0.5 | 23.65 | 1300000
2023-01-21 | 31150 | 31.15 | 7.18 | 7.41 | 155 | 15 | 324 | 40 | 279 | 19 | NA | 700 | 0.5 | 24.35 | 1700000
2023-01-22 | 31040 | 31.04 | 7.22 | 7.5 | 145 | 13 | 312 | 36 | 268 | 23 | NA | 600 | 0.4 | 23.65 | 1400000
2023-01-23 | 30290 | 30.29 | 7.28 | 7.58 | 140 | 12 | 304 | 36 | 277 | 22 | NA | 500 | 0.5 | 24.11 | 1300000
2023-01-24 | 30510 | 30.51 | 7.08 | 7.41 | 150 | 14 | 320 | 40 | 261 | 19 | NA | 400 | 0.4 | 23.61 | 1700000
2023-01-25 | 30070 | 30.07 | 7.16 | 7.53 | 155 | 15 | 316 | 44 | 273 | 20 | NA | 600 | 0.5 | 23.48 | 1400000
2023-01-26 | 27900 | 27.9 | 7.26 | 7.48 | 150 | 16 | 324 | 40 | 281 | 19 | NA | 500 | 0.4 | 24.35 | 1300000
2023-01-27 | 32970 | 32.97 | 7.19 | 7.54 | 140 | 13 | 308 | 36 | 267 | 21 | NA | 700 | 0.4 | 23.38 | 1100000
2023-01-28 | 29810 | 29.81 | 7.3 | 7.61 | 145 | 14 | 312 | 40 | 284 | 20 | NA | 500 | 0.5 | 24.18 | 1400000
2023-01-29 | 28880 | 28.88 | 7.27 | 7.57 | 150 | 13 | 320 | 44 | 272 | 21 | NA | 400 | 0.5 | 24.37 | 1700000
2023-01-30 | 28260 | 28.26 | 7.25 | 7.55 | 155 | 14 | 328 | 40 | 279 | 17 | NA | 600 | 0.4 | 24.48 | 1400000
2023-01-31 | 28140 | 28.14 | 7.18 | 7.5 | 145 | 11 | 316 | 36 | 283 | 20 | NA | 500 | 0.5 | 24.61 | 1300000
Average | 28843.5484 | 28.8435 | 7.2184 | 7.5055 | 143.871 | 13.6129 | 317.6774 | 39.4839 | 275.9677 | 21.129 | NA | 548.3871 | 0.45484 | 24.0216 | 1416129.0323
894.15
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 25210 | 25.21 | 7.08 | 7.41 | 130 | 11 | 304 | 32 | 261 | 17 |  | 400 | 0.4 | 22.86 | 1100000
Max | 32970 | 32.97 | 7.3 | 7.61 | 155 | 16 | 332 | 44 | 297 | 24 |  | 800 | 0.5 | 24.92 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-01-01 | 12820 | 12.82 | 7.31 | 7.42 | 145 | 18 | 304 | 40 | 285 | 22 | NA | 500 | 0.4 | 24.33 | 1400000
2023-01-02 | 12770 | 12.77 | 7.26 | 7.49 | 135 | 15 | 312 | 48 | 277 | 28 | NA | 700 | 0.3 | 23.17 | 1700000
2023-01-03 | 12280 | 12.28 | 7.22 | 7.35 | 150 | 17 | 300 | 40 | 274 | 26 | NA | 400 | 0.4 | 24.67 | 1300000
2023-01-04 | 12170 | 12.17 | 7.31 | 7.43 | 140 | 18 | 296 | 48 | 266 | 22 | NA | 500 | 0.3 | 23.97 | 1400000
2023-01-05 | 12470 | 12.47 | 7.2 | 7.33 | 145 | 15 | 308 | 40 | 270 | 28 | NA | 600 | 0.4 | 22.83 | 1700000
2023-01-06 | 11620 | 11.62 | 7.29 | 7.37 | 150 | 17 | 312 | 40 | 267 | 26 | NA | 500 | 0.3 | 25.13 | 1400000
2023-01-07 | 12610 | 12.61 | 7.32 | 7.38 | 140 | 18 | 304 | 48 | 278 | 27 | NA | 700 | 0.4 | 24.28 | 1200000
2023-01-08 | 13090 | 13.09 | 7.3 | 7.41 | 135 | 14 | 289 | 40 | 288 | 28 | NA | 400 | 0.3 | 23.39 | 1300000
2023-01-09 | 12100 | 12.1 | 7.28 | 7.39 | 145 | 19 | 300 | 44 | 265 | 24 | NA | 600 | 0.3 | 23.17 | 1700000
2023-01-10 | 12070 | 12.07 | 7.32 | 7.42 | 150 | 18 | 310 | 40 | 284 | 23 | NA | 700 | 0.4 | 24.28 | 1700000
2023-01-11 | 12840 | 12.84 | 7.3 | 7.34 | 145 | 16 | 308 | 48 | 294 | 22 | NA | 400 | 0.3 | 23.98 | 1400000
2023-01-12 | 11090 | 11.32 | 7.24 | 7.37 | 130 | 13 | 303 | 40 | 242 | 21 | NA | 500 | 0.3 | 23.85 | 1300000
2023-01-13 | 11620 | 11.62 | 7.36 | 7.41 | 145 | 17 | 320 | 48 | 273 | 23 | NA | 400 | 0.4 | 24.32 | 1300000
2023-01-14 | 12730 | 12.73 | 7.3 | 7.38 | 140 | 16 | 312 | 40 | 270 | 28 | NA | 700 | 0.3 | 22.93 | 1700000
2023-01-15 | 13330 | 13.33 | 7.34 | 7.44 | 150 | 15 | 304 | 48 | 284 | 22 | NA | 400 | 0.3 | 23.97 | 1200000
2023-01-16 | 12500 | 12.5 | 7.3 | 7.35 | 145 | 17 | 310 | 40 | 295 | 27 | NA | 600 | 0.4 | 24.74 | 1400000
2023-01-17 | 13280 | 13.28 | 7.32 | 7.46 | 140 | 16 | 287 | 44 | 274 | 26 | NA | 500 | 0.3 | 23.85 | 1400000
2023-01-18 | 13550 | 13.55 | 7.29 | 7.39 | 145 | 17 | 316 | 40 | 280 | 22 | NA | 700 | 0.4 | 22.35 | 1300000
2023-01-19 | 13790 | 13.79 | 7.26 | 7.36 | 150 | 16 | 302 | 48 | 286 | 29 | NA | 600 | 0.3 | 24.16 | 1700000
1900-01-19 | 13720 | 13.72 | 7.24 | 7.38 | 130 | 14 | 306 | 40 | 280 | 24 | NA | 500 | 0.3 | 23.72 | 1300000
2023-01-21 | 13310 | 13.31 | 7.36 | 7.43 | 145 | 16 | 312 | 44 | 277 | 27 | NA | 400 | 0.4 | 24.17 | 1400000
2023-01-22 | 13200 | 13.2 | 7.32 | 7.4 | 140 | 18 | 304 | 48 | 285 | 26 | NA | 500 | 0.3 | 24.57 | 1300000
2023-01-23 | 13250 | 13.25 | 7.34 | 7.43 | 135 | 16 | 310 | 44 | 265 | 24 | NA | 700 | 0.3 | 23.63 | 1400000
2023-01-24 | 13650 | 13.65 | 7.31 | 7.46 | 140 | 17 | 298 | 40 | 292 | 22 | NA | 600 | 0.3 | 24.1 | 1300000
2023-01-25 | 13010 | 13.01 | 7.28 | 7.39 | 135 | 18 | 310 | 48 | 286 | 26 | NA | 500 | 0.4 | 23.6 | 1400000
2023-01-26 | 13820 | 13.89 | 7.23 | 7.36 | 140 | 16 | 304 | 44 | 278 | 24 | NA | 600 | 0.3 | 23.4 | 1400000
2023-01-27 | 13180 | 13.18 | 7.34 | 7.43 | 145 | 17 | 312 | 48 | 273 | 27 | NA | 400 | 0.3 | 23.58 | 1300000
2023-01-28 | 12600 | 12.6 | 7.28 | 7.46 | 130 | 15 | 309 | 44 | 284 | 26 | NA | 500 | 0.4 | 24.33 | 1400000
2023-01-29 | 12790 | 12.79 | 7.24 | 7.38 | 145 | 16 | 324 | 40 | 295 | 24 | NA | 600 | 0.3 | 23.7 | 1400000
2023-01-30 | 12480 | 12.48 | 7.32 | 7.43 | 150 | 17 | 306 | 48 | 287 | 28 | NA | 500 | 0.4 | 23.13 | 1300000
2023-01-31 | 12750 | 12.75 | 7.26 | 7.38 | 135 | 15 | 309 | 44 | 292 | 27 | NA | 400 | 0.4 | 22.38 | 1200000
Average | 12790 | 12.7997 | 7.2916 | 7.4006 | 141.7742 | 16.3548 | 306.4839 | 43.7419 | 278.9032 | 25.129 | NA | 535.4839 | 0.34194 | 23.7961 | 1406451.6129
396.79
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11090 | 11.32 | 7.2 | 7.33 | 130 | 13 | 287 | 40 | 242 | 21 |  | 400 | 0.3 | 22.35 | 1200000
Max | 13820 | 13.89 | 7.36 | 7.49 | 150 | 19 | 324 | 48 | 295 | 29 |  | 700 | 0.4 | 25.13 | 1700000