## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-07-01 | 59860 | 59.86 | 7.4 | 7.68 | 145 | 15 | 312 | 36 | 226 | 24 | NA | 600 | 0.2 | 23.69 | 1400000
2023-07-02 | 60630 | 60.63 | 7.38 | 7.72 | 135 | 14 | 324 | 44 | 263 | 23 | NA | 500 | 0.3 | 23.39 | 1700000
2023-07-03 | 58400 | 58.4 | 7.36 | 7.78 | 145 | 16 | 312 | 40 | 248 | 24 | NA | 700 | 0.2 | 24.43 | 1300000
2023-07-04 | 60150 | 60.15 | 7.44 | 7.76 | 150 | 18 | 328 | 44 | 252 | 23 | NA | 400 | 0.3 | 23.5 | 1400000
2023-07-05 | 62750 | 62.75 | 7.28 | 7.67 | 130 | 17 | 316 | 40 | 256 | 25 | NA | 600 | 0.2 | 24.37 | 1700000
2023-07-06 | 60820 | 60.82 | 7.36 | 7.74 | 140 | 17 | 304 | 40 | 248 | 24 | NA | 400 | 0.2 | 24.82 | 1300000
2023-07-07 | 61390 | 61.39 | 7.48 | 7.76 | 135 | 16 | 324 | 44 | 258 | 25 | NA | 700 | 0.3 | 23.57 | 1400000
2023-07-08 | 58550 | 58.55 | 7.31 | 7.66 | 125 | 16 | 332 | 44 | 266 | 23 | NA | 500 | 0.2 | 23.64 | 1700000
2023-07-09 | 61600 | 61.6 | 7.26 | 7.71 | 130 | 15 | 304 | 40 | 257 | 25 | NA | 400 | 0.3 | 24.79 | 1100000
2023-07-10 | 57350 | 57.35 | 7.34 | 7.67 | 140 | 17 | 316 | 44 | 246 | 24 | NA | 600 | 0.3 | 24.23 | 1400000
2023-07-11 | 56870 | 56.87 | 7.28 | 7.71 | 130 | 16 | 320 | 40 | 253 | 22 | NA | 500 | 0.2 | 23.44 | 1100000
2023-07-12 | 51530 | 51.53 | 7.36 | 7.78 | 145 | 17 | 304 | 44 | 244 | 24 | NA | 400 | 0.3 | 24.04 | 1400000
2023-07-13 | 57950 | 57.95 | 7.38 | 7.74 | 140 | 15 | 308 | 36 | 256 | 23 | NA | 700 | 0.2 | 23.22 | 1300000
2023-07-14 | 62850 | 62.85 | 7.32 | 7.67 | 150 | 13 | 324 | 40 | 266 | 22 | NA | 400 | 0.2 | 23.11 | 1300000
2023-07-15 | 60140 | 60.14 | 7.41 | 7.76 | 135 | 16 | 300 | 36 | 268 | 25 | NA | 500 | 0.3 | 24.16 | 1700000
2023-07-16 | 60580 | 60.58 | 7.32 | 7.69 | 145 | 17 | 328 | 44 | 224 | 28 | NA | 600 | 0.3 | 23.54 | 1400000
2023-07-17 | 60920 | 60.92 | 7.27 | 7.72 | 135 | 16 | 280 | 40 | 246 | 26 | NA | 700 | 0.3 | 24.23 | 1300000
2023-07-18 | 61630 | 61.63 | 7.38 | 7.68 | 125 | 15 | 288 | 44 | 278 | 24 | NA | 400 | 0.3 | 24.62 | 1700000
2023-07-19 | 61350 | 61.35 | 7.27 | 7.76 | 140 | 16 | 320 | 40 | 296 | 27 | NA | 600 | 0.3 | 24.37 | 1300000
2023-07-20 | 59470 | 59.47 | 7.41 | 7.74 | 130 | 15 | 332 | 44 | 272 | 25 | NA | 400 | 0.2 | 23.22 | 1400000
2023-07-21 | 58630 | 58.63 | 7.36 | 7.64 | 145 | 17 | 304 | 40 | 266 | 23 | NA | 700 | 0.3 | 23.64 | 1700000
2023-07-22 | 53400 | 53.4 | 7.32 | 7.72 | 125 | 15 | 324 | 40 | 268 | 24 | NA | 500 | 0.2 | 23.54 | 1300000
2023-07-23 | 62900 | 62.9 | 7.41 | 7.78 | 140 | 17 | 328 | 44 | 272 | 22 | NA | 400 | 0.3 | 24.25 | 1100000
2023-07-24 | 60660 | 60.66 | 7.38 | 7.71 | 150 | 16 | 316 | 44 | 278 | 26 | NA | 600 | 0.3 | 23.98 | 1400000
2023-07-25 | 59380 | 59.38 | 7.44 | 7.78 | 130 | 17 | 324 | 40 | 268 | 25 | NA | 500 | 0.2 | 24.23 | 1700000
2023-07-26 | 60220 | 60.22 | 7.38 | 7.75 | 135 | 15 | 332 | 44 | 278 | 27 | NA | 700 | 0.3 | 23.75 | 1300000
2023-07-27 | 60320 | 60.32 | 7.42 | 7.76 | 125 | 16 | 304 | 36 | 271 | 24 | NA | 400 | 0.2 | 23.08 | 1400000
2023-07-28 | 60950 | 60.95 | 7.28 | 7.66 | 130 | 14 | 300 | 40 | 256 | 23 | NA | 600 | 0.3 | 24.5 | 1700000
2023-07-29 | 62460 | 62.46 | 7.36 | 7.75 | 150 | 16 | 308 | 40 | 267 | 24 | NA | 500 | 0.3 | 23.28 | 1400000
2023-07-30 | 56100 | 56.1 | 7.42 | 7.67 | 125 | 14 | 304 | 36 | 274 | 22 | NA | 700 | 0.2 | 23.64 | 1300000
2023-07-31 | 59020 | 59.02 | 7.28 | 7.71 | 140 | 15 | 320 | 44 | 273 | 25 | NA | 600 | 0.3 | 24.68 | 1700000
Average | 59639.6774 | 59.6397 | 7.3568 | 7.7203 | 136.9355 | 15.7742 | 314.1935 | 41.0323 | 261.0968 | 24.2258 | NA | 541.9355 | 0.25806 | 23.9016 | 1429032.2581
1848.83
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 51530 | 51.53 | 7.26 | 7.64 | 125 | 13 | 280 | 36 | 224 | 22 |  | 400 | 0.2 | 23.08 | 1100000
Max | 62900 | 62.9 | 7.48 | 7.78 | 150 | 18 | 332 | 44 | 296 | 28 |  | 700 | 0.3 | 24.82 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-07-01 | 38580 | 38.58 | 7.46 | 7.54 | 155 | 26 | 360 | 40 | 320 | 33 | NA | 800 | 0.3 | 24.8 | 1400000
2023-07-02 | 36730 | 36.73 | 7.51 | 7.57 | 160 | 26 | 356 | 44 | 336 | 35 | NA | 600 | 0.3 | 23.7 | 1700000
2023-07-03 | 40630 | 40.63 | 7.42 | 7.53 | 165 | 24 | 348 | 40 | 342 | 31 | NA | 700 | 0.2 | 24.6 | 1400000
2023-07-04 | 40630 | 40.32 | 7.35 | 7.47 | 160 | 23 | 344 | 40 | 338 | 32 | NA | 600 | 0.3 | 25.3 | 1200000
2023-07-05 | 35930 | 35.93 | 7.42 | 7.48 | 155 | 26 | 360 | 36 | 329 | 30 | NA | 500 | 0.2 | 24.7 | 1300000
2023-07-06 | 36840 | 36.84 | 7.33 | 7.44 | 160 | 25 | 356 | 40 | 336 | 31 | NA | 400 | 0.3 | 23.8 | 1400000
2023-07-07 | 38430 | 38.43 | 7.42 | 7.51 | 155 | 26 | 360 | 40 | 322 | 32 | NA | 700 | 0.3 | 25.6 | 1700000
2023-07-08 | 37770 | 37.77 | 7.37 | 7.46 | 145 | 24 | 344 | 36 | 332 | 34 | NA | 500 | 0.2 | 24.6 | 1400000
2023-07-09 | 39670 | 39.67 | 7.43 | 7.56 | 155 | 25 | 352 | 40 | 341 | 35 | NA | 800 | 0.3 | 25.3 | 1700000
2023-07-10 | 42940 | 42.94 | 7.46 | 7.57 | 160 | 27 | 356 | 40 | 331 | 30 | NA | 600 | 0.2 | 23.8 | 1300000
2023-07-11 | 36920 | 36.92 | 7.56 | 7.62 | 155 | 24 | 352 | 36 | 327 | 31 | NA | 500 | 0.3 | 24.6 | 1200000
2023-07-12 | 36760 | 36.76 | 7.63 | 7.67 | 150 | 25 | 360 | 40 | 319 | 33 | NA | 700 | 0.3 | 25.4 | 1400000
2023-07-13 | 39370 | 39.37 | 7.65 | 7.71 | 160 | 24 | 352 | 40 | 308 | 31 | NA | 800 | 0.2 | 24.3 | 1700000
2023-07-14 | 39990 | 39.99 | 7.58 | 7.64 | 155 | 27 | 360 | 36 | 313 | 32 | NA | 600 | 0.3 | 23.8 | 1400000
2023-07-15 | 36920 | 36.92 | 7.56 | 7.67 | 160 | 26 | 348 | 40 | 320 | 35 | NA | 400 | 0.3 | 25.5 | 1200000
2023-07-16 | 38040 | 38.04 | 7.59 | 7.62 | 165 | 25 | 356 | 44 | 297 | 34 | NA | 700 | 0.2 | 23.6 | 1400000
2023-07-17 | 37630 | 37.63 | 7.63 | 7.68 | 155 | 27 | 360 | 44 | 308 | 36 | NA | 600 | 0.3 | 24.5 | 1300000
2023-07-18 | 36610 | 36.61 | 7.61 | 7.66 | 160 | 28 | 352 | 40 | 312 | 38 | NA | 500 | 0.3 | 24.8 | 1100000
2023-07-19 | 40810 | 40.81 | 7.58 | 7.63 | 155 | 22 | 356 | 40 | 293 | 36 | NA | 700 | 0.2 | 23.7 | 1400000
2023-07-20 | 36560 | 36.56 | 7.61 | 7.64 | 160 | 25 | 348 | 36 | 289 | 28 | NA | 500 | 0.3 | 25.6 | 1300000
2023-07-21 | 38520 | 38.52 | 7.57 | 7.62 | 165 | 27 | 356 | 40 | 296 | 28 | NA | 800 | 0.2 | 24.6 | 1700000
2023-07-22 | 35830 | 35.83 | 7.62 | 7.65 | 155 | 22 | 360 | 36 | 314 | 29 | NA | 500 | 0.3 | 25.3 | 1200000
2023-07-23 | 37710 | 37.71 | 7.65 | 7.69 | 160 | 25 | 356 | 40 | 296 | 31 | NA | 700 | 0.2 | 23.8 | 1400000
2023-07-24 | 34790 | 34.79 | 7.58 | 7.64 | 150 | 26 | 360 | 40 | 310 | 33 | NA | 600 | 0.3 | 24.7 | 1200000
2023-07-25 | 36210 | 36.21 | 7.65 | 7.68 | 160 | 24 | 352 | 36 | 306 | 34 | NA | 400 | 0.3 | 23.5 | 1300000
2023-07-26 | 38340 | 38.34 | 7.63 | 7.66 | 165 | 21 | 360 | 36 | 313 | 29 | NA | 500 | 0.2 | 25.6 | 1400000
2023-07-27 | 36910 | 36.91 | 7.62 | 7.64 | 160 | 20 | 364 | 40 | 298 | 32 | NA | 400 | 0.3 | 25.2 | 1100000
2023-07-28 | 36780 | 36.78 | 7.65 | 7.68 | 155 | 22 | 356 | 44 | 311 | 34 | NA | 600 | 0.3 | 23.7 | 1400000
2023-07-29 | 35790 | 35.79 | 7.59 | 7.63 | 145 | 20 | 352 | 40 | 296 | 33 | NA | 800 | 0.2 | 24.6 | 1700000
2023-07-30 | 35880 | 35.88 | 7.63 | 7.65 | 155 | 21 | 360 | 44 | 319 | 31 | NA | 500 | 0.3 | 24.9 | 1300000
2023-07-31 | 42110 | 42.11 | 7.65 | 7.67 | 160 | 19 | 356 | 40 | 320 | 28 | NA | 700 | 0.3 | 25.4 | 1200000
Average | 37955.8065 | 37.9458 | 7.5487 | 7.609 | 157.2581 | 24.2581 | 355.2258 | 39.6129 | 315.871 | 32.2258 | NA | 603.2258 | 0.26452 | 24.6226 | 1380645.1613
1176.32
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 34790 | 34.79 | 7.33 | 7.44 | 145 | 19 | 344 | 36 | 289 | 28 |  | 400 | 0.2 | 23.5 | 1100000
Max | 42940 | 42.94 | 7.65 | 7.71 | 165 | 28 | 364 | 44 | 342 | 38 |  | 800 | 0.3 | 25.6 | 1700000

## Kodra
kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-07-01 | 36870 | 36.87 | 7.28 | 7.48 | 140 | 15 | 328 | 40 | 271 | 21 | NA | 400 | 0.3 | 24.11 | 1200000
2023-07-02 | 31850 | 31.85 | 7.23 | 7.46 | 130 | 11 | 292 | 36 | 282 | 22 | NA | 600 | 0.2 | 24.06 | 1400000
2023-07-03 | 30210 | 30.21 | 7.19 | 7.52 | 140 | 13 | 304 | 40 | 268 | 24 | NA | 500 | 0.2 | 23.56 | 1300000
2023-07-04 | 35970 | 35.97 | 7.26 | 7.47 | 135 | 15 | 316 | 44 | 276 | 26 | NA | 600 | 0.3 | 24.26 | 1200000
2023-07-05 | 31320 | 31.32 | 7.29 | 7.44 | 145 | 13 | 304 | 40 | 263 | 24 | NA | 400 | 0.3 | 23.51 | 1400000
2023-07-06 | 28520 | 28.52 | 7.24 | 7.45 | 150 | 12 | 308 | 36 | 268 | 25 | NA | 700 | 0.3 | 23.77 | 1200000
2023-07-07 | 30290 | 30.29 | 7.31 | 7.48 | 135 | 14 | 316 | 40 | 274 | 26 | NA | 600 | 0.2 | 23.56 | 1300000
2023-07-08 | 29620 | 29.62 | 7.32 | 7.47 | 145 | 11 | 300 | 36 | 263 | 21 | NA | 700 | 0.3 | 23.08 | 1700000
2023-07-09 | 32390 | 32.39 | 7.27 | 7.49 | 130 | 13 | 324 | 40 | 282 | 22 | NA | 500 | 0.2 | 23.62 | 1400000
2023-07-10 | 33320 | 33.32 | 7.3 | 7.52 | 140 | 14 | 312 | 36 | 267 | 21 | NA | 600 | 0.2 | 24.53 | 1700000
2023-07-11 | 29970 | 29.97 | 7.29 | 7.44 | 135 | 15 | 332 | 40 | 260 | 20 | NA | 500 | 0.3 | 23.51 | 1200000
2023-07-12 | 30540 | 30.54 | 7.24 | 7.48 | 130 | 14 | 320 | 44 | 279 | 22 | NA | 400 | 0.2 | 23.7 | 1300000
2023-07-13 | 27850 | 27.85 | 7.26 | 7.5 | 135 | 12 | 304 | 36 | 268 | 20 | NA | 700 | 0.2 | 24.4 | 1200000
2023-07-14 | 29170 | 29.17 | 7.34 | 7.53 | 140 | 13 | 312 | 40 | 275 | 22 | NA | 500 | 0.3 | 24.96 | 1300000
2023-07-15 | 30750 | 30.75 | 7.32 | 7.55 | 150 | 15 | 308 | 44 | 266 | 20 | NA | 700 | 0.2 | 23.61 | 1400000
2023-07-16 | 30790 | 30.79 | 7.3 | 7.52 | 145 | 16 | 296 | 40 | 269 | 21 | NA | 400 | 0.2 | 23.08 | 1200000
2023-07-17 | 30110 | 30.11 | 7.32 | 7.48 | 135 | 11 | 312 | 36 | 270 | 22 | NA | 700 | 0.3 | 23.64 | 1300000
2023-07-18 | 28530 | 28.53 | 7.22 | 7.51 | 130 | 12 | 304 | 40 | 265 | 20 | NA | 600 | 0.3 | 24.11 | 1400000
2023-07-19 | 31450 | 31.45 | 7.28 | 7.49 | 140 | 13 | 320 | 36 | 272 | 21 | NA | 400 | 0.2 | 24.47 | 1100000
2023-07-20 | 30320 | 30.32 | 7.26 | 7.5 | 150 | 15 | 328 | 40 | 287 | 23 | NA | 500 | 0.3 | 24.18 | 1200000
2023-07-21 | 33100 | 33.1 | 7.29 | 7.53 | 140 | 12 | 316 | 36 | 282 | 22 | NA | 400 | 0.2 | 24.32 | 1400000
2023-07-22 | 33740 | 33.74 | 7.16 | 7.54 | 135 | 11 | 324 | 32 | 296 | 23 | NA | 600 | 0.2 | 23.64 | 1300000
2023-07-23 | 35900 | 35.9 | 7.21 | 7.46 | 145 | 13 | 300 | 36 | 264 | 22 | NA | 500 | 0.3 | 23.52 | 1100000
2023-07-24 | 30870 | 30.87 | 7.24 | 7.48 | 135 | 12 | 316 | 40 | 269 | 21 | NA | 700 | 0.3 | 23.32 | 1700000
2023-07-25 | 32950 | 32.95 | 7.19 | 7.44 | 130 | 14 | 312 | 36 | 283 | 22 | NA | 600 | 0.3 | 24.11 | 1300000
2023-07-26 | 32640 | 32.64 | 7.26 | 7.54 | 135 | 13 | 328 | 40 | 278 | 23 | NA | 700 | 0.2 | 24.87 | 1400000
2023-07-27 | 27700 | 27.7 | 7.16 | 7.55 | 140 | 12 | 308 | 36 | 271 | 21 | NA | 400 | 0.2 | 24.94 | 1200000
2023-07-28 | 28440 | 28.44 | 7.22 | 7.53 | 130 | 10 | 316 | 32 | 283 | 24 | NA | 500 | 0.2 | 22.6 | 1400000
2023-07-29 | 28310 | 28.31 | 7.3 | 7.5 | 145 | 11 | 320 | 36 | 276 | 23 | NA | 700 | 0.2 | 22.72 | 1300000
2023-07-30 | 29850 | 29.85 | 7.27 | 7.54 | 140 | 10 | 296 | 32 | 267 | 21 | NA | 400 | 0.3 | 24.43 | 1100000
2023-07-31 | 29030 | 29.03 | 7.19 | 7.48 | 150 | 12 | 316 | 36 | 278 | 22 | NA | 600 | 0.3 | 24.42 | 1700000
Average | 31044.1935 | 31.0442 | 7.2584 | 7.4958 | 138.871 | 12.8065 | 312.6452 | 37.9355 | 273.2903 | 22.1613 | NA | 551.6129 | 0.24839 | 23.8906 | 1332258.0645
962.37
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 27700 | 27.7 | 7.16 | 7.44 | 130 | 10 | 292 | 32 | 260 | 20 |  | 400 | 0.2 | 22.6 | 1100000
Max | 36870 | 36.87 | 7.34 | 7.55 | 150 | 16 | 332 | 44 | 296 | 26 |  | 700 | 0.3 | 24.96 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-07-01 | 13490 | 13.49 | 7.41 | 7.5 | 135 | 18 | 310 | 48 | 293 | 26 | NA | 400 | 0.2 | 23.23 | 1300000
2023-07-02 | 12940 | 12.94 | 7.43 | 7.74 | 140 | 17 | 312 | 44 | 286 | 23 | NA | 300 | 0.3 | 23.51 | 1200000
2023-07-03 | 13150 | 13.15 | 7.46 | 7.8 | 145 | 16 | 300 | 48 | 280 | 24 | NA | 500 | 0.3 | 23.06 | 1400000
2023-07-04 | 14420 | 14.42 | 7.42 | 7.82 | 135 | 17 | 308 | 44 | 294 | 22 | NA | 400 | 0.2 | 22.49 | 1200000
2023-07-05 | 11400 | 11.4 | 7.4 | 7.81 | 145 | 18 | 310 | 48 | 289 | 25 | NA | 300 | 0.3 | 23.68 | 1500000
2023-07-06 | 12790 | 12.79 | 7.41 | 7.77 | 150 | 17 | 316 | 44 | 274 | 22 | NA | 500 | 0.3 | 23.67 | 1400000
2023-07-07 | 13820 | 13.82 | 7.43 | 7.74 | 140 | 18 | 306 | 48 | 296 | 25 | NA | 600 | 0.2 | 23.5 | 1300000
2023-07-08 | 13930 | 13.93 | 7.44 | 7.71 | 145 | 17 | 308 | 44 | 284 | 24 | NA | 400 | 0.3 | 23.1 | 1200000
2023-07-09 | 13250 | 13.25 | 7.42 | 7.65 | 135 | 18 | 300 | 48 | 278 | 23 | NA | 500 | 0.2 | 23.42 | 1400000
2023-07-10 | 14210 | 14.21 | 7.4 | 7.55 | 140 | 17 | 296 | 44 | 298 | 22 | NA | 600 | 0.3 | 23.2 | 1500000
2023-07-11 | 13390 | 13.39 | 7.43 | 7.68 | 150 | 18 | 308 | 48 | 276 | 23 | NA | 500 | 0.3 | 22.94 | 1300000
2023-07-12 | 13650 | 13.65 | 7.45 | 7.78 | 145 | 17 | 312 | 44 | 282 | 24 | NA | 400 | 0.2 | 23.18 | 1400000
2023-07-13 | 13850 | 13.85 | 7.48 | 7.76 | 135 | 16 | 320 | 48 | 292 | 23 | NA | 500 | 0.3 | 23.02 | 1200000
2023-07-14 | 14740 | 14.74 | 7.43 | 7.88 | 145 | 18 | 304 | 44 | 286 | 25 | NA | 600 | 0.3 | 23.81 | 1300000
2023-07-15 | 14660 | 14.66 | 7.41 | 7.84 | 140 | 19 | 308 | 48 | 275 | 26 | NA | 400 | 0.3 | 23.45 | 1400000
2023-07-16 | 14930 | 14.93 | 7.44 | 7.74 | 150 | 16 | 316 | 44 | 288 | 24 | NA | 500 | 0.2 | 23.09 | 1200000
2023-07-17 | 15130 | 15.13 | 7.38 | 7.65 | 145 | 17 | 320 | 48 | 275 | 23 | NA | 600 | 0.3 | 23.36 | 1500000
2023-07-18 | 13840 | 13.84 | 7.42 | 7.73 | 140 | 18 | 308 | 44 | 282 | 24 | NA | 400 | 0.3 | 22.92 | 1300000
2023-07-19 | 14960 | 14.96 | 7.46 | 7.85 | 130 | 16 | 300 | 48 | 270 | 25 | NA | 500 | 0.2 | 23.08 | 1200000
2023-07-20 | 14280 | 14.28 | 7.43 | 7.84 | 145 | 17 | 316 | 44 | 284 | 27 | NA | 600 | 0.3 | 23.46 | 1400000
2023-07-21 | 14110 | 14.11 | 7.45 | 7.8 | 140 | 16 | 300 | 48 | 294 | 26 | NA | 500 | 0.3 | 23.15 | 1300000
2023-07-22 | 12110 | 12.11 | 7.41 | 7.68 | 135 | 17 | 308 | 44 | 282 | 25 | NA | 400 | 0.2 | 22.85 | 1200000
2023-07-23 | 14610 | 14.61 | 7.37 | 7.65 | 145 | 16 | 312 | 48 | 291 | 22 | NA | 500 | 0.2 | 23.14 | 1500000
2023-07-24 | 13530 | 13.53 | 7.39 | 7.61 | 140 | 18 | 316 | 44 | 272 | 21 | NA | 600 | 0.3 | 22.92 | 1400000
2023-07-25 | 13230 | 13.23 | 7.42 | 7.7 | 135 | 16 | 300 | 48 | 284 | 23 | NA | 500 | 0.2 | 23.3 | 1300000
2023-07-26 | 13650 | 13.65 | 7.46 | 7.74 | 145 | 17 | 310 | 44 | 278 | 25 | NA | 600 | 0.3 | 23.14 | 1400000
2023-07-27 | 12750 | 12.75 | 7.42 | 7.81 | 150 | 18 | 304 | 48 | 272 | 22 | NA | 400 | 0.3 | 23 | 1200000
2023-07-28 | 13000 | 13 | 7.38 | 7.79 | 135 | 17 | 300 | 44 | 267 | 23 | NA | 500 | 0.2 | 23.46 | 1300000
2023-07-29 | 12990 | 12.99 | 7.44 | 7.59 | 145 | 16 | 312 | 48 | 275 | 24 | NA | 600 | 0.3 | 22.86 | 1500000
2023-07-30 | 14840 | 14.84 | 7.41 | 7.68 | 130 | 18 | 304 | 44 | 282 | 25 | NA | 400 | 0.3 | 23.28 | 1400000
2023-07-31 | 14080 | 14.08 | 7.47 | 7.7 | 140 | 16 | 300 | 48 | 274 | 24 | NA | 500 | 0.2 | 22.53 | 1300000
Average | 13733.2258 | 13.7332 | 7.4248 | 7.7287 | 141.129 | 17.0968 | 307.871 | 46.0645 | 282.3548 | 23.871 | NA | 483.871 | 0.26129 | 23.1871 | 1335483.871
425.73
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11400 | 11.4 | 7.37 | 7.5 | 130 | 16 | 296 | 44 | 267 | 21 |  | 300 | 0.2 | 22.49 | 1200000
Max | 15130 | 15.13 | 7.48 | 7.88 | 150 | 19 | 320 | 48 | 298 | 27 |  | 600 | 0.3 | 23.81 | 1500000