## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-07-01 | 58110 | 58.11 | 7.22 | 7.8 | 140 | 18 | 320 | 40 | 265 | 22 | NA | 700 | 0.3 | 24.97 | 1100000
2022-07-02 | 54760 | 54.76 | 7.11 | 7.68 | 145 | 16 | 336 | 44 | 255 | 24 | NA | 400 | 0.2 | 23.9 | 1400000
2022-07-03 | 61890 | 61.89 | 7.18 | 7.63 | 130 | 13 | 328 | 36 | 242 | 23 | NA | 600 | 0.3 | 21.86 | 1700000
2022-07-04 | 58860 | 58.86 | 7.24 | 7.78 | 145 | 15 | 312 | 40 | 267 | 26 | NA | 500 | 0.2 | 23.38 | 1300000
2022-07-05 | 61880 | 61.88 | 7.19 | 7.67 | 150 | 18 | 332 | 48 | 256 | 25 | NA | 700 | 0.3 | 24.56 | 1400000
2022-07-06 | 61910 | 61.91 | 7.21 | 7.79 | 140 | 14 | 312 | 36 | 248 | 23 | NA | 400 | 0.3 | 22.5 | 1700000
2022-07-07 | 63320 | 63.32 | 7.26 | 7.61 | 135 | 16 | 328 | 44 | 263 | 26 | NA | 500 | 0.2 | 23.56 | 1400000
2022-07-08 | 63620 | 63.62 | 7.18 | 7.67 | 140 | 17 | 316 | 40 | 272 | 24 | NA | 700 | 0.3 | 21.72 | 1300000
2022-07-09 | 60990 | 60.99 | 7.21 | 7.76 | 130 | 12 | 320 | 36 | 261 | 27 | NA | 600 | 0.2 | 24.44 | 1100000
2022-07-10 | 67630 | 67.63 | 7.23 | 7.63 | 140 | 13 | 324 | 44 | 285 | 28 | NA | 400 | 0.3 | 24.02 | 1300000
2022-07-11 | 62870 | 62.87 | 7.29 | 7.62 | 135 | 15 | 312 | 40 | 266 | 24 | NA | 500 | 0.2 | 22.66 | 1700000
2022-07-12 | 65840 | 65.84 | 7.12 | 7.68 | 140 | 15 | 304 | 36 | 272 | 26 | NA | 700 | 0.2 | 23.49 | 1400000
2022-07-13 | 61950 | 61.95 | 7.17 | 7.71 | 150 | 17 | 328 | 44 | 265 | 23 | NA | 400 | 0.3 | 22.81 | 1100000
2022-07-14 | 60200 | 60.2 | 7.21 | 7.81 | 135 | 15 | 296 | 40 | 268 | 27 | NA | 600 | 0.2 | 24.29 | 1300000
2022-07-15 | 62640 | 62.64 | 7.23 | 7.78 | 125 | 12 | 324 | 44 | 276 | 25 | NA | 400 | 0.3 | 24.96 | 1400000
2022-07-16 | 64870 | 64.87 | 7.18 | 7.74 | 140 | 14 | 312 | 36 | 282 | 28 | NA | 400 | 0.2 | 23.52 | 1400000
2022-07-17 | 64150 | 64.15 | 7.21 | 7.66 | 150 | 16 | 328 | 40 | 240 | 18 | NA | 700 | 0.2 | 24.91 | 1300000
2022-07-18 | 63100 | 63.1 | 7.53 | 7.58 | 135 | 13 | 300 | 36 | 202 | 22 | NA | 500 | 0.3 | 23.63 | 1700000
2022-07-19 | 64200 | 64.2 | 7.32 | 7.72 | 145 | 15 | 308 | 44 | 238 | 26 | NA | 600 | 0.2 | 24.25 | 1100000
2022-07-20 | 65960 | 65.96 | 7.46 | 7.5 | 150 | 17 | 304 | 32 | 213 | 23 | NA | 400 | 0.3 | 23.79 | 1300000
2022-07-21 | 59360 | 59.36 | 7.31 | 7.65 | 130 | 14 | 328 | 40 | 262 | 25 | NA | 600 | 0.3 | 24.09 | 1700000
2022-07-22 | 61960 | 61.96 | 7.19 | 7.74 | 145 | 16 | 316 | 36 | 256 | 22 | NA | 500 | 0.2 | 23.04 | 1400000
2022-07-23 | 57180 | 57.18 | 7.24 | 7.69 | 145 | 15 | 312 | 44 | 268 | 26 | NA | 400 | 0.3 | 24.37 | 1100000
2022-07-24 | 58700 | 58.7 | 7.22 | 7.64 | 135 | 17 | 316 | 40 | 234 | 24 | NA | 700 | 0.2 | 21.92 | 1300000
2022-07-25 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | 23.42 | 1700000 | Numayadahi STP is in shutdown from 9:30 PM on 24.07.2022 due to damage in rising main from Ghagharnalla MPS to Numayadahi STP. Subsequently, Sasur Khaderi SPS is also stopped.
2022-07-26 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | - | Maintenance work for rising main from Ghagharnalla MPS to Numayadahi STP is in progress.
2022-07-27 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-07-28 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-07-29 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-07-30 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | 23.68 | 1400000
2022-07-31 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | 24.37 | 1100000
Average | 47933.871 | 47.9339 | 7.2379 | 7.6892 | 139.7917 | 15.125 | 317.3333 | 40 | 256.5 | 24.4583 | NA | 537.5 | 0.25 | 23.6337 | 1374074.0741
| 1485950 | 1485.95
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.11 | 7.5 | 125 | 12 | 296 | 32 | 202 | 18 |  | 400 | 0.2 | 21.72 | 1100000
Max | 67630 | 67.63 | 7.53 | 7.81 | 150 | 18 | 336 | 48 | 285 | 28 |  | 700 | 0.3 | 24.97 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-07-01 | 38780 | 38.78 | 7.4 | 7.92 | 156 | 28 | 356 | 48 | 338 | 47 | NA | 500 | 0.3 | 23.4 | 1400000
2022-07-02 | 36100 | 36.1 | 7.42 | 7.84 | 165 | 26 | 364 | 40 | 310 | 38 | NA | 600 | 0.2 | 23.7 | 1300000
2022-07-03 | 33420 | 33.42 | 7.49 | 7.65 | 153 | 24 | 352 | 36 | 323 | 39 | NA | 400 | 0.3 | 25.8 | 1200000
2022-07-04 | 37480 | 37.48 | 7.46 | 7.67 | 159 | 25 | 356 | 40 | 319 | 37 | NA | 700 | 0.2 | 24.2 | 1400000
2022-07-05 | 38600 | 38.6 | 7.38 | 7.6 | 156 | 28 | 360 | 44 | 305 | 43 | NA | 500 | 0.3 | 23.5 | 1300000
2022-07-06 | 37250 | 37.25 | 7.27 | 7.32 | 153 | 26 | 356 | 48 | 316 | 37 | NA | 600 | 0.3 | 21.8 | 1100000
2022-07-07 | 35660 | 35.66 | 7.6 | 7.71 | 156 | 24 | 348 | 40 | 318 | 37 | NA | 400 | 0.2 | 23.2 | 1200000
2022-07-08 | 35140 | 35.14 | 7.42 | 7.53 | 159 | 27 | 352 | 36 | 309 | 35 | NA | 500 | 0.2 | 24.6 | 1400000
2022-07-09 | 37530 | 37.53 | 7.4 | 7.49 | 156 | 25 | 356 | 40 | 301 | 31 | NA | 600 | 0.2 | 23.4 | 1300000
2022-07-10 | 38920 | 38.92 | 7.29 | 7.32 | 153 | 26 | 348 | 36 | 310 | 38 | NA | 500 | 0.3 | 23.8 | 1200000
2022-07-11 | 36060 | 36.06 | 7.56 | 7.65 | 159 | 25 | 352 | 40 | 321 | 33 | NA | 700 | 0.3 | 24.5 | 1300000
2022-07-12 | 35210 | 35.21 | 7.4 | 7.49 | 156 | 24 | 356 | 44 | 323 | 38 | NA | 800 | 0.2 | 23.2 | 1700000
2022-07-13 | 37410 | 37.41 | 7.6 | 7.69 | 153 | 26 | 352 | 48 | 298 | 35 | NA | 600 | 0.2 | 25.2 | 1400000
2022-07-14 | 39070 | 39.07 | 7.31 | 7.97 | 156 | 28 | 360 | 44 | 317 | 42 | NA | 700 | 0.3 | 23.4 | 1400000
2022-07-15 | 40190 | 40.19 | 7.36 | 7.82 | 159 | 29 | 364 | 48 | 330 | 45 | NA | 400 | 0.2 | 23.8 | 1200000
2022-07-16 | 43170 | 43.17 | 7.42 | 7.68 | 162 | 31 | 360 | 48 | 310 | 48 | NA | 500 | 0.3 | 24.5 | 1100000
2022-07-17 | 38010 | 38.01 | 7.6 | 7.71 | 156 | 27 | 356 | 40 | 305 | 40 | NA | 700 | 0.3 | 24.9 | 1300000
2022-07-18 | 36310 | 36.31 | 7.3 | 7.34 | 159 | 24 | 352 | 44 | 301 | 35 | NA | 600 | 0.2 | 22.1 | 1200000
2022-07-19 | 39160 | 39.16 | 7.29 | 7.37 | 153 | 26 | 348 | 40 | 303 | 36 | NA | 500 | 0.2 | 23.3 | 1300000
2022-07-20 | 41120 | 41.12 | 7.38 | 7.45 | 156 | 27 | 352 | 48 | 325 | 44 | NA | 500 | 0.3 | 21.1 | 1700000
2022-07-21 | 40070 | 40.07 | 7.31 | 7.53 | 159 | 26 | 360 | 44 | 322 | 38 | NA | 600 | 0.2 | 24.2 | 1200000
2022-07-22 | 44020 | 44.02 | 7.35 | 7.42 | 156 | 28 | 364 | 52 | 326 | 49 | NA | 500 | 0.3 | 24.6 | 1400000
2022-07-23 | 44030 | 44.03 | 7.56 | 7.87 | 159 | 29 | 352 | 48 | 300 | 42 | NA | 400 | 0.3 | 23.8 | 1300000
2022-07-24 | 42580 | 42.58 | 7.6 | 7.71 | 153 | 28 | 356 | 44 | 292 | 43 | NA | 700 | 0.2 | 25.5 | 1400000
2022-07-25 | 36150 | 36.15 | 7.26 | 7.38 | 153 | 25 | 348 | 40 | 293 | 37 | NA | 600 | 0.2 | 23.8 | 1300000
2022-07-26 | 35450 | 35.45 | 7.63 | 7.75 | 156 | 24 | 352 | 36 | 298 | 34 | NA | 500 | 0.3 | 24.2 | 1300000
2022-07-27 | 41690 | 41.69 | 7.61 | 7.73 | 153 | 27 | 356 | 40 | 310 | 39 | NA | 800 | 0.3 | 24.8 | 1700000
2022-07-28 | 42280 | 42.28 | 7.28 | 7.64 | 159 | 28 | 352 | 44 | 305 | 37 | NA | 700 | 0.2 | 25.2 | 1400000
2022-07-29 | 31290 | 31.29 | 7.22 | 7.51 | 156 | 24 | 360 | 36 | 298 | 35 | NA | 500 | 0.2 | 23.6 | 1200000 | Tapping point at Amitabh bachchan culvert is closed at 6:30 PM on 29.07.2022 due to increase in river level. Currently, raw sewage is being received from Allahpur drain and house connections.
2022-07-30 | 17010 | 17.01 | 7.45 | 7.15 | 153 | 20 | 352 | 44 | 300 | 32 | NA | 400 | 0.3 | 23.7 | 1100000
2022-07-31 | 14810 | 14.81 | 7.39 | 7.28 | 156 | 19 | 356 | 36 | 293 | 30 | NA | 500 | 0.3 | 24.4 | 1300000
Average | 36902.2581 | 36.9023 | 7.4197 | 7.5868 | 156.3871 | 25.9355 | 355.0968 | 42.4516 | 310.2903 | 38.5161 | NA | 564.5161 | 0.25161 | 23.9097 | 1322580.6452
| 1143970 | 1143.97
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 14810 | 14.81 | 7.22 | 7.15 | 153 | 19 | 348 | 36 | 292 | 30 |  | 400 | 0.2 | 21.1 | 1100000
Max | 44030 | 44.03 | 7.63 | 7.97 | 165 | 31 | 364 | 52 | 338 | 49 |  | 800 | 0.3 | 25.8 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-07-01 | 27890 | 27.89 | 7.18 | 7.49 | 146 | 13 | 320 | 40 | 265 | 19 | NA | 700 | 0.2 | 22.42 | 1400000
2022-07-02 | 27830 | 27.83 | 7.25 | 7.58 | 140 | 12 | 324 | 44 | 276 | 21 | NA | 500 | 0.3 | 22.9 | 1200000
2022-07-03 | 27340 | 27.34 | 7.34 | 7.69 | 136 | 13 | 312 | 36 | 268 | 18 | NA | 400 | 0.2 | 23.27 | 1600000
2022-07-04 | 28110 | 28.11 | 7.21 | 7.62 | 143 | 14 | 316 | 40 | 279 | 20 | NA | 600 | 0.3 | 23.58 | 1300000
2022-07-05 | 26720 | 26.72 | 7.28 | 7.55 | 146 | 13 | 308 | 36 | 270 | 17 | NA | 700 | 0.2 | 22.94 | 1400000
2022-07-06 | 27960 | 27.96 | 7.19 | 7.67 | 136 | 12 | 320 | 44 | 282 | 21 | NA | 500 | 0.3 | 24.08 | 1600000
2022-07-07 | 26030 | 26.03 | 7.32 | 7.59 | 140 | 13 | 308 | 40 | 268 | 18 | NA | 600 | 0.3 | 23.74 | 1400000
2022-07-08 | 26870 | 26.87 | 7.24 | 7.71 | 133 | 11 | 316 | 44 | 274 | 20 | NA | 700 | 0.2 | 24.21 | 1300000
2022-07-09 | 27250 | 27.25 | 7.18 | 7.64 | 143 | 13 | 324 | 40 | 285 | 22 | NA | 500 | 0.3 | 23.56 | 1600000
2022-07-10 | 28130 | 28.13 | 7.29 | 7.53 | 136 | 12 | 308 | 36 | 265 | 19 | NA | 400 | 0.2 | 24.13 | 1200000
2022-07-11 | 26360 | 26.36 | 7.36 | 7.59 | 140 | 13 | 320 | 44 | 278 | 21 | NA | 700 | 0.2 | 23.76 | 1400000
2022-07-12 | 25920 | 25.92 | 7.21 | 7.69 | 133 | 12 | 312 | 40 | 269 | 20 | NA | 600 | 0.3 | 23.48 | 1300000
2022-07-13 | 26890 | 26.89 | 7.32 | 7.48 | 143 | 14 | 304 | 32 | 258 | 18 | NA | 500 | 0.2 | 24.38 | 1700000
2022-07-14 | 27110 | 27.11 | 7.19 | 7.41 | 136 | 12 | 312 | 36 | 265 | 21 | NA | 600 | 0.3 | 24.16 | 1400000
2022-07-15 | 26340 | 26.34 | 7.24 | 7.56 | 140 | 13 | 320 | 40 | 271 | 20 | NA | 400 | 0.2 | 23.86 | 1200000
2022-07-16 | 31840 | 31.84 | 7.35 | 7.52 | 146 | 14 | 308 | 44 | 284 | 22 | NA | 700 | 0.3 | 23.47 | 1300000
2022-07-17 | 26020 | 26.02 | 7.28 | 7.61 | 136 | 12 | 304 | 40 | 276 | 19 | NA | 600 | 0.2 | 24.42 | 1400000
2022-07-18 | 27360 | 27.36 | 7.21 | 7.68 | 143 | 13 | 316 | 36 | 269 | 21 | NA | 500 | 0.2 | 23.68 | 1200000
2022-07-19 | 27720 | 27.72 | 7.33 | 7.57 | 140 | 12 | 308 | 40 | 278 | 18 | NA | 400 | 0.3 | 24.12 | 1700000
2022-07-20 | 28120 | 28.12 | 7.27 | 7.64 | 146 | 14 | 312 | 36 | 264 | 20 | NA | 700 | 0.2 | 23.92 | 1400000
2022-07-21 | 31720 | 31.72 | 7.38 | 7.58 | 136 | 12 | 324 | 44 | 286 | 22 | NA | 600 | 0.3 | 24.26 | 1300000
2022-07-22 | 28230 | 28.23 | 7.24 | 7.69 | 143 | 13 | 316 | 40 | 276 | 20 | NA | 400 | 0.2 | 23.78 | 1200000
2022-07-23 | 26460 | 26.46 | 7.31 | 7.56 | 133 | 11 | 304 | 36 | 268 | 18 | NA | 500 | 0.3 | 24.14 | 1700000
2022-07-24 | 30650 | 30.65 | 7.42 | 7.64 | 140 | 14 | 312 | 40 | 280 | 21 | NA | 700 | 0.3 | 24.38 | 1400000
2022-07-25 | 31040 | 31.04 | 7.27 | 7.52 | 136 | 12 | 320 | 44 | 274 | 19 | NA | 600 | 0.2 | 23.84 | 1300000
2022-07-26 | 29570 | 29.57 | 7.34 | 7.46 | 133 | 11 | 308 | 36 | 269 | 18 | NA | 400 | 0.3 | 23.29 | 1700000
2022-07-27 | 28320 | 28.32 | 7.39 | 7.57 | 143 | 13 | 316 | 40 | 282 | 20 | NA | 600 | 0.2 | 24.08 | 1400000
2022-07-28 | 30860 | 30.86 | 7.29 | 7.52 | 136 | 12 | 324 | 44 | 276 | 22 | NA | 700 | 0.3 | 23.54 | 1300000
2022-07-29 | 29620 | 29.62 | 7.34 | 7.61 | 140 | 13 | 340 | 36 | 286 | 19 | NA | 500 | 0.3 | 23.86 | 1700000
2022-07-30 | 31430 | 31.43 | 7.13 | 7.42 | 146 | 14 | 328 | 40 | 276 | 21 | NA | 400 | 0.2 | 24.45 | 1200000
2022-07-31 | 29980 | 29.98 | 7.26 | 7.51 | 136 | 12 | 320 | 36 | 279 | 20 | NA | 700 | 0.3 | 24.17 | 1400000
Average | 28248.0645 | 28.2481 | 7.2777 | 7.5774 | 139.4839 | 12.6452 | 315.6129 | 39.4839 | 274.0645 | 19.8387 | NA | 561.2903 | 0.25161 | 23.8023 | 1406451.6129
| 875690 | 875.69
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 25920 | 25.92 | 7.13 | 7.41 | 133 | 11 | 304 | 32 | 258 | 17 |  | 400 | 0.2 | 22.42 | 1200000
Max | 31840 | 31.84 | 7.42 | 7.71 | 146 | 14 | 340 | 44 | 286 | 22 |  | 700 | 0.3 | 24.45 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-07-01 | 13900 | 13.9 | 7.24 | 7.58 | 135 | 16 | 304 | 36 | 266 | 22 | NA | 400 | 0.3 | 22.31 | 1600000
2022-07-02 | 13310 | 13.31 | 7.36 | 7.66 | 140 | 15 | 316 | 40 | 276 | 24 | NA | 600 | 0.2 | 21.54 | 1400000
2022-07-03 | 14920 | 14.92 | 7.29 | 7.47 | 146 | 14 | 328 | 36 | 284 | 26 | NA | 500 | 0.3 | 23.13 | 1300000
2022-07-04 | 14880 | 14.88 | 7.21 | 7.54 | 155 | 16 | 320 | 40 | 272 | 23 | NA | 700 | 0.2 | 22.68 | 1700000
2022-07-05 | 13010 | 13.01 | 7.32 | 7.67 | 150 | 17 | 324 | 44 | 282 | 25 | NA | 600 | 0.3 | 23.34 | 1600000
2022-07-06 | 14610 | 14.61 | 7.26 | 7.51 | 142 | 15 | 308 | 40 | 268 | 22 | NA | 500 | 0.3 | 22.74 | 1300000
2022-07-07 | 14940 | 14.94 | 7.34 | 7.71 | 152 | 13 | 332 | 36 | 279 | 24 | NA | 400 | 0.2 | 23.2 | 1200000
2022-07-08 | 14350 | 14.35 | 7.25 | 7.61 | 145 | 14 | 312 | 40 | 261 | 21 | NA | 600 | 0.3 | 21.83 | 1400000
2022-07-09 | 15480 | 15.48 | 7.18 | 7.54 | 150 | 16 | 320 | 44 | 270 | 23 | NA | 700 | 0.2 | 22.38 | 1600000
2022-07-10 | 15390 | 15.39 | 7.31 | 7.76 | 160 | 14 | 328 | 36 | 286 | 25 | NA | 500 | 0.3 | 21.46 | 1300000
2022-07-11 | 14370 | 14.37 | 7.29 | 7.69 | 146 | 15 | 316 | 44 | 277 | 22 | NA | 600 | 0.2 | 23.16 | 1200000
2022-07-12 | 14380 | 14.38 | 7.22 | 7.56 | 140 | 13 | 324 | 36 | 269 | 20 | NA | 500 | 0.2 | 22.66 | 1400000
2022-07-13 | 14470 | 14.47 | 7.33 | 7.73 | 135 | 14 | 336 | 32 | 280 | 23 | NA | 400 | 0.3 | 23.51 | 1300000
2022-07-14 | 14430 | 14.43 | 7.24 | 7.68 | 142 | 15 | 320 | 36 | 271 | 21 | NA | 700 | 0.2 | 22.44 | 1400000
2022-07-15 | 14650 | 14.65 | 7.31 | 7.63 | 138 | 16 | 312 | 40 | 266 | 23 | NA | 500 | 0.2 | 22.57 | 1200000
2022-07-16 | 15390 | 15.39 | 7.21 | 7.71 | 145 | 15 | 324 | 44 | 282 | 22 | NA | 600 | 0.3 | 23.12 | 1700000
2022-07-17 | 14980 | 14.98 | 7.26 | 7.67 | 136 | 14 | 316 | 40 | 276 | 20 | NA | 500 | 0.2 | 23.53 | 1300000
2022-07-18 | 13410 | 13.41 | 7.36 | 7.61 | 130 | 15 | 304 | 44 | 251 | 24 | NA | 600 | 0.2 | 22.29 | 1400000
2022-07-19 | 14820 | 14.82 | 7.23 | 7.57 | 140 | 14 | 320 | 36 | 268 | 22 | NA | 400 | 0.3 | 21.98 | 1200000
2022-07-20 | 14590 | 14.59 | 7.29 | 7.66 | 133 | 15 | 312 | 40 | 286 | 25 | NA | 500 | 0.2 | 23.27 | 1600000
2022-07-21 | 14260 | 14.26 | 7.18 | 7.52 | 136 | 14 | 328 | 36 | 273 | 23 | NA | 600 | 0.2 | 22.48 | 1400000
2022-07-22 | 13370 | 13.37 | 7.28 | 7.58 | 130 | 16 | 308 | 44 | 260 | 25 | NA | 500 | 0.3 | 22.56 | 1300000
2022-07-23 | 13630 | 13.63 | 7.24 | 7.63 | 139 | 15 | 300 | 40 | 271 | 22 | NA | 700 | 0.2 | 21.86 | 1400000
2022-07-24 | 15220 | 15.22 | 7.31 | 7.55 | 145 | 16 | 312 | 44 | 280 | 24 | NA | 400 | 0.3 | 20.41 | 1700000
2022-07-25 | 16890 | 16.89 | 7.19 | 7.61 | 140 | 14 | 304 | 40 | 268 | 23 | NA | 500 | 0.2 | 22.13 | 1300000
2022-07-26 | 12910 | 12.91 | 7.25 | 7.58 | 135 | 13 | 316 | 36 | 274 | 21 | NA | 600 | 0.3 | 21.78 | 1400000
2022-07-27 | 10720 | 10.72 | 7.34 | 7.64 | 130 | 15 | 300 | 40 | 261 | 24 | NA | 400 | 0.3 | 23.18 | 1700000
2022-07-28 | 14200 | 14.2 | 7.17 | 7.53 | 139 | 14 | 320 | 36 | 276 | 22 | NA | 500 | 0.2 | 22.34 | 1200000
2022-07-29 | 13800 | 13.8 | 7.22 | 7.66 | 132 | 16 | 312 | 44 | 269 | 20 | NA | 600 | 0.2 | 21.44 | 1400000
2022-07-30 | 13310 | 13.31 | 7.26 | 7.51 | 140 | 15 | 316 | 40 | 258 | 23 | NA | 400 | 0.3 | 22.25 | 1300000
2022-07-31 | 16010 | 16.01 | 7.33 | 7.62 | 135 | 13 | 304 | 36 | 264 | 21 | NA | 500 | 0.2 | 21.81 | 1200000
Average | 14341.9355 | 14.3419 | 7.2668 | 7.6126 | 140.6774 | 14.7419 | 316 | 39.3548 | 271.7419 | 22.7419 | NA | 532.2581 | 0.24516 | 22.4316 | 1400000
| 444600 | 444.6
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 10720 | 10.72 | 7.17 | 7.47 | 130 | 13 | 300 | 32 | 251 | 20 |  | 400 | 0.2 | 20.41 | 1200000
Max | 16890 | 16.89 | 7.36 | 7.76 | 160 | 17 | 336 | 44 | 286 | 26 |  | 700 | 0.3 | 23.53 | 1700000