## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-06-01 | 61520 | 61.52 | 7.38 | 7.76 | 140 | 15 | 308 | 36 | 257 | 23 | NA | 400 | 0.3 | 23.5 | 1700000
2023-06-02 | 63400 | 63.4 | 7.42 | 7.7 | 130 | 14 | 324 | 40 | 268 | 22 | NA | 600 | 0.2 | 24.47 | 1300000
2023-06-03 | 58410 | 58.41 | 7.23 | 7.64 | 145 | 16 | 320 | 40 | 264 | 24 | NA | 500 | 0.3 | 24.04 | 1100000
2023-06-04 | 59620 | 59.62 | 7.28 | 7.7 | 150 | 16 | 308 | 40 | 271 | 22 | NA | 700 | 0.3 | 23.55 | 1700000
2023-06-05 | 61420 | 61.42 | 7.36 | 7.74 | 140 | 18 | 332 | 44 | 276 | 25 | NA | 400 | 0.2 | 24.26 | 1300000
2023-06-06 | 60750 | 60.75 | 7.44 | 7.78 | 145 | 17 | 328 | 40 | 274 | 26 | NA | 600 | 0.3 | 23.72 | 1400000
2023-06-07 | 60960 | 60.96 | 7.32 | 7.68 | 135 | 16 | 324 | 44 | 258 | 23 | NA | 500 | 0.3 | 23.78 | 1700000
2023-06-08 | 60720 | 60.72 | 7.48 | 7.75 | 145 | 14 | 312 | 36 | 252 | 22 | NA | 600 | 0.2 | 24.23 | 1300000
2023-06-09 | 60960 | 60.96 | 7.28 | 7.65 | 140 | 15 | 328 | 40 | 248 | 19 | NA | 400 | 0.3 | 23.64 | 1100000
2023-06-10 | 58780 | 58.78 | 7.4 | 7.7 | 130 | 14 | 320 | 44 | 224 | 20 | NA | 700 | 0.3 | 24.02 | 1700000
2023-06-11 | 59990 | 59.88 | 7.36 | 7.72 | 145 | 16 | 316 | 36 | 246 | 20 | NA | 500 | 0.2 | 23.69 | 1400000
2023-06-12 | 59990 | 59.99 | 7.42 | 7.76 | 150 | 16 | 308 | 40 | 256 | 19 | NA | 600 | 0.2 | 24.16 | 1100000
2023-06-13 | 58270 | 58.27 | 7.38 | 7.73 | 130 | 18 | 312 | 44 | 261 | 23 | NA | 400 | 0.3 | 23.57 | 1300000
2023-06-14 | 55380 | 55.38 | 7.26 | 7.71 | 145 | 15 | 300 | 44 | 268 | 24 | NA | 500 | 0.2 | 24.82 | 1400000
2023-06-15 | 53350 | 53.35 | 7.32 | 7.75 | 140 | 16 | 304 | 40 | 246 | 22 | NA | 600 | 0.3 | 23.44 | 1300000
2023-06-16 | 59700 | 59.7 | 7.28 | 7.69 | 130 | 14 | 328 | 44 | 254 | 23 | NA | 500 | 0.3 | 23.69 | 1400000
2023-06-17 | 58330 | 58.33 | 7.38 | 7.68 | 150 | 17 | 320 | 40 | 240 | 22 | NA | 700 | 0.3 | 24.86 | 1700000
2023-06-18 | 55900 | 55.9 | 7.38 | 7.77 | 135 | 16 | 332 | 44 | 248 | 23 | NA | 600 | 0.2 | 24.09 | 1300000
2023-06-19 | 48980 | 48.98 | 7.26 | 7.74 | 145 | 16 | 316 | 44 | 267 | 23 | NA | 400 | 0.3 | 24.82 | 1100000 | Raw sewage received is less due to power cut for more than 24 hrs because of fault in power cable to Numayadahi STP and Sasurkadheri SPS. Plant was operated on DG power for complete day.
2023-06-20 | 56340 | 56.34 | 7.36 | 7.76 | 150 | 18 | 312 | 40 | 244 | 22 | NA | 500 | 0.2 | 23.22 | 1300000
2023-06-21 | 50260 | 50.26 | 7.26 | 7.68 | 130 | 15 | 320 | 44 | 263 | 23 | NA | 700 | 0.3 | 23.64 | 1400000
2023-06-22 | 51780 | 51.78 | 7.42 | 7.78 | 145 | 16 | 308 | 40 | 268 | 23 | NA | 600 | 0.3 | 24.25 | 1700000
2023-06-23 | 51650 | 51.65 | 7.33 | 7.74 | 135 | 14 | 324 | 44 | 257 | 24 | NA | 500 | 0.2 | 22.85 | 1400000
2023-06-24 | 52860 | 52.86 | 7.26 | 7.75 | 140 | 17 | 316 | 44 | 263 | 24 | NA | 700 | 0.3 | 24.79 | 1300000
2023-06-25 | 62180 | 62.18 | 7.34 | 7.77 | 130 | 16 | 328 | 40 | 248 | 22 | NA | 600 | 0.2 | 23.78 | 1100000
2023-06-26 | 64020 | 64.02 | 7.42 | 7.78 | 150 | 17 | 332 | 44 | 259 | 25 | NA | 400 | 0.2 | 24.37 | 1400000
2023-06-27 | 62750 | 62.75 | 7.46 | 7.7 | 135 | 15 | 312 | 36 | 271 | 23 | NA | 700 | 0.3 | 23.75 | 1100000
2023-06-28 | 55150 | 55.15 | 7.36 | 7.78 | 140 | 17 | 320 | 44 | 276 | 26 | NA | 500 | 0.2 | 24.2 | 1400000 | Raw sewage received is less on 28.06.2023 & 29.06.2023 due to leakge in rising main from Ghagharnalla MPR to Numayadahi STP. Numayadahi STP, Ghagharnalla SPS, Sasur Kadheri SPS were stopped at 8:30 PM on 28.06.2023 and started at 4:30 PM on 29.06.2023
2023-06-29 | 18720 | 18.72 | 7.28 | 7.67 | 130 | 14 | 304 | 36 | 247 | 22 | NA | 600 | 0.3 | 23.57 | 1300000
2023-06-30 | 57530 | 57.53 | 7.44 | 7.76 | 145 | 16 | 324 | 40 | 266 | 25 | NA | 400 | 0.3 | 24.98 | 1700000
Average | 56655.6667 | 56.652 | 7.352 | 7.7273 | 140 | 15.8 | 318 | 41.0667 | 258 | 22.8 | NA | 546.6667 | 0.26 | 23.9917 | 1380000
1699.56
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 18720 | 18.72 | 7.23 | 7.64 | 130 | 14 | 300 | 36 | 224 | 19 |  | 400 | 0.2 | 22.85 | 1100000
Max | 64020 | 64.02 | 7.48 | 7.78 | 150 | 18 | 332 | 44 | 276 | 26 |  | 700 | 0.3 | 24.98 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-06-01 | 35270 | 35.27 | 7.34 | 7.42 | 165 | 27 | 364 | 44 | 328 | 37 | NA | 600 | 0.3 | 24.4 | 1400000
2023-06-02 | 37810 | 37.81 | 7.28 | 7.39 | 160 | 25 | 360 | 44 | 336 | 39 | NA | 700 | 0.2 | 23.6 | 1300000
2023-06-03 | 35020 | 35.02 | 7.31 | 7.4 | 155 | 22 | 356 | 40 | 340 | 33 | NA | 400 | 0.3 | 24.7 | 1400000
2023-06-04 | 37260 | 37.26 | 7.29 | 7.35 | 160 | 23 | 352 | 40 | 297 | 36 | NA | 500 | 0.3 | 25.3 | 1700000
2023-06-05 | 35100 | 35.1 | 7.33 | 7.42 | 150 | 25 | 360 | 48 | 314 | 42 | NA | 800 | 0.2 | 24.5 | 1200000
2023-06-06 | 36710 | 36.71 | 7.34 | 7.44 | 155 | 23 | 364 | 40 | 323 | 37 | NA | 600 | 0.3 | 23.7 | 1400000
2023-06-07 | 35500 | 35.5 | 7.3 | 7.5 | 150 | 21 | 356 | 32 | 296 | 28 | NA | 700 | 0.2 | 23.1 | 1100000
2023-06-08 | 36350 | 36.35 | 7.35 | 7.41 | 155 | 23 | 360 | 36 | 330 | 29 | NA | 400 | 0.3 | 24.6 | 1300000
2023-06-09 | 35820 | 35.82 | 7.32 | 7.47 | 160 | 25 | 352 | 36 | 314 | 28 | NA | 600 | 0.2 | 25.2 | 1700000
2023-06-10 | 35510 | 35.51 | 7.43 | 7.52 | 165 | 26 | 360 | 40 | 322 | 30 | NA | 700 | 0.3 | 24.3 | 1400000
2023-06-11 | 38240 | 38.24 | 7.45 | 7.49 | 160 | 26 | 348 | 40 | 308 | 29 | NA | 800 | 0.3 | 23.8 | 1700000
2023-06-12 | 40350 | 40.35 | 7.39 | 7.5 | 165 | 25 | 356 | 40 | 298 | 31 | NA | 400 | 0.2 | 25.3 | 1100000
2023-06-13 | 38700 | 38.7 | 7.4 | 7.48 | 155 | 19 | 360 | 36 | 309 | 33 | NA | 500 | 0.3 | 24.2 | 1300000
2023-06-14 | 39140 | 39.1 | 7.37 | 7.44 | 160 | 24 | 364 | 40 | 320 | 31 | NA | 700 | 0.3 | 25.4 | 1400000
2023-06-15 | 37140 | 37.14 | 7.42 | 7.46 | 165 | 25 | 360 | 40 | 310 | 30 | NA | 400 | 0.2 | 24.6 | 1200000
2023-06-16 | 40480 | 40.48 | 7.37 | 7.43 | 170 | 27 | 364 | 36 | 317 | 31 | NA | 600 | 0.3 | 24.2 | 1100000
2023-06-17 | 41360 | 41.36 | 7.45 | 7.52 | 165 | 24 | 360 | 40 | 328 | 33 | NA | 800 | 0.2 | 23.5 | 1700000
2023-06-18 | 39440 | 39.44 | 7.42 | 7.51 | 160 | 27 | 368 | 44 | 332 | 32 | NA | 500 | 0.3 | 25.3 | 1400000 | Timely testing of fecal coliform samples for effluent and sludge hence results obtained for the same will not be deemed as valid.
2023-06-19 | 46040 | 46.04 | 7.46 | 7.5 | 165 | 26 | 372 | 44 | 326 | 37 | NA | 700 | 0.3 | 24.5 | 1700000
2023-06-20 | 40100 | 40.1 | 7.37 | 7.45 | 155 | 24 | 364 | 48 | 322 | 39 | NA | 600 | 0.2 | 24.7 | 1400000
2023-06-21 | 39040 | 39.04 | 7.43 | 7.49 | 160 | 22 | 368 | 40 | 335 | 38 | NA | 500 | 0.2 | 23.9 | 1300000
2023-06-22 | 43700 | 43.7 | 7.44 | 7.53 | 155 | 24 | 364 | 40 | 332 | 34 | NA | 700 | 0.3 | 25.3 | 1200000
2023-06-23 | 43950 | 43.95 | 7.42 | 7.48 | 165 | 27 | 360 | 44 | 340 | 31 | NA | 400 | 0.3 | 25.6 | 1100000
2023-06-24 | 39820 | 39.82 | 7.51 | 7.55 | 160 | 28 | 364 | 44 | 335 | 32 | NA | 700 | 0.2 | 24.2 | 1700000
2023-06-25 | 41840 | 41.84 | 7.08 | 7.39 | 165 | 27 | 368 | 40 | 345 | 35 | NA | 800 | 0.3 | 23.7 | 1300000
2023-06-26 | 43250 | 43.25 | 7.47 | 7.56 | 160 | 21 | 364 | 36 | 328 | 31 | NA | 500 | 0.3 | 24.6 | 1400000
2023-06-27 | 38690 | 38.69 | 7.32 | 7.48 | 155 | 21 | 352 | 36 | 321 | 32 | NA | 700 | 0.3 | 25.4 | 1200000
2023-06-28 | 36120 | 36.12 | 7.43 | 7.52 | 150 | 22 | 348 | 40 | 340 | 35 | NA | 600 | 0.2 | 24.5 | 1300000
2023-06-29 | 37900 | 37.9 | 7.48 | 7.54 | 155 | 21 | 356 | 40 | 343 | 34 | NA | 400 | 0.3 | 25.3 | 1400000
2023-06-30 | 38510 | 38.51 | 7.37 | 7.56 | 160 | 23 | 360 | 36 | 332 | 31 | NA | 500 | 0.3 | 24.7 | 1700000
Average | 38805.3333 | 38.804 | 7.378 | 7.4733 | 159.3333 | 24.1 | 360.1333 | 40.1333 | 324.0333 | 33.2667 | NA | 593.3333 | 0.26333 | 24.5367 | 1383333.3333
1164.12
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 35020 | 35.02 | 7.08 | 7.35 | 150 | 19 | 348 | 32 | 296 | 28 |  | 400 | 0.2 | 23.1 | 1100000
Max | 46040 | 46.04 | 7.51 | 7.56 | 170 | 28 | 372 | 48 | 345 | 42 |  | 800 | 0.3 | 25.6 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-06-01 | 25860 | 25.86 | 7.23 | 7.48 | 135 | 11 | 312 | 36 | 259 | 21 | NA | 700 | 0.2 | 22.41 | 1400000
2023-06-02 | 26280 | 26.28 | 7.18 | 7.53 | 140 | 13 | 320 | 40 | 265 | 23 | NA | 500 | 0.3 | 23.19 | 1200000
2023-06-03 | 28360 | 28.36 | 7.24 | 7.46 | 145 | 12 | 304 | 36 | 275 | 22 | NA | 400 | 0.3 | 24.49 | 1300000
2023-06-04 | 28030 | 28.03 | 7.22 | 7.41 | 140 | 15 | 296 | 40 | 262 | 20 | NA | 600 | 0.2 | 24.11 | 1700000
2023-06-05 | 28660 | 28.66 | 7.17 | 7.54 | 130 | 12 | 304 | 36 | 281 | 22 | NA | 500 | 0.3 | 23.78 | 1300000
2023-06-06 | 28130 | 28.13 | 7.2 | 7.49 | 145 | 13 | 292 | 40 | 270 | 20 | NA | 600 | 0.2 | 23.36 | 1200000
2023-06-07 | 27170 | 27.17 | 7.26 | 7.45 | 150 | 15 | 308 | 44 | 279 | 21 | NA | 400 | 0.2 | 24.35 | 1300000
2023-06-08 | 30560 | 30.56 | 7.24 | 7.47 | 135 | 16 | 296 | 40 | 273 | 22 | NA | 700 | 0.2 | 23.97 | 1700000
2023-06-09 | 27790 | 27.79 | 7.19 | 7.5 | 130 | 11 | 284 | 32 | 267 | 21 | NA | 400 | 0.3 | 24.21 | 1200000
2023-06-10 | 25920 | 25.92 | 7.22 | 7.48 | 140 | 13 | 292 | 36 | 270 | 22 | NA | 500 | 0.2 | 23.27 | 1400000
2023-06-11 | 26500 | 26.5 | 7.28 | 7.52 | 145 | 14 | 304 | 40 | 264 | 20 | NA | 700 | 0.2 | 23.09 | 1300000
2023-06-12 | 26370 | 26.37 | 7.26 | 7.54 | 150 | 15 | 296 | 44 | 268 | 21 | NA | 600 | 0.3 | 23.16 | 1400000
2023-06-13 | 26390 | 26.39 | 7.21 | 7.49 | 140 | 12 | 288 | 36 | 275 | 22 | NA | 500 | 0.3 | 23.44 | 1300000
2023-06-14 | 26760 | 26.76 | 7.25 | 7.51 | 135 | 14 | 308 | 40 | 283 | 25 | NA | 400 | 0.2 | 24.35 | 1200000
2023-06-15 | 27030 | 27.03 | 7.24 | 7.48 | 130 | 12 | 316 | 36 | 298 | 27 | NA | 500 | 0.3 | 24.65 | 1400000
2023-06-16 | 26980 | 26.98 | 7.18 | 7.53 | 140 | 14 | 304 | 40 | 263 | 25 | NA | 400 | 0.3 | 23.73 | 1300000
2023-06-17 | 26950 | 26.95 | 7.23 | 7.5 | 145 | 15 | 320 | 44 | 287 | 28 | NA | 700 | 0.2 | 24.4 | 1200000
2023-06-18 | 29220 | 29.22 | 7.25 | 7.48 | 130 | 12 | 296 | 36 | 289 | 26 | NA | 600 | 0.3 | 24 | 1700000
2023-06-19 | 28430 | 28.43 | 7.28 | 7.57 | 155 | 13 | 304 | 40 | 262 | 24 | NA | 400 | 0.3 | 22.81 | 1300000
2023-06-20 | 29510 | 29.51 | 7.31 | 7.52 | 135 | 12 | 288 | 36 | 275 | 25 | NA | 700 | 0.3 | 23.71 | 1400000
2023-06-21 | 28730 | 28.73 | 7.27 | 7.48 | 150 | 14 | 312 | 40 | 284 | 24 | NA | 500 | 0.2 | 24.54 | 1200000
2023-06-22 | 28390 | 28.39 | 7.29 | 7.51 | 145 | 16 | 324 | 44 | 296 | 29 | NA | 600 | 0.2 | 22.57 | 1300000
2023-06-23 | 28910 | 28.91 | 7.21 | 7.47 | 140 | 11 | 308 | 32 | 279 | 22 | NA | 500 | 0.2 | 23.39 | 1700000
2023-06-24 | 30010 | 30.01 | 7.25 | 7.43 | 150 | 14 | 310 | 40 | 273 | 25 | NA | 700 | 0.3 | 23.44 | 1200000
2023-06-25 | 28840 | 28.84 | 7.19 | 7.45 | 135 | 12 | 296 | 36 | 267 | 23 | NA | 400 | 0.2 | 24.28 | 1400000
2023-06-26 | 29140 | 29.14 | 7.26 | 7.43 | 145 | 13 | 304 | 40 | 278 | 21 | NA | 700 | 0.3 | 23.75 | 1300000
2023-06-27 | 33590 | 33.59 | 7.22 | 7.52 | 130 | 15 | 324 | 44 | 307 | 29 | NA | 600 | 0.3 | 23.94 | 1700000
2023-06-28 | 33500 | 33.5 | 7.24 | 7.49 | 140 | 13 | 308 | 36 | 286 | 23 | NA | 400 | 0.2 | 23.68 | 1200000
2023-06-29 | 32530 | 32.53 | 7.28 | 7.44 | 145 | 12 | 316 | 40 | 292 | 22 | NA | 600 | 0.3 | 24.94 | 1700000
2023-06-30 | 39250 | 39.25 | 7.27 | 7.46 | 140 | 13 | 312 | 36 | 277 | 23 | NA | 500 | 0.3 | 24.57 | 1400000
Average | 28793 | 28.793 | 7.2373 | 7.4877 | 140.5 | 13.2333 | 304.8667 | 38.6667 | 276.8 | 23.2667 | NA | 543.3333 | 0.25333 | 23.786 | 1376666.6667
863.79
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 25860 | 25.86 | 7.17 | 7.41 | 130 | 11 | 284 | 32 | 259 | 20 |  | 400 | 0.2 | 22.41 | 1200000
Max | 39250 | 39.25 | 7.31 | 7.57 | 155 | 16 | 324 | 44 | 307 | 29 |  | 700 | 0.3 | 24.94 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-06-01 | 12790 | 12.79 | 7.4 | 7.72 | 145 | 19 | 300 | 48 | 263 | 27 | NA | 500 | 0.2 | 23.11 | 1200000
2023-06-02 | 12870 | 12.87 | 7.48 | 7.65 | 150 | 17 | 308 | 44 | 285 | 26 | NA | 400 | 0.3 | 23.4 | 1300000
2023-06-03 | 13810 | 13.81 | 7.39 | 7.68 | 130 | 18 | 304 | 48 | 276 | 25 | NA | 300 | 0.3 | 22.88 | 1200000
2023-06-04 | 13070 | 13.07 | 7.29 | 7.67 | 140 | 17 | 312 | 44 | 292 | 24 | NA | 400 | 0.2 | 22.41 | 1300000
2023-06-05 | 13510 | 13.51 | 7.38 | 7.7 | 135 | 18 | 302 | 48 | 282 | 26 | NA | 300 | 0.3 | 23.43 | 1400000
2023-06-06 | 12590 | 12.59 | 7.4 | 7.66 | 145 | 17 | 306 | 44 | 298 | 24 | NA | 500 | 0.3 | 21.85 | 1200000
2023-06-07 | 11590 | 11.59 | 7.42 | 7.69 | 130 | 18 | 300 | 48 | 284 | 25 | NA | 400 | 0.3 | 22.49 | 1500000
2023-06-08 | 12450 | 12.45 | 7.41 | 7.72 | 140 | 16 | 302 | 44 | 270 | 24 | NA | 600 | 0.2 | 23.51 | 1200000
2023-06-09 | 13660 | 13.66 | 7.4 | 7.74 | 135 | 17 | 308 | 48 | 286 | 23 | NA | 300 | 0.3 | 23.7 | 1400000
2023-06-10 | 15380 | 15.38 | 7.46 | 7.76 | 150 | 18 | 312 | 44 | 289 | 22 | NA | 400 | 0.3 | 23.5 | 1200000
2023-06-11 | 13290 | 13.29 | 7.43 | 7.73 | 145 | 16 | 306 | 48 | 274 | 23 | NA | 500 | 0.3 | 23.67 | 1300000
2023-06-12 | 14300 | 12.62 | 7.45 | 7.68 | 140 | 15 | 310 | 44 | 286 | 24 | NA | 400 | 0.2 | 22.38 | 1400000
2023-06-13 | 14300 | 14.3 | 7.44 | 7.7 | 130 | 17 | 300 | 48 | 279 | 27 | NA | 300 | 0.3 | 23.68 | 1200000
2023-06-14 | 13260 | 13.26 | 7.4 | 7.74 | 145 | 16 | 308 | 44 | 283 | 25 | NA | 600 | 0.3 | 23.72 | 1500000
2023-06-15 | 12460 | 12.46 | 7.44 | 7.75 | 135 | 18 | 318 | 48 | 294 | 24 | NA | 400 | 0.2 | 23.5 | 1300000
2023-06-16 | 13400 | 13.46 | 7.41 | 7.7 | 150 | 17 | 312 | 44 | 289 | 25 | NA | 300 | 0.3 | 23.23 | 1200000
2023-06-17 | 13150 | 13.15 | 7.43 | 7.72 | 140 | 18 | 300 | 48 | 294 | 26 | NA | 400 | 0.3 | 23.77 | 1300000
2023-06-18 | 13370 | 13.37 | 7.46 | 7.75 | 130 | 16 | 296 | 44 | 270 | 24 | NA | 500 | 0.3 | 23.55 | 1400000
2023-06-19 | 13540 | 13.54 | 7.43 | 7.78 | 145 | 17 | 308 | 48 | 294 | 25 | NA | 300 | 0.3 | 23.06 | 1200000
2023-06-20 | 14510 | 14.51 | 7.41 | 7.75 | 135 | 18 | 300 | 44 | 283 | 26 | NA | 200 | 0.2 | 23.67 | 1300000
2023-06-21 | 13620 | 13.62 | 7.4 | 7.64 | 140 | 17 | 306 | 48 | 296 | 25 | NA | 400 | 0.3 | 23.72 | 1200000
2023-06-22 | 13450 | 13.45 | 7.46 | 7.69 | 150 | 18 | 312 | 44 | 290 | 26 | NA | 300 | 0.3 | 21.85 | 1400000
2023-06-23 | 13760 | 13.76 | 7.43 | 7.71 | 145 | 16 | 316 | 48 | 286 | 24 | NA | 500 | 0.3 | 23.5 | 1200000
2023-06-24 | 11390 | 11.39 | 7.4 | 7.75 | 140 | 17 | 320 | 44 | 298 | 27 | NA | 300 | 0.3 | 22.41 | 1300000
2023-06-25 | 13690 | 13.69 | 7.46 | 7.79 | 145 | 18 | 308 | 48 | 288 | 23 | NA | 200 | 0.2 | 23.43 | 1400000
2023-06-26 | 14000 | 14 | 7.42 | 7.74 | 130 | 16 | 304 | 44 | 294 | 22 | NA | 400 | 0.3 | 23.51 | 1200000
2023-06-27 | 13650 | 13.65 | 7.4 | 7.78 | 150 | 15 | 310 | 48 | 290 | 21 | NA | 500 | 0.3 | 23.72 | 1300000
2023-06-28 | 12880 | 12.88 | 7.41 | 7.73 | 140 | 18 | 300 | 44 | 282 | 26 | NA | 600 | 0.3 | 23.36 | 1400000
2023-06-29 | 14870 | 14.87 | 7.44 | 7.55 | 145 | 17 | 308 | 48 | 276 | 23 | NA | 400 | 0.2 | 22.96 | 1300000
2023-06-30 | 14320 | 14.32 | 7.38 | 7.38 | 135 | 16 | 312 | 44 | 289 | 24 | NA | 600 | 0.3 | 23.45 | 1200000
Average | 13431 | 13.377 | 7.4177 | 7.7017 | 140.5 | 17.0333 | 306.9333 | 46 | 285.3333 | 24.5333 | NA | 406.6667 | 0.27333 | 23.214 | 1296666.6667
401.31
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11390 | 11.39 | 7.29 | 7.38 | 130 | 15 | 296 | 44 | 263 | 21 |  | 200 | 0.2 | 21.85 | 1200000
Max | 15380 | 15.38 | 7.48 | 7.79 | 150 | 19 | 320 | 48 | 298 | 27 |  | 600 | 0.3 | 23.77 | 1500000