## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-06-01 | 51830 | 51.83 | 7.16 | 7.64 | 145 | 16 | 360 | 40 | 292 | 24 | NA | 700 | 0.2 | 22.56 | 1300000
2022-06-02 | 52730 | 52.73 | 7.28 | 7.82 | 140 | 14 | 316 | 36 | 268 | 28 | NA | 500 | 0.3 | 23.53 | 1700000
2022-06-03 | 59970 | 59.97 | 7.22 | 7.76 | 135 | 17 | 312 | 40 | 238 | 24 | NA | 700 | 0.2 | 24.06 | 1700000
2022-06-04 | 50820 | 50.82 | 7.19 | 7.68 | 145 | 17 | 320 | 36 | 254 | 26 | NA | 400 | 0.3 | 23.63 | 1300000 | Raw sewage received is less due to problem in bypass valve at Sasur Kadheri pumping station.
2022-06-05 | 42090 | 42.09 | 7.14 | 7.64 | 130 | 14 | 348 | 44 | 240 | 28 | NA | 600 | 0.2 | 24.18 | 1400000 | Raw sewage received is less as water supply was stopped for 15 - 16 hours in Kareli area
2022-06-06 | 53860 | 53.86 | 7.23 | 7.76 | 135 | 16 | 320 | 40 | 258 | 26 | NA | 400 | 0.3 | 23.39 | 1700000
2022-06-07 | 59210 | 59.21 | 7.24 | 7.74 | 140 | 14 | 328 | 36 | 242 | 25 | NA | 700 | 0.2 | 24.29 | 1300000
2022-06-08 | 57170 | 57.17 | 7.18 | 7.26 | 140 | 13 | 340 | 44 | 264 | 28 | NA | 500 | 0.2 | 22.81 | 1700000
2022-06-09 | 63060 | 63.06 | 7.23 | 7.46 | 150 | 16 | 344 | 40 | 255 | 26 | NA | 600 | 0.3 | 24.97 | 1300000
2022-06-10 | 58710 | 58.71 | 7.21 | 7.52 | 140 | 17 | 360 | 36 | 294 | 24 | NA | 400 | 0.2 | 24.33 | 1300000
2022-06-11 | 57540 | 57.54 | 7.18 | 7.46 | 135 | 19 | 316 | 40 | 256 | 26 | NA | 700 | 0.3 | 21.86 | 1400000
2022-06-12 | 60980 | 60.98 | 7.19 | 7.68 | 140 | 15 | 296 | 40 | 264 | 28 | NA | 500 | 0.3 | 22.5 | 1300000
2022-06-13 | 56150 | 56.15 | 7.21 | 7.72 | 130 | 16 | 348 | 44 | 294 | 24 | NA | 600 | 0.2 | 23.52 | 1700000
2022-06-14 | 57860 | 57.86 | 7.26 | 7.78 | 140 | 17 | 328 | 36 | 248 | 26 | NA | 400 | 0.3 | 21.55 | 1400000
2022-06-15 | 53090 | 53.09 | 7.18 | 7.67 | 135 | 16 | 316 | 40 | 268 | 28 | NA | 900 | 0.2 | 24.96 | 1300000
2022-06-16 | 54890 | 54.89 | 7.23 | 7.71 | 125 | 15 | 328 | 40 | 264 | 26 | NA | 700 | 0.2 | 23.38 | 1400000
2022-06-17 | 55080 | 55.08 | 7.18 | 7.64 | 130 | 17 | 304 | 40 | 269 | 24 | NA | 500 | 0.3 | 22.81 | 1700000
2022-06-18 | 60730 | 60.73 | 7.22 | 7.71 | 135 | 14 | 344 | 44 | 248 | 28 | NA | 600 | 0.2 | 24.2 | 1300000
2022-06-19 | 59050 | 59.05 | 7.26 | 7.81 | 130 | 15 | 332 | 36 | 264 | 30 | NA | 400 | 0.3 | 23.66 | 1700000
2022-06-20 | 45510 | 45.51 | 7.18 | 7.69 | 145 | 17 | 328 | 40 | 286 | 24 | NA | 500 | 0.3 | 21.86 | 1400000 | Raw sewage received is less due to problem in inlet valve of Ghagharnalla pumping station in between 3 AM to 10:30 AM.
2022-06-21 | 61540 | 61.54 | 7.24 | 7.76 | 150 | 16 | 332 | 44 | 250 | 28 | NA | 700 | 0.2 | 23.26 | 1300000
2022-06-22 | 57610 | 57.61 | 7.27 | 7.68 | 130 | 14 | 332 | 36 | 258 | 24 | NA | 400 | 0.3 | 22.18 | 1400000
2022-06-23 | 58850 | 58.85 | 7.16 | 7.62 | 145 | 17 | 320 | 40 | 270 | 26 | NA | 600 | 0.2 | 24.02 | 1700000
2022-06-24 | 61190 | 61.19 | 7.23 | 7.74 | 125 | 15 | 360 | 48 | 256 | 29 | NA | 700 | 0.3 | 21.92 | 1300000
2022-06-25 | 64410 | 64.41 | 7.19 | 7.67 | 140 | 16 | 344 | 44 | 243 | 27 | NA | 900 | 0.2 | 22.41 | 1400000
2022-06-26 | 52580 | 52.58 | 7.21 | 7.62 | 150 | 14 | 328 | 36 | 249 | 25 | NA | 500 | 0.3 | 24.25 | 1100000
2022-06-27 | 58570 | 58.57 | 7.29 | 7.58 | 145 | 13 | 324 | 40 | 254 | 28 | NA | 700 | 0.2 | 21.95 | 1700000
2022-06-28 | 56960 | 56.96 | 7.19 | 7.61 | 135 | 15 | 340 | 44 | 261 | 26 | NA | 400 | 0.3 | 23.42 | 1300000
2022-06-29 | 57840 | 57.84 | 7.23 | 7.71 | 140 | 17 | 320 | 36 | 245 | 24 | NA | 600 | 0.3 | 24.24 | 1300000
2022-06-30 | 59510 | 59.51 | 7.21 | 7.67 | 150 | 14 | 308 | 40 | 257 | 28 | NA | 500 | 0.2 | 24.81 | 1700000
Average | 56646.3333 | 56.6463 | 7.213 | 7.6603 | 138.5 | 15.5333 | 329.8667 | 40 | 260.3 | 26.2667 | NA | 576.6667 | 0.25 | 23.3503 | 1450000
1699.39
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 42090 | 42.09 | 7.14 | 7.26 | 125 | 13 | 296 | 36 | 238 | 24 |  | 400 | 0.2 | 21.55 | 1100000
Max | 64410 | 64.41 | 7.29 | 7.82 | 150 | 19 | 360 | 48 | 294 | 30 |  | 900 | 0.3 | 24.97 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-06-01 | 35700 | 35.7 | 7.34 | 7.47 | 162 | 25 | 356 | 36 | 310 | 32 | NA | 600 | 0.3 | 23.8 | 1400000
2022-06-02 | 36710 | 36.71 | 7.46 | 7.51 | 158 | 26 | 348 | 40 | 305 | 36 | NA | 500 | 0.2 | 22.4 | 1600000
2022-06-03 | 33610 | 33.61 | 7.37 | 7.53 | 160 | 24 | 352 | 44 | 303 | 41 | NA | 700 | 0.2 | 24.6 | 1300000
2022-06-04 | 39140 | 39.14 | 7.42 | 7.64 | 168 | 28 | 360 | 40 | 315 | 38 | NA | 500 | 0.3 | 24.2 | 1100000
2022-06-05 | 40010 | 40.01 | 7.5 | 7.58 | 174 | 29 | 364 | 36 | 310 | 35 | NA | 800 | 0.2 | 21.3 | 1700000
2022-06-06 | 42060 | 42.06 | 7.51 | 7.62 | 165 | 32 | 368 | 44 | 298 | 48 | NA | 700 | 0.3 | 22.7 | 1600000
2022-06-07 | 40110 | 40.11 | 7.56 | 7.68 | 167 | 28 | 364 | 48 | 323 | 46 | NA | 600 | 0.3 | 23.5 | 1400000
2022-06-08 | 41500 | 41.5 | 7.49 | 7.58 | 164 | 29 | 356 | 48 | 306 | 49 | NA | 800 | 0.2 | 22.1 | 1600000
2022-06-09 | 36720 | 36.72 | 7.39 | 7.4 | 159 | 24 | 348 | 40 | 294 | 41 | NA | 500 | 0.2 | 23.9 | 1200000
2022-06-10 | 35800 | 35.8 | 7.56 | 7.65 | 165 | 25 | 356 | 36 | 321 | 38 | NA | 400 | 0.2 | 24.2 | 1300000
2022-06-11 | 39150 | 39.15 | 7.48 | 7.52 | 157 | 27 | 364 | 44 | 318 | 42 | NA | 600 | 0.3 | 23.6 | 1400000
2022-06-12 | 41280 | 41.28 | 7.49 | 7.58 | 159 | 28 | 360 | 48 | 334 | 46 | NA | 500 | 0.2 | 24 | 1700000
2022-06-13 | 40750 | 40.75 | 7.3 | 7.55 | 153 | 26 | 356 | 40 | 313 | 40 | NA | 800 | 0.3 | 22.5 | 1300000
2022-06-14 | 40820 | 40.82 | 7.34 | 7.48 | 156 | 27 | 364 | 40 | 311 | 38 | NA | 700 | 0.2 | 23.2 | 1200000
2022-06-15 | 40390 | 40.39 | 7.31 | 7.62 | 153 | 25 | 352 | 44 | 308 | 42 | NA | 600 | 0.3 | 22.9 | 1400000
2022-06-16 | 35580 | 35.58 | 7.25 | 7.64 | 159 | 23 | 364 | 36 | 316 | 34 | NA | 400 | 0.3 | 22.4 | 1200000
2022-06-17 | 38520 | 38.52 | 7.37 | 7.59 | 171 | 26 | 360 | 40 | 296 | 39 | NA | 500 | 0.2 | 23.4 | 1100000
2022-06-18 | 40050 | 40.05 | 7.3 | 7.56 | 165 | 26 | 368 | 36 | 304 | 32 | NA | 600 | 0.2 | 23.1 | 1400000
2022-06-19 | 36230 | 36.23 | 7.34 | 7.63 | 153 | 23 | 344 | 32 | 318 | 37 | NA | 700 | 0.3 | 23.8 | 1300000
2022-06-20 | 40460 | 40.46 | 7.42 | 7.61 | 159 | 25 | 360 | 44 | 301 | 40 | NA | 500 | 0.2 | 24.3 | 1700000
2022-06-21 | 35010 | 35.01 | 7.17 | 7.26 | 156 | 22 | 348 | 40 | 307 | 35 | NA | 400 | 0.3 | 23.9 | 1200000
2022-06-22 | 35600 | 35.6 | 7.28 | 7.42 | 157 | 24 | 340 | 36 | 284 | 42 | NA | 500 | 0.3 | 26.5 | 1100000
2022-06-23 | 37830 | 37.83 | 7.3 | 7.39 | 159 | 27 | 352 | 40 | 278 | 36 | NA | 600 | 0.2 | 24.8 | 1700000
2022-06-24 | 34130 | 34.13 | 7.31 | 7.35 | 162 | 26 | 344 | 32 | 298 | 35 | NA | 400 | 0.2 | 22.9 | 1400000
2022-06-25 | 40340 | 40.34 | 7.28 | 7.55 | 158 | 27 | 356 | 44 | 310 | 38 | NA | 500 | 0.2 | 23.2 | 1300000
2022-06-26 | 42140 | 42.14 | 7.59 | 7.71 | 153 | 29 | 352 | 48 | 306 | 44 | NA | 700 | 0.3 | 23.8 | 1700000
2022-06-27 | 44230 | 44.23 | 7.21 | 7.31 | 149 | 32 | 356 | 52 | 309 | 48 | NA | 700 | 0.2 | 22.7 | 1400000
2022-06-28 | 44880 | 44.88 | 7.41 | 7.54 | 153 | 34 | 364 | 56 | 322 | 49 | NA | 800 | 0.2 | 23.8 | 1600000
2022-06-29 | 45390 | 45.39 | 7.32 | 7.53 | 152 | 35 | 360 | 52 | 310 | 48 | NA | 700 | 0.3 | 22.4 | 1300000
2022-06-30 | 40160 | 40.16 | 7.46 | 7.6 | 153 | 30 | 352 | 48 | 314 | 46 | NA | 600 | 0.2 | 24.1 | 1700000
Average | 39143.3333 | 39.1433 | 7.3843 | 7.5367 | 159.3 | 27.0667 | 356.2667 | 42.1333 | 308.0667 | 40.5 | NA | 596.6667 | 0.24333 | 23.4667 | 1410000
1174.3
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 33610 | 33.61 | 7.17 | 7.26 | 149 | 22 | 340 | 32 | 278 | 32 |  | 400 | 0.2 | 21.3 | 1100000
Max | 45390 | 45.39 | 7.59 | 7.71 | 174 | 35 | 368 | 56 | 334 | 49 |  | 800 | 0.3 | 26.5 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-06-01 | 26870 | 26.87 | 7.21 | 7.53 | 140 | 12 | 308 | 40 | 265 | 17 | NA | 600 | 0.3 | 23.48 | 1300000
2022-06-02 | 27230 | 27.23 | 7.17 | 7.46 | 136 | 11 | 316 | 36 | 274 | 18 | NA | 700 | 0.2 | 22.71 | 1400000
2022-06-03 | 26560 | 26.56 | 7.25 | 7.58 | 143 | 13 | 312 | 40 | 268 | 16 | NA | 500 | 0.3 | 23.07 | 1200000
2022-06-04 | 26130 | 26.13 | 7.2 | 7.51 | 140 | 12 | 320 | 36 | 279 | 17 | NA | 600 | 0.2 | 22.55 | 1300000
2022-06-05 | 27860 | 27.86 | 7.28 | 7.62 | 146 | 13 | 308 | 32 | 272 | 19 | NA | 400 | 0.3 | 23.2 | 1600000
2022-06-06 | 26810 | 26.81 | 7.18 | 7.56 | 136 | 12 | 312 | 36 | 266 | 18 | NA | 700 | 0.2 | 23.45 | 1400000
2022-06-07 | 26330 | 26.33 | 7.24 | 7.66 | 149 | 14 | 324 | 40 | 282 | 17 | NA | 500 | 0.2 | 22.84 | 1300000
2022-06-08 | 25850 | 25.85 | 7.13 | 7.55 | 143 | 13 | 316 | 36 | 274 | 19 | NA | 400 | 0.3 | 23.18 | 1200000
2022-06-09 | 27140 | 27.14 | 7.19 | 7.62 | 140 | 11 | 308 | 40 | 279 | 18 | NA | 600 | 0.2 | 24.09 | 1400000
2022-06-10 | 27930 | 27.93 | 7.26 | 7.58 | 146 | 12 | 320 | 36 | 268 | 20 | NA | 700 | 0.3 | 23.64 | 1300000
2022-06-11 | 27760 | 27.76 | 7.17 | 7.65 | 136 | 11 | 312 | 32 | 282 | 17 | NA | 400 | 0.2 | 23.26 | 1600000
2022-06-12 | 27410 | 27.41 | 7.22 | 7.54 | 145 | 13 | 324 | 40 | 275 | 19 | NA | 500 | 0.3 | 22.98 | 1200000
2022-06-13 | 28080 | 28.08 | 7.29 | 7.61 | 140 | 12 | 316 | 44 | 269 | 18 | NA | 700 | 0.2 | 23.55 | 1400000
2022-06-14 | 27320 | 27.32 | 7.18 | 7.57 | 133 | 11 | 308 | 36 | 272 | 20 | NA | 400 | 0.3 | 22.71 | 1300000
2022-06-15 | 26390 | 26.39 | 7.26 | 7.69 | 146 | 13 | 320 | 40 | 258 | 17 | NA | 500 | 0.2 | 23.11 | 1600000
2022-06-16 | 27450 | 27.45 | 7.21 | 7.62 | 140 | 12 | 312 | 36 | 266 | 19 | NA | 600 | 0.2 | 23.74 | 1400000
2022-06-17 | 26870 | 26.87 | 7.31 | 7.72 | 149 | 14 | 324 | 32 | 276 | 18 | NA | 700 | 0.3 | 22.61 | 1300000
2022-06-18 | 26620 | 26.62 | 7.27 | 7.66 | 143 | 11 | 316 | 40 | 264 | 20 | NA | 400 | 0.2 | 23.04 | 1200000
2022-06-19 | 28560 | 28.56 | 7.19 | 7.59 | 156 | 14 | 320 | 36 | 269 | 17 | NA | 600 | 0.3 | 23.41 | 1300000
2022-06-20 | 28790 | 28.79 | 7.24 | 7.63 | 146 | 12 | 308 | 40 | 281 | 19 | NA | 500 | 0.2 | 22.86 | 1200000
2022-06-21 | 26670 | 26.67 | 7.32 | 7.68 | 140 | 11 | 316 | 32 | 274 | 21 | NA | 700 | 0.2 | 23.16 | 1400000
2022-06-22 | 26230 | 26.23 | 7.21 | 7.55 | 143 | 13 | 304 | 36 | 279 | 18 | NA | 500 | 0.3 | 23.48 | 1600000
2022-06-23 | 27050 | 27.05 | 7.17 | 7.59 | 136 | 12 | 312 | 40 | 265 | 20 | NA | 400 | 0.2 | 22.72 | 1200000
2022-06-24 | 27190 | 27.19 | 7.27 | 7.52 | 146 | 13 | 308 | 36 | 275 | 19 | NA | 600 | 0.3 | 22.49 | 1400000
2022-06-25 | 28320 | 28.32 | 7.22 | 7.48 | 140 | 14 | 316 | 40 | 258 | 17 | NA | 700 | 0.2 | 23.22 | 1300000
2022-06-26 | 26750 | 26.75 | 7.34 | 7.62 | 136 | 11 | 324 | 44 | 268 | 20 | NA | 500 | 0.3 | 23.63 | 1200000
2022-06-27 | 26910 | 26.91 | 7.26 | 7.58 | 143 | 12 | 312 | 36 | 263 | 18 | NA | 400 | 0.3 | 22.75 | 1600000
2022-06-28 | 26870 | 26.87 | 7.19 | 7.53 | 153 | 14 | 320 | 40 | 272 | 19 | NA | 700 | 0.2 | 23.65 | 1400000
2022-06-29 | 26460 | 26.46 | 7.29 | 7.64 | 149 | 13 | 308 | 32 | 276 | 17 | NA | 500 | 0.3 | 23.33 | 1200000
2022-06-30 | 32130 | 32.13 | 7.24 | 7.59 | 156 | 14 | 316 | 36 | 267 | 20 | NA | 600 | 0.2 | 23.78 | 1300000
Average | 27284.6667 | 27.2847 | 7.232 | 7.591 | 143.1667 | 12.4333 | 314.6667 | 37.3333 | 271.2 | 18.4 | NA | 553.3333 | 0.24667 | 23.1897 | 1350000
818.54
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 25850 | 25.85 | 7.13 | 7.46 | 133 | 11 | 304 | 32 | 258 | 16 |  | 400 | 0.2 | 22.49 | 1200000
Max | 32130 | 32.13 | 7.34 | 7.72 | 156 | 14 | 324 | 44 | 282 | 21 |  | 700 | 0.3 | 24.09 | 1600000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-06-01 | 13840 | 13.84 | 7.15 | 7.46 | 130 | 16 | 304 | 40 | 268 | 22 | NA | 700 | 0.3 | 22.52 | 1400000
2022-06-02 | 12610 | 12.61 | 7.22 | 7.58 | 138 | 15 | 320 | 36 | 253 | 20 | NA | 600 | 0.2 | 23.18 | 1200000
2022-06-03 | 12690 | 12.69 | 7.31 | 7.67 | 135 | 17 | 312 | 44 | 276 | 23 | NA | 500 | 0.3 | 22.76 | 1600000
2022-06-04 | 12620 | 12.62 | 7.26 | 7.53 | 142 | 15 | 324 | 40 | 261 | 21 | NA | 700 | 0.2 | 21.86 | 1300000
2022-06-05 | 14090 | 14.09 | 7.18 | 7.41 | 146 | 14 | 316 | 36 | 248 | 24 | NA | 400 | 0.2 | 22.14 | 1700000
2022-06-06 | 13280 | 13.28 | 7.25 | 7.56 | 140 | 15 | 300 | 40 | 274 | 22 | NA | 500 | 0.3 | 20.61 | 1400000
2022-06-07 | 13800 | 13.8 | 7.34 | 7.61 | 135 | 16 | 308 | 44 | 259 | 25 | NA | 600 | 0.2 | 21.46 | 1600000
2022-06-08 | 13490 | 13.49 | 7.21 | 7.49 | 144 | 14 | 320 | 36 | 269 | 21 | NA | 700 | 0.2 | 22.25 | 1300000
2022-06-09 | 13180 | 13.18 | 7.28 | 7.66 | 138 | 15 | 304 | 40 | 256 | 23 | NA | 500 | 0.3 | 21.57 | 1400000
2022-06-10 | 13160 | 13.16 | 7.17 | 7.57 | 145 | 13 | 312 | 36 | 271 | 22 | NA | 600 | 0.2 | 22.68 | 1200000
2022-06-11 | 14110 | 14.11 | 7.24 | 7.68 | 136 | 14 | 332 | 32 | 283 | 20 | NA | 400 | 0.3 | 21.74 | 1700000
2022-06-12 | 13010 | 13.01 | 7.16 | 7.51 | 140 | 13 | 316 | 36 | 277 | 23 | NA | 500 | 0.2 | 22.46 | 1300000
2022-06-13 | 13880 | 13.88 | 7.23 | 7.48 | 135 | 15 | 300 | 40 | 266 | 21 | NA | 600 | 0.2 | 23.16 | 1600000
2022-06-14 | 14140 | 14.14 | 7.15 | 7.43 | 144 | 14 | 320 | 36 | 258 | 24 | NA | 400 | 0.3 | 21.94 | 1200000
2022-06-15 | 13110 | 13.11 | 7.27 | 7.55 | 138 | 16 | 308 | 40 | 270 | 22 | NA | 700 | 0.2 | 22.53 | 1400000
2022-06-16 | 13000 | 13 | 7.19 | 7.48 | 146 | 15 | 316 | 36 | 264 | 20 | NA | 600 | 0.3 | 23.24 | 1300000
2022-06-17 | 14900 | 14.9 | 7.24 | 7.59 | 150 | 17 | 312 | 40 | 275 | 23 | NA | 500 | 0.2 | 22.84 | 1700000
2022-06-18 | 13570 | 13.57 | 7.18 | 7.63 | 142 | 14 | 304 | 36 | 268 | 21 | NA | 600 | 0.2 | 21.78 | 1400000
2022-06-19 | 15320 | 15.32 | 7.28 | 7.56 | 155 | 16 | 324 | 44 | 281 | 24 | NA | 700 | 0.3 | 22.17 | 1600000
2022-06-20 | 13960 | 13.96 | 7.22 | 7.41 | 145 | 15 | 308 | 40 | 276 | 22 | NA | 600 | 0.2 | 21.88 | 1300000
2022-06-21 | 13380 | 13.38 | 7.31 | 7.68 | 158 | 17 | 332 | 44 | 261 | 23 | NA | 500 | 0.3 | 22.54 | 1200000
2022-06-22 | 13570 | 13.57 | 7.26 | 7.46 | 152 | 15 | 324 | 40 | 280 | 25 | NA | 600 | 0.2 | 23.21 | 1400000
2022-06-23 | 13330 | 13.33 | 7.21 | 7.54 | 140 | 14 | 304 | 36 | 271 | 23 | NA | 400 | 0.3 | 21.96 | 1700000
2022-06-24 | 12830 | 12.83 | 7.33 | 7.61 | 146 | 15 | 316 | 40 | 286 | 21 | NA | 500 | 0.2 | 22.48 | 1600000
2022-06-25 | 12130 | 12.13 | 7.25 | 7.58 | 135 | 14 | 300 | 36 | 265 | 22 | NA | 600 | 0.2 | 23.4 | 1300000
2022-06-26 | 13730 | 13.73 | 7.16 | 7.49 | 143 | 15 | 312 | 40 | 277 | 24 | NA | 700 | 0.3 | 22.77 | 1200000
2022-06-27 | 14300 | 14.3 | 7.37 | 7.63 | 140 | 14 | 320 | 44 | 288 | 26 | NA | 600 | 0.2 | 21.38 | 1700000
2022-06-28 | 13950 | 13.95 | 7.29 | 7.55 | 146 | 16 | 308 | 40 | 269 | 23 | NA | 500 | 0.3 | 23.11 | 1400000
2022-06-29 | 13790 | 13.79 | 7.23 | 7.71 | 136 | 14 | 300 | 36 | 283 | 21 | NA | 400 | 0.3 | 22.56 | 1600000
2022-06-30 | 15120 | 15.12 | 7.31 | 7.65 | 140 | 15 | 312 | 40 | 274 | 25 | NA | 600 | 0.2 | 21.84 | 1300000
Average | 13596.3333 | 13.5963 | 7.2417 | 7.5587 | 142 | 14.9333 | 312.9333 | 38.9333 | 270.2333 | 22.5333 | NA | 560 | 0.24333 | 22.334 | 1433333.3333
407.89
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 12130 | 12.13 | 7.15 | 7.41 | 130 | 13 | 300 | 32 | 248 | 20 |  | 400 | 0.2 | 20.61 | 1200000
Max | 15320 | 15.32 | 7.37 | 7.71 | 158 | 17 | 332 | 44 | 288 | 26 |  | 700 | 0.3 | 23.4 | 1700000