## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-06-01 | 58500 | 58.5 | 7.22 | 7.8 | 145 | 15 | 324 | 36 | 215 | 24 | NA | 600 | 0.2 | 22.03 | 1100000
2024-06-02 | 58850 | 58.85 | 7.21 | 7.78 | 150 | 16 | 316 | 40 | 217 | 26 | NA | 400 | 0.3 | 21.82 | 1400000
2024-06-03 | 58000 | 58 | 7.22 | 7.74 | 145 | 15 | 312 | 44 | 216 | 25 | NA | 500 | 0.2 | 21.77 | 1300000
2024-06-04 | 57700 | 57.7 | 7.2 | 7.79 | 140 | 16 | 324 | 36 | 218 | 24 | NA | 700 | 0.3 | 21.67 | 1700000
2024-06-05 | 58950 | 58.95 | 7.21 | 7.73 | 145 | 15 | 320 | 40 | 217 | 27 | NA | 400 | 0.2 | 21.71 | 1300000
2024-06-06 | 57520 | 57.52 | 7.16 | 7.7 | 140 | 14 | 300 | 44 | 214 | 26 | NA | 500 | 0.3 | 22.93 | 1200000
2024-06-07 | 59700 | 59.7 | 7.17 | 7.74 | 150 | 16 | 312 | 40 | 217 | 24 | NA | 600 | 0.2 | 22.84 | 1100000
2024-06-08 | 58100 | 58.1 | 7.2 | 7.76 | 145 | 15 | 312 | 44 | 245 | 25 | NA | 400 | 0.3 | 22.81 | 1400000
2024-06-09 | 59600 | 59.6 | 7.16 | 7.71 | 150 | 14 | 316 | 36 | 218 | 26 | NA | 500 | 0.2 | 22.95 | 1100000
2024-06-10 | 55770 | 55.77 | 7.18 | 7.74 | 145 | 16 | 320 | 40 | 248 | 26 | NA | 600 | 0.3 | 21.91 | 1100000
2024-06-11 | 59750 | 59.75 | 7.21 | 7.8 | 140 | 15 | 324 | 44 | 218 | 25 | NA | 700 | 0.2 | 22.2 | 1700000
2024-06-12 | 59680 | 59.68 | 7.16 | 7.77 | 145 | 17 | 308 | 40 | 216 | 26 | NA | 500 | 0.3 | 22.98 | 1400000
2024-06-13 | 56150 | 56.15 | 7.19 | 7.78 | 145 | 16 | 312 | 44 | 254 | 27 | NA | 700 | 0.2 | 23.15 | 1300000
2024-06-14 | 59200 | 59.2 | 7.3 | 7.7 | 150 | 15 | 324 | 36 | 244 | 24 | NA | 400 | 0.2 | 22.71 | 1100000
2024-06-15 | 57600 | 57.6 | 7.28 | 7.8 | 145 | 16 | 332 | 40 | 264 | 25 | NA | 600 | 0.3 | 22.93 | 1200000
2024-06-16 | 58320 | 58.32 | 7.17 | 7.72 | 150 | 15 | 328 | 44 | 273 | 28 | NA | 500 | 0.3 | 22.72 | 1300000
2024-06-17 | 60160 | 60.16 | 7.26 | 7.73 | 145 | 16 | 340 | 40 | 280 | 26 | NA | 700 | 0.3 | 22.95 | 1400000
2024-06-18 | 58400 | 58.4 | 7.3 | 7.76 | 150 | 15 | 332 | 44 | 260 | 25 | NA | 600 | 0.2 | 22.59 | 1700000
2024-06-19 | 60020 | 60.02 | 7.28 | 7.74 | 145 | 16 | 336 | 40 | 266 | 24 | NA | 400 | 0.3 | 22.8 | 1200000
2024-06-20 | 57050 | 57.05 | 7.24 | 7.78 | 150 | 15 | 328 | 40 | 261 | 25 | NA | 500 | 0.3 | 22.77 | 1100000
2024-06-21 | 60150 | 60.15 | 7.26 | 7.8 | 135 | 14 | 344 | 36 | 259 | 24 | NA | 700 | 0.2 | 23.22 | 1700000
2024-06-22 | 52330 | 52.33 | 7.22 | 7.72 | 145 | 16 | 328 | 44 | 262 | 25 | NA | 600 | 0.3 | 23.03 | 1100000
2024-06-23 | 59430 | 59.43 | 7.24 | 7.78 | 150 | 15 | 332 | 40 | 260 | 26 | NA | 400 | 0.2 | 22.63 | 1200000
2024-06-24 | 59120 | 59.12 | 7.26 | 7.73 | 145 | 16 | 324 | 40 | 268 | 24 | NA | 500 | 0.3 | 23.1 | 1700000
2024-06-25 | 57990 | 57.99 | 7.21 | 7.76 | 135 | 15 | 328 | 44 | 279 | 25 | NA | 700 | 0.2 | 23.03 | 1400000
2024-06-26 | 54460 | 54.46 | 7.22 | 7.77 | 130 | 14 | 300 | 36 | 294 | 24 | NA | 600 | 0.3 | 22.96 | 1200000
2024-06-27 | 57700 | 57.7 | 7.24 | 7.79 | 140 | 15 | 308 | 40 | 281 | 28 | NA | 500 | 0.2 | 22.91 | 1100000
2024-06-28 | 61000 | 61 | 7.21 | 7.81 | 150 | 18 | 304 | 44 | 278 | 27 | NA | 600 | 0.3 | 22.69 | 1700000
2024-06-29 | 57840 | 57.84 | 7.18 | 7.72 | 135 | 16 | 320 | 40 | 288 | 26 | NA | 400 | 0.2 | 22.82 | 1400000
2024-06-30 | 57450 | 57.45 | 7.23 | 7.76 | 130 | 17 | 300 | 40 | 260 | 25 | NA | 500 | 0.2 | 23.56 | 1200000
Average | 58216.3333 | 58.2163 | 7.2197 | 7.757 | 143.8333 | 15.4667 | 320.2667 | 40.5333 | 249.6667 | 25.4 |  | 543.3333 | 0.25 | 22.673 | 1326666.6667
1746.49
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 52330 | 52.33 | 7.16 | 7.7 | 130 | 14 | 300 | 36 | 214 | 24 |  | 400 | 0.2 | 21.67 | 1100000
Max | 61000 | 61 | 7.3 | 7.81 | 150 | 18 | 344 | 44 | 294 | 28 |  | 700 | 0.3 | 23.56 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-06-01 | 37940 | 37.94 | 7.21 | 7.75 | 160 | 25 | 360 | 44 | 326 | 38 | NA | 700 | 0.3 | 23.97 | 1700000
2024-06-02 | 37180 | 37.18 | 7.27 | 7.74 | 165 | 23 | 372 | 40 | 336 | 36 | NA | 600 | 0.3 | 24.38 | 1400000
2024-06-03 | 33520 | 33.52 | 7.38 | 7.7 | 155 | 24 | 364 | 44 | 321 | 42 | NA | 400 | 0.3 | 23.49 | 1300000
2024-06-04 | 35410 | 35.41 | 7.64 | 7.79 | 150 | 26 | 368 | 40 | 344 | 39 | NA | 700 | 0.3 | 24.48 | 1400000
2024-06-05 | 34900 | 34.9 | 7.87 | 7.94 | 160 | 27 | 340 | 40 | 323 | 34 | NA | 600 | 0.3 | 23.02 | 1100000
2024-06-06 | 35750 | 35.75 | 8.22 | 7.8 | 155 | 26 | 352 | 36 | 367 | 33 | NA | 500 | 0.3 | 25.03 | 1400000
2024-06-07 | 35280 | 35.28 | 8.31 | 7.86 | 165 | 23 | 356 | 40 | 362 | 35 | NA | 700 | 0.3 | 23.48 | 1700000
2024-06-08 | 34460 | 34.46 | 7.99 | 7.82 | 160 | 24 | 344 | 44 | 331 | 38 | NA | 600 | 0.3 | 23.02 | 1400000
2024-06-09 | 35100 | 35.1 | 7.97 | 7.81 | 155 | 22 | 360 | 40 | 367 | 35 | NA | 400 | 0.3 | 24.41 | 1300000
2024-06-10 | 35860 | 35.86 | 7.83 | 7.9 | 150 | 22 | 364 | 36 | 323 | 34 | NA | 500 | 0.3 | 25.68 | 1700000
2024-06-11 | 33170 | 33.17 | 7.51 | 7.69 | 155 | 23 | 352 | 40 | 365 | 33 | NA | 700 | 0.3 | 25.42 | 1300000
2024-06-12 | 36190 | 36.19 | 7.39 | 7.74 | 165 | 24 | 360 | 44 | 344 | 44 | NA | 600 | 0.3 | 24.02 | 1200000
2024-06-13 | 36780 | 36.78 | 7.48 | 7.64 | 165 | 23 | 356 | 40 | 319 | 45 | NA | 400 | 0.3 | 23.76 | 1100000
2024-06-14 | 36050 | 36.05 | 7.39 | 7.56 | 155 | 23 | 344 | 44 | 337 | 40 | NA | 500 | 0.3 | 22.59 | 1400000
2024-06-15 | 33520 | 33.52 | 7.4 | 7.67 | 160 | 21 | 360 | 36 | 357 | 34 | NA | 700 | 0.3 | 23.97 | 1400000
2024-06-16 | 33310 | 33.31 | 7.36 | 7.62 | 165 | 22 | 368 | 40 | 362 | 40 | NA | 500 | 0.3 | 23.7 | 1100000
2024-06-17 | 35620 | 35.62 | 7.29 | 7.6 | 160 | 23 | 364 | 36 | 359 | 35 | NA | 400 | 0.3 | 22.87 | 1300000
2024-06-18 | 37200 | 37.2 | 7.26 | 7.76 | 155 | 21 | 352 | 40 | 321 | 39 | NA | 700 | 0.3 | 24.73 | 1700000
2024-06-19 | 37130 | 37.13 | 7.41 | 7.65 | 160 | 22 | 360 | 36 | 315 | 34 | NA | 500 | 0.3 | 25.14 | 1400000
2024-06-20 | 39340 | 39.34 | 7.32 | 7.58 | 160 | 23 | 356 | 40 | 333 | 39 | NA | 700 | 0.3 | 22.73 | 1300000
2024-06-21 | 38720 | 38.72 | 7.39 | 7.71 | 155 | 22 | 352 | 44 | 354 | 44 | NA | 600 | 0.3 | 24.75 | 1700000
2024-06-22 | 36100 | 36.1 | 7.26 | 7.51 | 165 | 23 | 336 | 48 | 303 | 43 | NA | 400 | 0.3 | 23.97 | 1100000
2024-06-23 | 36680 | 36.68 | 7.42 | 7.58 | 160 | 21 | 344 | 40 | 336 | 36 | NA | 500 | 0.3 | 23 | 1400000
2024-06-24 | 37320 | 37.32 | 7.61 | 7.65 | 160 | 22 | 312 | 44 | 340 | 38 | NA | 500 | 0.3 | 23.3 | 1400000
2024-06-25 | 35270 | 35.27 | 6.95 | 7.68 | 155 | 19 | 324 | 36 | 289 | 31 | NA | 600 | 0.3 | 23.61 | 1300000
2024-06-26 | 37470 | 37.47 | 7.23 | 7.62 | 160 | 23 | 332 | 40 | 315 | 33 | NA | 700 | 0.3 | 23.66 | 1700000
2024-06-27 | 37550 | 37.55 | 7.16 | 7.69 | 145 | 22 | 336 | 40 | 329 | 32 | NA | 400 | 0.3 | 24.66 | 1200000
2024-06-28 | 36240 | 36.24 | 7.05 | 7.64 | 150 | 22 | 344 | 36 | 338 | 35 | NA | 500 | 0.3 | 24.52 | 1400000
2024-06-29 | 37670 | 37.67 | 7.09 | 7.68 | 155 | 21 | 328 | 40 | 305 | 36 | NA | 600 | 0.3 | 23.71 | 1300000
2024-06-30 | 37980 | 37.98 | 7.26 | 7.64 | 150 | 22 | 340 | 36 | 323 | 33 | NA | 400 | 0.3 | 24.88 | 1100000
Average | 36157 | 36.157 | 7.464 | 7.7007 | 157.6667 | 22.8 | 350 | 40.1333 | 334.8 | 36.9333 |  | 553.3333 | 0.3 | 23.9983 | 1373333.3333
1084.71
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 33170 | 33.17 | 6.95 | 7.51 | 145 | 19 | 312 | 36 | 289 | 31 |  | 400 | 0.3 | 22.59 | 1100000
Max | 39340 | 39.34 | 8.31 | 7.94 | 165 | 27 | 372 | 48 | 367 | 45 |  | 700 | 0.3 | 25.68 | 1700000

## Kodra
kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-06-01 | 30460 | 30.46 | 7.16 | 7.38 | 140 | 13 | 332 | 40 | 304 | 15 | NA | 500 | 0.3 | 23.68 | 1200000
2024-06-02 | 29930 | 29.93 | 7.19 | 7.36 | 135 | 14 | 328 | 36 | 294 | 16 | NA | 800 | 0.3 | 22.74 | 1300000
2024-06-03 | 30180 | 30.18 | 7.16 | 7.37 | 130 | 13 | 320 | 40 | 288 | 16 | NA | 500 | 0.3 | 24.8 | 1100000
2024-06-04 | 30340 | 30.34 | 7.03 | 7.39 | 145 | 14 | 324 | 40 | 291 | 17 | NA | 400 | 0.3 | 22.88 | 1400000
2024-06-05 | 28640 | 28.64 | 6.93 | 7.4 | 130 | 15 | 332 | 44 | 274 | 16 | NA | 600 | 0.3 | 22.97 | 1200000
2024-06-06 | 28270 | 28.27 | 6.92 | 7.34 | 145 | 14 | 344 | 40 | 287 | 17 | NA | 700 | 0.3 | 21.72 | 1300000
2024-06-07 | 31190 | 31.19 | 7.02 | 7.42 | 140 | 15 | 336 | 44 | 290 | 16 | NA | 500 | 0.3 | 23.16 | 1200000
2024-06-08 | 29650 | 29.65 | 7.11 | 7.35 | 130 | 16 | 312 | 40 | 276 | 15 | NA | 400 | 0.3 | 22.37 | 1400000
2024-06-09 | 30780 | 30.78 | 7.05 | 7.43 | 135 | 12 | 324 | 36 | 282 | 16 | NA | 700 | 0.2 | 22.04 | 1100000
2024-06-10 | 29360 | 29.36 | 7.03 | 7.39 | 140 | 13 | 332 | 40 | 294 | 17 | NA | 600 | 0.2 | 21.75 | 1300000
2024-06-11 | 30250 | 30.25 | 6.92 | 7.34 | 135 | 15 | 316 | 44 | 287 | 16 | NA | 500 | 0.3 | 23.6 | 1400000
2024-06-12 | 30790 | 30.79 | 7.1 | 7.48 | 140 | 14 | 328 | 40 | 301 | 17 | NA | 600 | 0.3 | 22.38 | 1700000
2024-06-13 | 30290 | 30.29 | 7.23 | 7.42 | 135 | 14 | 316 | 36 | 279 | 18 | NA | 400 | 0.3 | 24.36 | 1200000
2024-06-14 | 29130 | 29.13 | 7.21 | 7.32 | 130 | 13 | 304 | 40 | 275 | 17 | NA | 500 | 0.3 | 24.69 | 1100000
2024-06-15 | 29900 | 29.9 | 7.19 | 7.28 | 145 | 15 | 324 | 40 | 298 | 16 | NA | 700 | 0.3 | 23.31 | 1300000
2024-06-16 | 30760 | 30.76 | 7.31 | 7.4 | 135 | 16 | 316 | 44 | 286 | 17 | NA | 600 | 0.3 | 23.6 | 1400000
2024-06-17 | 30630 | 30.63 | 7.26 | 7.42 | 130 | 11 | 308 | 32 | 282 | 16 | NA | 400 | 0.2 | 22.76 | 1700000
2024-06-18 | 28770 | 28.77 | 7.32 | 7.27 | 140 | 12 | 316 | 36 | 294 | 15 | NA | 500 | 0.2 | 23.48 | 1200000
2024-06-19 | 30090 | 30.09 | 7.13 | 7.28 | 135 | 13 | 312 | 36 | 284 | 17 | NA | 800 | 0.2 | 24.06 | 1400000
2024-06-20 | 31660 | 31.66 | 7.12 | 7.26 | 140 | 14 | 328 | 40 | 289 | 16 | NA | 700 | 0.3 | 22.1 | 1700000
2024-06-21 | 29760 | 29.76 | 7.27 | 7.31 | 130 | 16 | 336 | 44 | 297 | 17 | NA | 400 | 0.3 | 23.58 | 1300000
2024-06-22 | 32310 | 32.31 | 7.24 | 7.3 | 135 | 12 | 324 | 36 | 290 | 16 | NA | 600 | 0.2 | 21.91 | 1200000
2024-06-23 | 31350 | 31.35 | 7.19 | 7.34 | 150 | 13 | 340 | 40 | 308 | 18 | NA | 700 | 0.3 | 23.15 | 1400000
2024-06-24 | 32280 | 32.28 | 7.39 | 7.36 | 135 | 12 | 332 | 36 | 296 | 17 | NA | 400 | 0.2 | 24.29 | 1700000
2024-06-25 | 31450 | 31.45 | 7.22 | 7.16 | 140 | 13 | 348 | 40 | 305 | 16 | NA | 500 | 0.3 | 24.54 | 1300000
2024-06-26 | 27120 | 27.12 | 6.92 | 7.13 | 140 | 14 | 324 | 44 | 296 | 17 | NA | 700 | 0.3 | 23.96 | 1100000
2024-06-27 | 29890 | 29.89 | 6.93 | 7.41 | 145 | 13 | 332 | 36 | 287 | 16 | NA | 500 | 0.3 | 23.96 | 1400000
2024-06-28 | 28110 | 28.11 | 7.02 | 7.34 | 150 | 16 | 348 | 44 | 315 | 17 | NA | 600 | 0.3 | 25.05 | 1700000
2024-06-29 | 28400 | 28.4 | 6.83 | 7.54 | 140 | 12 | 328 | 36 | 290 | 16 | NA | 800 | 0.2 | 24.76 | 1400000
2024-06-30 | 30480 | 30.48 | 6.81 | 7.6 | 150 | 13 | 340 | 40 | 306 | 15 | NA | 400 | 0.2 | 23.63 | 1300000
Average | 30074 | 30.074 | 7.107 | 7.3597 | 138.3333 | 13.6667 | 326.8 | 39.4667 | 291.5 | 16.3667 |  | 566.6667 | 0.27 | 23.376 | 1346666.6667
902.22
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 27120 | 27.12 | 6.81 | 7.13 | 130 | 11 | 304 | 32 | 274 | 15 |  | 400 | 0.2 | 21.72 | 1100000
Max | 32310 | 32.31 | 7.39 | 7.6 | 150 | 16 | 348 | 44 | 315 | 18 |  | 800 | 0.3 | 25.05 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-06-01 | 13530 | 13.53 | 7.52 | 7.69 | 140 | 15 | 308 | 40 | 238 | 27 | NA | 600 | 0.3 | 23.52 | 1400000
2024-06-02 | 12250 | 12.25 | 7.46 | 7.66 | 135 | 17 | 300 | 36 | 224 | 26 | NA | 500 | 0.2 | 21.8 | 1200000
2024-06-03 | 13350 | 13.35 | 7.42 | 7.69 | 130 | 16 | 296 | 36 | 232 | 27 | NA | 700 | 0.3 | 22.76 | 1300000
2024-06-04 | 13720 | 13.72 | 7.34 | 7.64 | 155 | 17 | 304 | 40 | 256 | 25 | NA | 800 | 0.3 | 23.02 | 1700000
2024-06-05 | 14020 | 14.02 | 7.59 | 7.72 | 125 | 15 | 300 | 36 | 241 | 26 | NA | 600 | 0.3 | 21.95 | 1100000
2024-06-06 | 13590 | 13.59 | 7.66 | 7.65 | 140 | 16 | 292 | 40 | 240 | 28 | NA | 400 | 0.2 | 22.69 | 1300000
2024-06-07 | 13010 | 13.01 | 7.7 | 7.63 | 135 | 17 | 284 | 36 | 233 | 29 | NA | 500 | 0.3 | 23.38 | 1200000
2024-06-08 | 13620 | 13.62 | 7.58 | 7.66 | 130 | 16 | 296 | 40 | 242 | 26 | NA | 700 | 0.2 | 23.06 | 1700000
2024-06-09 | 14030 | 14.03 | 7.46 | 7.7 | 140 | 15 | 304 | 36 | 249 | 24 | NA | 600 | 0.3 | 23.82 | 1200000
2024-06-10 | 13130 | 13.13 | 7.58 | 7.67 | 145 | 16 | 312 | 36 | 244 | 27 | NA | 500 | 0.2 | 22.57 | 1300000
2024-06-11 | 13200 | 13.2 | 7.63 | 7.69 | 150 | 17 | 300 | 40 | 256 | 28 | NA | 400 | 0.3 | 22.01 | 1400000
2024-06-12 | 14200 | 14.2 | 7.67 | 7.73 | 140 | 15 | 308 | 32 | 259 | 24 | NA | 700 | 0.2 | 23.16 | 1100000
2024-06-13 | 13450 | 13.45 | 7.54 | 7.68 | 150 | 16 | 296 | 40 | 228 | 28 | NA | 600 | 0.2 | 23.4 | 1700000
2024-06-14 | 13170 | 13.17 | 7.58 | 7.75 | 135 | 15 | 288 | 32 | 223 | 25 | NA | 500 | 0.3 | 22.6 | 1200000
2024-06-15 | 13310 | 13.31 | 7.67 | 7.78 | 145 | 17 | 312 | 36 | 247 | 26 | NA | 400 | 0.2 | 24.13 | 1300000
2024-06-16 | 12120 | 12.12 | 7.63 | 7.76 | 150 | 18 | 304 | 44 | 253 | 27 | NA | 700 | 0.3 | 22.33 | 1100000
2024-06-17 | 12310 | 12.31 | 7.56 | 7.73 | 145 | 16 | 308 | 40 | 256 | 28 | NA | 600 | 0.2 | 23.18 | 1700000
2024-06-18 | 6730 | 6.73 | 7.67 | 7.77 | 140 | 17 | 300 | 36 | 242 | 28 | NA | 500 | 0.3 | 22.03 | 1300000 | From 18.06.2024 to 20.06.2024: Aeration Tank no. 1 is under shut down for maintenance of diffusers
2024-06-19 | 6760 | 6.76 | 7.66 | 7.79 | 135 | 15 | 312 | 32 | 262 | 27 | NA | 400 | 0.2 | 23.78 | 1200000
2024-06-20 | 10940 | 10.94 | 7.64 | 7.78 | 145 | 14 | 308 | 32 | 268 | 23 | NA | 700 | 0.2 | 21.72 | 1400000
2024-06-21 | 11990 | 11.99 | 7.63 | 7.76 | 140 | 16 | 304 | 36 | 247 | 28 | NA | 800 | 0.2 | 23.61 | 1200000 | From 21.06.2024 to 23.06.2024: Aeration Tank no. 2 is under shut down for maintenance of diffusers
2024-06-22 | 14570 | 14.57 | 7.54 | 7.78 | 135 | 17 | 288 | 40 | 224 | 25 | NA | 500 | 0.3 | 22.19 | 1700000
2024-06-23 | 12630 | 12.63 | 7.59 | 7.75 | 150 | 15 | 300 | 36 | 241 | 23 | NA | 600 | 0.3 | 22.46 | 1400000
2024-06-24 | 12290 | 12.29 | 7.67 | 7.72 | 145 | 18 | 292 | 44 | 228 | 27 | NA | 700 | 0.3 | 23.63 | 1200000
2024-06-25 | 13220 | 13.22 | 7.66 | 7.74 | 130 | 16 | 268 | 32 | 205 | 24 | NA | 400 | 0.2 | 24.32 | 1300000
2024-06-26 | 13130 | 13.13 | 7.64 | 7.76 | 135 | 17 | 284 | 40 | 216 | 26 | NA | 500 | 0.3 | 22.86 | 1100000
2024-06-27 | 13180 | 13.18 | 7.62 | 7.73 | 125 | 16 | 296 | 36 | 246 | 24 | NA | 600 | 0.3 | 23.18 | 1700000
2024-06-28 | 13070 | 13.07 | 7.59 | 7.77 | 130 | 15 | 288 | 32 | 214 | 23 | NA | 700 | 0.2 | 22.84 | 1400000
2024-06-29 | 13010 | 13.01 | 7.57 | 7.72 | 125 | 16 | 300 | 40 | 232 | 24 | NA | 400 | 0.2 | 21.52 | 1200000
2024-06-30 | 14180 | 14.18 | 7.52 | 7.75 | 130 | 17 | 304 | 44 | 244 | 28 | NA | 800 | 0.3 | 23.09 | 1100000
Average | 12723.6667 | 12.7237 | 7.5863 | 7.7217 | 138.5 | 16.1 | 298.5333 | 37.3333 | 239.6667 | 26.0333 |  | 580 | 0.25333 | 22.887 | 1336666.6667
381.71
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 6730 | 6.73 | 7.34 | 7.63 | 125 | 14 | 268 | 32 | 205 | 23 |  | 400 | 0.2 | 21.52 | 1100000
Max | 14570 | 14.57 | 7.7 | 7.79 | 155 | 18 | 312 | 44 | 268 | 29 |  | 800 | 0.3 | 24.32 | 1700000