## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-03-01 | 60920 | 60.92 | 7.28 | 7.72 | 135 | 17 | 312 | 36 | 288 | 23 | NA | 400 | 0.3 | 23.5 | 1300000
2023-03-02 | 62480 | 62.48 | 7.24 | 7.76 | 150 | 16 | 324 | 40 | 294 | 24 | NA | 600 | 0.2 | 24.47 | 1400000
2023-03-03 | 62510 | 62.51 | 7.27 | 7.74 | 140 | 14 | 328 | 36 | 276 | 22 | NA | 700 | 0.2 | 23.78 | 1700000
2023-03-04 | 58610 | 58.61 | 7.21 | 7.69 | 150 | 15 | 320 | 40 | 292 | 25 | NA | 500 | 0.3 | 23.69 | 1400000
2023-03-05 | 59110 | 59.11 | 7.28 | 7.74 | 140 | 15 | 336 | 40 | 288 | 21 | NA | 400 | 0.3 | 23.5 | 1700000
2023-03-06 | 59180 | 59.18 | 7.22 | 7.71 | 145 | 18 | 320 | 44 | 298 | 26 | NA | 600 | 0.3 | 24.82 | 1300000
2023-03-07 | 59500 | 59.5 | 7.18 | 7.78 | 130 | 17 | 328 | 36 | 284 | 24 | NA | 500 | 0.3 | 23.78 | 1400000
2023-03-08 | 61860 | 61.86 | 7.21 | 7.72 | 145 | 15 | 324 | 40 | 298 | 29 | NA | 700 | 0.2 | 24.04 | 1300000
2023-03-09 | 58650 | 58.65 | 7.26 | 7.71 | 135 | 14 | 312 | 36 | 288 | 25 | NA | 600 | 0.3 | 23.86 | 1700000
2023-03-10 | 61590 | 61.59 | 7.21 | 7.74 | 130 | 15 | 320 | 40 | 296 | 27 | NA | 400 | 0.3 | 23.22 | 1300000
2023-03-11 | 61730 | 61.73 | 7.28 | 7.76 | 145 | 18 | 316 | 44 | 297 | 28 | NA | 700 | 0.2 | 24.26 | 1400000
2023-03-12 | 61820 | 61.82 | 7.26 | 7.71 | 150 | 19 | 324 | 48 | 282 | 26 | NA | 500 | 0.3 | 23.45 | 1700000
2023-03-13 | 60630 | 60.63 | 7.22 | 7.68 | 145 | 17 | 304 | 40 | 297 | 27 | NA | 600 | 0.3 | 23.69 | 1300000
2023-03-14 | 62360 | 62.36 | 7.26 | 7.74 | 135 | 16 | 320 | 44 | 286 | 28 | NA | 400 | 0.2 | 24.09 | 1700000
2023-03-15 | 61400 | 61.4 | 7.23 | 7.71 | 140 | 15 | 328 | 36 | 291 | 25 | NA | 700 | 0.3 | 23.57 | 1300000
2023-03-16 | 59420 | 59.42 | 7.21 | 7.74 | 135 | 17 | 316 | 40 | 298 | 26 | NA | 500 | 0.2 | 24.04 | 1400000
2023-03-17 | 48320 | 48.32 | 7.27 | 7.76 | 145 | 16 | 312 | 36 | 279 | 27 | NA | 400 | 0.2 | 23.21 | 1300000 | Due to state level strike organised by UPPCL staff, water supply to various areas of Prayagraj was reduced because of several power cuts. Hence, raw sewage generated was less.
2023-03-18 | 36510 | 36.51 | 7.22 | 7.69 | 135 | 15 | 308 | 36 | 273 | 24 | NA | 700 | 0.2 | 23.66 | 1400000
2023-03-19 | 51070 | 51.07 | 7.24 | 7.78 | 140 | 17 | 316 | 40 | 281 | 23 | NA | 400 | 0.3 | 23.5 | 1400000
2023-03-20 | 54630 | 54.63 | 7.21 | 7.73 | 150 | 19 | 328 | 44 | 293 | 27 | NA | 600 | 0.2 | 24.25 | 1700000
2023-03-21 | 56420 | 56.42 | 7.26 | 7.75 | 135 | 15 | 312 | 36 | 287 | 25 | NA | 700 | 0.3 | 24.82 | 1300000
2023-03-22 | 58850 | 58.85 | 7.21 | 7.68 | 130 | 14 | 304 | 40 | 292 | 23 | NA | 500 | 0.3 | 23.64 | 1400000
2023-03-23 | 58260 | 58.26 | 7.25 | 7.72 | 140 | 13 | 328 | 36 | 298 | 24 | NA | 600 | 0.2 | 23.69 | 1700000
2023-03-24 | 70370 | 70.37 | 7.28 | 7.74 | 135 | 15 | 316 | 40 | 304 | 23 | NA | 400 | 0.3 | 23.57 | 1300000
2023-03-25 | 66880 | 66.88 | 7.22 | 7.76 | 145 | 16 | 308 | 40 | 298 | 25 | NA | 700 | 0.3 | 23.78 | 1400000
2023-03-26 | 55350 | 55.35 | 7.25 | 7.73 | 145 | 16 | 316 | 36 | 286 | 24 | NA | 500 | 0.2 | 24.04 | 1700000
2023-03-27 | 57440 | 57.44 | 7.29 | 7.74 | 150 | 16 | 324 | 44 | 306 | 27 | NA | 600 | 0.3 | 23.55 | 1300000
2023-03-28 | 63120 | 63.12 | 7.23 | 7.68 | 140 | 15 | 328 | 40 | 291 | 24 | NA | 400 | 0.3 | 24.98 | 1700000
2023-03-29 | 58680 | 58.68 | 7.26 | 7.74 | 150 | 17 | 316 | 36 | 289 | 23 | NA | 700 | 0.2 | 23.64 | 1400000
2023-03-30 | 62520 | 62.52 | 7.24 | 7.76 | 130 | 15 | 312 | 40 | 296 | 25 | NA | 400 | 0.3 | 24.82 | 1700000
2023-03-31 | 59930 | 59.93 | 7.22 | 7.71 | 140 | 17 | 328 | 36 | 292 | 28 | NA | 600 | 0.2 | 23.5 | 1400000
Average | 59036.129 | 59.0361 | 7.241 | 7.7297 | 140.6452 | 15.9355 | 318.9677 | 39.3548 | 290.9032 | 25.0968 | NA | 548.3871 | 0.25806 | 23.8842 | 1464516.129
1830.12
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 36510 | 36.51 | 7.18 | 7.68 | 130 | 13 | 304 | 36 | 273 | 21 |  | 400 | 0.2 | 23.21 | 1300000
Max | 70370 | 70.37 | 7.29 | 7.78 | 150 | 19 | 336 | 48 | 306 | 29 |  | 700 | 0.3 | 24.98 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-03-01 | 36930 | 36.93 | 7.4 | 7.13 | 165 | 27 | 360 | 44 | 318 | 33 | NA | 700 | 0.3 | 25.2 | 1700000
2023-03-02 | 38480 | 38.48 | 7.56 | 7.07 | 160 | 28 | 368 | 40 | 324 | 34 | NA | 800 | 0.3 | 24.9 | 1700000
2023-03-03 | 37410 | 37.41 | 7.54 | 7.15 | 155 | 29 | 364 | 44 | 309 | 37 | NA | 700 | 0.2 | 24.6 | 1400000
2023-03-04 | 42110 | 42.11 | 7.46 | 7.21 | 165 | 22 | 360 | 40 | 320 | 33 | NA | 600 | 0.3 | 25.3 | 1300000
2023-03-05 | 41070 | 41.07 | 7.48 | 7.2 | 160 | 23 | 368 | 40 | 331 | 35 | NA | 700 | 0.2 | 25.2 | 1400000
2023-03-06 | 39610 | 39.61 | 7.51 | 7.19 | 165 | 22 | 364 | 36 | 335 | 33 | NA | 800 | 0.3 | 24.8 | 1700000
2023-03-07 | 41750 | 41.75 | 7.49 | 7.22 | 155 | 23 | 372 | 40 | 321 | 33 | NA | 700 | 0.3 | 24.6 | 1400000
2023-03-08 | 42580 | 42.58 | 7.52 | 7.16 | 160 | 23 | 368 | 40 | 325 | 32 | NA | 800 | 0.2 | 25.3 | 1700000
2023-03-09 | 45860 | 45.86 | 7.54 | 7.19 | 165 | 25 | 360 | 36 | 318 | 31 | NA | 600 | 0.3 | 24.7 | 1300000
2023-03-10 | 40660 | 40.66 | 7.48 | 7.12 | 155 | 26 | 368 | 40 | 317 | 33 | NA | 700 | 0.2 | 24.5 | 1400000
2023-03-11 | 40840 | 40.84 | 7.58 | 7.38 | 160 | 26 | 364 | 40 | 308 | 32 | NA | 600 | 0.3 | 25.3 | 1300000
2023-03-12 | 44030 | 44.03 | 7.44 | 7.43 | 165 | 25 | 360 | 44 | 312 | 33 | NA | 800 | 0.2 | 25.1 | 1700000
2023-03-13 | 43900 | 43.9 | 7.56 | 7.4 | 155 | 27 | 368 | 44 | 309 | 32 | NA | 700 | 0.3 | 24.8 | 1400000
2023-03-14 | 42850 | 42.85 | 7.47 | 7.35 | 165 | 26 | 364 | 40 | 320 | 35 | NA | 600 | 0.3 | 24.6 | 1400000
2023-03-15 | 43330 | 43.33 | 7.53 | 7.44 | 160 | 29 | 372 | 44 | 307 | 36 | NA | 800 | 0.2 | 24.7 | 1700000
2023-03-16 | 44360 | 44.36 | 7.49 | 7.37 | 165 | 28 | 368 | 44 | 304 | 35 | NA | 700 | 0.3 | 25.3 | 1300000
2023-03-17 | 35150 | 35.15 | 7.52 | 7.42 | 155 | 22 | 364 | 40 | 310 | 34 | NA | 600 | 0.2 | 25.4 | 1400000 | Due to state level strike organised by UPPCL staff, water supply to various areas of Prayagraj was reduced because of several power cuts. Hence, raw sewage generated was less.
2023-03-18 | 36190 | 36.19 | 7.54 | 7.4 | 160 | 23 | 360 | 44 | 306 | 36 | NA | 500 | 0.3 | 25.2 | 1200000
2023-03-19 | 30120 | 30.12 | 7.51 | 7.47 | 165 | 26 | 368 | 44 | 311 | 38 | NA | 400 | 0.2 | 24.8 | 1200000
2023-03-20 | 37810 | 37.81 | 7.53 | 7.38 | 160 | 27 | 360 | 48 | 313 | 37 | NA | 500 | 0.2 | 24.7 | 1300000
2023-03-21 | 38580 | 38.58 | 7.49 | 7.37 | 155 | 25 | 356 | 44 | 307 | 35 | NA | 600 | 0.3 | 23.9 | 1200000
2023-03-22 | 35260 | 35.26 | 7.53 | 7.34 | 165 | 26 | 360 | 40 | 303 | 34 | NA | 700 | 0.2 | 23.6 | 1400000
2023-03-23 | 35110 | 35.11 | 7.46 | 7.31 | 160 | 28 | 356 | 40 | 310 | 33 | NA | 500 | 0.3 | - | 1300000 | Sludge dewatering unit was under maintenance hence sludge consistency test was not performed on 23.03.2023 & 24.03.2023
2023-03-24 | 40220 | 40.22 | 7.51 | 7.28 | 165 | 27 | 360 | 44 | 312 | 34 | NA | 800 | 0.3 | - | 1700000
2023-03-25 | 39670 | 39.67 | 7.39 | 7.25 | 170 | 28 | 364 | 44 | 306 | 36 | NA | 600 | 0.2 | 24.5 | 1400000
2023-03-26 | 39750 | 39.75 | 7.36 | 7.24 | 165 | 26 | 356 | 48 | 314 | 40 | NA | 700 | 0.3 | 23.9 | 1700000
2023-03-27 | 37150 | 37.15 | 7.3 | 7.33 | 155 | 23 | 350 | 44 | 316 | 46 | NA | 400 | 0.2 | 23.6 | 1200000
2023-03-28 | 37760 | 37.76 | 7.29 | 7.34 | 160 | 22 | 364 | 40 | 321 | 34 | NA | 600 | 0.3 | 24.8 | 1400000
2023-03-29 | 36670 | 36.67 | 7.26 | 7.29 | 150 | 24 | 368 | 40 | 320 | 36 | NA | 700 | 0.3 | 24.4 | 1700000
2023-03-30 | 34720 | 34.72 | 7.23 | 7.3 | 155 | 23 | 360 | 44 | 309 | 39 | NA | 800 | 0.3 | 25.4 | 1700000
2023-03-31 | 37130 | 37.13 | 7.3 | 7.37 | 160 | 22 | 364 | 44 | 298 | 42 | NA | 400 | 0.2 | 24.8 | 1300000
Average | 39260 | 39.26 | 7.4603 | 7.2935 | 160.4839 | 25.1935 | 363.1613 | 42.0645 | 314 | 35.1935 | NA | 648.3871 | 0.25806 | 24.7552 | 1448387.0968
1217.06
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 30120 | 30.12 | 7.23 | 7.07 | 150 | 22 | 350 | 36 | 298 | 31 |  | 400 | 0.2 | 23.6 | 1200000
Max | 45860 | 45.86 | 7.58 | 7.47 | 170 | 29 | 372 | 48 | 335 | 46 |  | 800 | 0.3 | 25.4 | 1700000

## Kodra
kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-03-01 | 30180 | 30.18 | 7.23 | 7.45 | 145 | 15 | 308 | 40 | 280 | 18 | NA | 400 | 0.2 | 24.63 | 1300000
2023-03-02 | 28880 | 28.88 | 7.26 | 7.58 | 155 | 14 | 320 | 44 | 273 | 19 | NA | 500 | 0.3 | 23.31 | 1400000
2023-03-03 | 29240 | 29.24 | 7.21 | 7.51 | 140 | 13 | 312 | 36 | 265 | 18 | NA | 600 | 0.2 | 24.14 | 1700000
2023-03-04 | 28760 | 28.76 | 7.25 | 7.53 | 135 | 15 | 304 | 40 | 270 | 19 | NA | 500 | 0.2 | 23.51 | 1300000
2023-03-05 | 29850 | 29.85 | 7.2 | 7.48 | 140 | 16 | 316 | 44 | 261 | 20 | NA | 700 | 0.3 | 23.87 | 1200000
2023-03-06 | 29670 | 29.67 | 7.22 | 7.41 | 150 | 14 | 324 | 40 | 279 | 19 | NA | 500 | 0.2 | 24.11 | 1400000
2023-03-07 | 30410 | 30.41 | 7.27 | 7.51 | 145 | 13 | 312 | 36 | 285 | 18 | NA | 600 | 0.3 | 23.71 | 1300000
2023-03-08 | 32080 | 32.08 | 7.24 | 7.43 | 135 | 15 | 320 | 40 | 275 | 17 | NA | 400 | 0.2 | 24.28 | 1700000
2023-03-09 | 30760 | 30.76 | 7.29 | 7.47 | 130 | 14 | 308 | 36 | 264 | 21 | NA | 500 | 0.2 | 23.46 | 1400000
2023-03-10 | 30800 | 30.8 | 7.23 | 7.42 | 140 | 15 | 316 | 40 | 276 | 18 | NA | 600 | 0.3 | 24.16 | 1300000
2023-03-11 | 30220 | 30.22 | 7.26 | 7.5 | 135 | 13 | 304 | 36 | 281 | 17 | NA | 700 | 0.2 | 24.36 | 1200000
2023-03-12 | 30540 | 30.54 | 7.22 | 7.48 | 145 | 17 | 312 | 44 | 273 | 19 | NA | 500 | 0.3 | 23.53 | 1400000
2023-03-13 | 29160 | 29.16 | 7.31 | 7.54 | 130 | 14 | 308 | 36 | 284 | 20 | NA | 600 | 0.2 | 24.35 | 1300000
2023-03-14 | 29390 | 29.39 | 7.25 | 7.46 | 145 | 16 | 320 | 40 | 266 | 18 | NA | 400 | 0.2 | 24.41 | 1700000
2023-03-15 | 30750 | 30.75 | 7.21 | 7.44 | 155 | 15 | 328 | 44 | 259 | 20 | NA | 500 | 0.3 | 23.15 | 1400000
2023-03-16 | 28720 | 28.72 | 7.27 | 7.51 | 150 | 13 | 316 | 36 | 277 | 19 | NA | 600 | 0.2 | 24.36 | 1300000
2023-03-17 | 28410 | 28.41 | 7.24 | 7.45 | 140 | 15 | 312 | 40 | 282 | 21 | NA | 500 | 0.3 | 24.61 | 1200000 | Due to state level strike organised by UPPCL staff, water supply to various areas of Prayagraj was reduced because of several power cuts. Hence, raw sewage generated was less.
2023-03-18 | 29750 | 29.75 | 7.31 | 7.56 | 145 | 14 | 324 | 44 | 278 | 18 | NA | 600 | 0.3 | 23.48 | 1400000
2023-03-19 | 21360 | 21.36 | 7.26 | 7.53 | 135 | 15 | 308 | 40 | 265 | 19 | NA | 700 | 0.2 | 24.44 | 1200000
2023-03-20 | 28280 | 28.28 | 7.23 | 7.49 | 140 | 16 | 316 | 44 | 275 | 18 | NA | 500 | 0.2 | 24.15 | 1300000
2023-03-21 | 30090 | 30.09 | 7.29 | 7.54 | 150 | 13 | 320 | 36 | 280 | 21 | NA | 400 | 0.3 | 23.86 | 1700000
2023-03-22 | 30360 | 30.36 | 7.31 | 7.58 | 145 | 14 | 312 | 40 | 268 | 20 | NA | 600 | 0.2 | 24.28 | 1400000
2023-03-23 | 27850 | 27.85 | 7.22 | 7.42 | 140 | 15 | 308 | 44 | 283 | 19 | NA | 500 | 0.3 | 23.31 | 1300000
2023-03-24 | 29520 | 29.52 | 7.19 | 7.48 | 135 | 12 | 304 | 36 | 270 | 21 | NA | 700 | 0.2 | 24.11 | 1200000
2023-03-25 | 28580 | 28.58 | 7.24 | 7.51 | 140 | 11 | 316 | 32 | 261 | 20 | NA | 600 | 0.3 | 24.65 | 1400000
2023-03-26 | 28870 | 28.87 | 7.21 | 7.47 | 155 | 12 | 324 | 36 | 276 | 21 | NA | 400 | 0.2 | 23.18 | 1200000
2023-03-27 | 26240 | 26.24 | 7.19 | 7.41 | 145 | 14 | 312 | 40 | 266 | 17 | NA | 500 | 0.3 | 22.94 | 1300000
2023-03-28 | 27300 | 27.3 | 7.23 | 7.46 | 140 | 15 | 320 | 44 | 258 | 16 | NA | 600 | 0.2 | 22.67 | 1400000
2023-03-29 | 27510 | 27.51 | 7.25 | 7.5 | 135 | 14 | 308 | 40 | 271 | 18 | NA | 500 | 0.3 | 23.34 | 1700000
2023-03-30 | 25680 | 25.68 | 7.22 | 7.53 | 145 | 18 | 316 | 48 | 281 | 15 | NA | 700 | 0.2 | 24.09 | 1300000
2023-03-31 | 28250 | 28.25 | 7.27 | 7.55 | 130 | 15 | 304 | 44 | 275 | 19 | NA | 500 | 0.2 | 24.31 | 1200000
Average | 28950.3226 | 28.9503 | 7.2445 | 7.4903 | 141.7742 | 14.3548 | 313.9355 | 40 | 272.8065 | 18.8065 | NA | 545.1613 | 0.24194 | 23.8955 | 1370967.7419
897.46
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 21360 | 21.36 | 7.19 | 7.41 | 130 | 11 | 304 | 32 | 258 | 15 |  | 400 | 0.2 | 22.67 | 1200000
Max | 32080 | 32.08 | 7.31 | 7.58 | 155 | 18 | 328 | 48 | 285 | 21 |  | 700 | 0.3 | 24.65 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-03-01 | 13700 | 13.7 | 7.21 | 7.35 | 155 | 17 | 312 | 44 | 284 | 25 | NA | 600 | 0.3 | 22.61 | 1400000
2023-03-02 | 12650 | 12.65 | 7.26 | 7.41 | 145 | 15 | 308 | 48 | 296 | 22 | NA | 400 | 0.2 | 23.49 | 1500000
2023-03-03 | 12490 | 12.49 | 7.3 | 7.44 | 150 | 17 | 304 | 44 | 289 | 19 | NA | 500 | 0.3 | 23.18 | 1300000
2023-03-04 | 12700 | 12.7 | 7.32 | 7.42 | 140 | 16 | 300 | 48 | 292 | 23 | NA | 700 | 0.3 | 23.96 | 1400000
2023-03-05 | 13460 | 13.46 | 7.33 | 7.43 | 135 | 17 | 295 | 44 | 286 | 22 | NA | 600 | 0.2 | 23.09 | 1700000
2023-03-06 | 11900 | 11.9 | 7.28 | 7.48 | 145 | 18 | 308 | 44 | 276 | 20 | NA | 500 | 0.2 | 23.51 | 1500000
2023-03-07 | 14300 | 14.03 | 7.25 | 7.51 | 150 | 16 | 316 | 48 | 281 | 22 | NA | 600 | 0.3 | 23.66 | 1300000
2023-03-08 | 13620 | 13.62 | 7.36 | 7.38 | 135 | 17 | 306 | 44 | 278 | 21 | NA | 500 | 0.3 | 23.74 | 1400000
2023-03-09 | 13200 | 13.2 | 7.29 | 7.45 | 130 | 19 | 312 | 48 | 266 | 20 | NA | 400 | 0.2 | 22.43 | 1300000
2023-03-10 | 12520 | 12.52 | 7.28 | 7.52 | 150 | 16 | 308 | 44 | 284 | 21 | NA | 600 | 0.3 | 23.56 | 1400000
2023-03-11 | 13040 | 13.04 | 7.39 | 7.48 | 135 | 15 | 304 | 48 | 298 | 20 | NA | 400 | 0.3 | 24.81 | 1200000
2023-03-12 | 13110 | 13.11 | 7.27 | 7.41 | 155 | 17 | 302 | 44 | 284 | 19 | NA | 500 | 0.3 | 23.19 | 1300000
2023-03-13 | 13440 | 13.44 | 7.29 | 7.4 | 145 | 18 | 312 | 48 | 276 | 18 | NA | 400 | 0.3 | 23.93 | 1200000
2023-03-14 | 13810 | 13.81 | 7.28 | 7.47 | 140 | 16 | 300 | 44 | 292 | 17 | NA | 700 | 0.2 | 23.12 | 1400000
2023-03-15 | 12910 | 12.91 | 7.24 | 7.41 | 135 | 17 | 308 | 48 | 290 | 20 | NA | 500 | 0.3 | 22.7 | 1200000
2023-03-16 | 13900 | 13.9 | 7.29 | 7.43 | 155 | 18 | 309 | 44 | 288 | 19 | NA | 400 | 0.3 | 23.02 | 1500000
2023-03-17 | 13430 | 13.43 | 7.32 | 7.44 | 130 | 16 | 304 | 48 | 293 | 17 | NA | 500 | 0.3 | 24.31 | 1400000
2023-03-18 | 13140 | 13.14 | 7.35 | 7.48 | 145 | 17 | 308 | 44 | 284 | 19 | NA | 600 | 0.3 | 22.66 | 1700000
2023-03-19 | 13730 | 13.73 | 7.42 | 7.52 | 135 | 18 | 316 | 48 | 296 | 21 | NA | 400 | 0.2 | 23.51 | 1400000
2023-03-20 | 13890 | 13.89 | 7.4 | 7.44 | 140 | 16 | 312 | 44 | 284 | 23 | NA | 600 | 0.3 | 23.3 | 1700000
2023-03-21 | 13410 | 13.41 | 7.38 | 7.46 | 130 | 17 | 302 | 48 | 274 | 22 | NA | 500 | 0.3 | 23.78 | 1400000
2023-03-22 | 13440 | 13.94 | 7.32 | 7.41 | 150 | 18 | 306 | 44 | 289 | 21 | NA | 400 | 0.3 | 22.42 | 1200000
2023-03-23 | 12730 | 12.73 | 7.34 | 7.43 | 145 | 17 | 308 | 48 | 278 | 20 | NA | 600 | 0.3 | 22.61 | 1400000
2023-03-24 | 13150 | 13.5 | 7.28 | 7.41 | 150 | 18 | 300 | 44 | 298 | 22 | NA | 700 | 0.3 | 22.91 | 1500000
2023-03-25 | 13580 | 12.91 | 7.29 | 7.43 | 135 | 16 | 312 | 48 | 266 | 21 | NA | 400 | 0.3 | 23.78 | 1400000
2023-03-26 | 13580 | 13.58 | 7.3 | 7.49 | 140 | 17 | 304 | 44 | 282 | 24 | NA | 600 | 0.3 | 23.61 | 1200000
2023-03-27 | 12810 | 12.81 | 7.32 | 7.47 | 130 | 15 | 309 | 48 | 264 | 29 | NA | 400 | 0.3 | 22.93 | 1400000
2023-03-28 | 12160 | 12.16 | 7.34 | 7.48 | 140 | 19 | 302 | 44 | 281 | 26 | NA | 700 | 0.2 | 23.36 | 1300000
2023-03-29 | 12700 | 12.7 | 7.32 | 7.46 | 135 | 17 | 308 | 48 | 286 | 28 | NA | 500 | 0.3 | 23.63 | 1200000
2023-03-30 | 12570 | 12.57 | 7.36 | 7.49 | 150 | 15 | 312 | 44 | 298 | 27 | NA | 400 | 0.3 | 22.8 | 1400000
2023-03-31 | 13910 | 13.8 | 7.34 | 7.47 | 145 | 18 | 298 | 48 | 304 | 26 | NA | 600 | 0.3 | 22.32 | 1200000
Average | 13192.9032 | 13.1865 | 7.3135 | 7.4474 | 141.9355 | 16.871 | 306.6129 | 45.9355 | 285.0645 | 21.7419 | NA | 522.5806 | 0.27742 | 23.2881 | 1380645.1613
408.78
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11900 | 11.9 | 7.21 | 7.35 | 130 | 15 | 295 | 44 | 264 | 17 |  | 400 | 0.2 | 22.32 | 1200000
Max | 14300 | 14.03 | 7.42 | 7.52 | 155 | 19 | 316 | 48 | 304 | 29 |  | 700 | 0.3 | 24.81 | 1700000