## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-03-01 | 63180 | 63.18 | 7.16 | 7.7 | 130 | 12 | 308 | 40 | 266 | 26 | NA | 400 | 0.2 | 24.1 | 1200000
2022-03-02 | 59520 | 59.52 | 7.22 | 7.66 | 145 | 16 | 316 | 32 | 228 | 28 | NA | 900 | 0.2 | 24.76 | 1400000
2022-03-03 | 61050 | 61.05 | 7.15 | 7.8 | 135 | 17 | 336 | 40 | 288 | 26 | NA | 500 | 0.3 | 25.3 | 1300000
2022-03-04 | 65200 | 65.2 | 7.15 | 7.74 | 140 | 16 | 324 | 40 | 256 | 28 | NA | 400 | 0.3 | 23.48 | 1400000
2022-03-05 | 62160 | 62.16 | 7.16 | 7.88 | 150 | 17 | 304 | 36 | 276 | 26 | NA | 500 | 0.3 | 24.18 | 1300000
2022-03-06 | 67390 | 67.39 | 7.22 | 7.89 | 145 | 18 | 332 | 44 | 246 | 24 | NA | 600 | 0.2 | 22.34 | 1200000
2022-03-07 | 64860 | 64.86 | 7.19 | 7.74 | 150 | 18 | 328 | 40 | 270 | 28 | NA | 400 | 0.3 | 23.67 | 1200000
2022-03-08 | 63570 | 63.57 | 7.26 | 7.56 | 140 | 14 | 320 | 48 | 250 | 26 | NA | 600 | 0.3 | 23.47 | 1400000
2022-03-09 | 63120 | 63.12 | 7.14 | 7.6 | 135 | 13 | 328 | 40 | 230 | 24 | NA | 700 | 0.2 | 21.52 | 1700000
2022-03-10 | 62620 | 62.62 | 7.21 | 7.84 | 150 | 16 | 316 | 36 | 260 | 28 | NA | 400 | 0.2 | 24.13 | 1400000
2022-03-11 | 61010 | 61.01 | 7.28 | 7.74 | 145 | 16 | 304 | 48 | 254 | 26 | NA | 700 | 0.3 | 23.84 | 1300000
2022-03-12 | 61130 | 61.13 | 7.26 | 7.8 | 138 | 15 | 320 | 40 | 228 | 24 | NA | 600 | 0.3 | 24.3 | 1400000
2022-03-13 | 63910 | 63.91 | 7.3 | 7.82 | 148 | 13 | 332 | 36 | 282 | 22 | NA | 500 | 0.2 | 23.14 | 1300000
2022-03-14 | 57800 | 57.8 | 7.24 | 7.64 | 152 | 15 | 336 | 40 | 275 | 26 | NA | 400 | 0.2 | 23.78 | 1600000
2022-03-15 | 63570 | 63.57 | 7.22 | 7.68 | 145 | 14 | 324 | 36 | 255 | 28 | NA | 700 | 0.3 | 24.22 | 1400000
2022-03-16 | 59920 | 59.92 | 7.29 | 7.71 | 150 | 16 | 316 | 44 | 264 | 24 | NA | 600 | 0.2 | 23.34 | 1300000
2022-03-17 | 63140 | 63.14 | 7.35 | 7.82 | 145 | 15 | 328 | 40 | 272 | 25 | NA | 500 | 0.3 | 23.74 | 1700000
2022-03-18 | 68780 | 68.78 | 7.26 | 7.78 | 140 | 17 | 312 | 36 | 258 | 23 | NA | 400 | 0.3 | 22.49 | 1400000
2022-03-19 | 72020 | 72.02 | 7.21 | 7.65 | 140 | 18 | 324 | 40 | 280 | 26 | NA | 500 | 0.2 | 24.11 | 1600000
2022-03-20 | 62010 | 62.01 | 7.28 | 7.54 | 150 | 17 | 308 | 36 | 265 | 24 | NA | 600 | 0.2 | 23.68 | 1300000
2022-03-21 | 54910 | 54.91 | 7.18 | 7.73 | 140 | 18 | 316 | 40 | 256 | 22 | NA | 400 | 0.3 | 22.56 | 1400000
2022-03-22 | 57130 | 57.13 | 7.31 | 7.62 | 135 | 13 | 304 | 44 | 277 | 24 | NA | 600 | 0.2 | 24.33 | 1300000
2022-03-23 | 54820 | 54.82 | 7.24 | 7.64 | 140 | 14 | 320 | 40 | 255 | 28 | NA | 500 | 0.2 | 22.99 | 1300000
2022-03-24 | 60850 | 60.85 | 7.14 | 7.88 | 140 | 14 | 328 | 40 | 284 | 26 | NA | 700 | 0.2 | 24.19 | 1300000
2022-03-25 | 62190 | 62.19 | 7.18 | 7.67 | 135 | 16 | 320 | 44 | 254 | 24 | NA | 400 | 0.3 | 22.9 | 1400000
2022-03-26 | 52100 | 52.1 | 7.14 | 7.76 | 150 | 15 | 324 | 40 | 268 | 22 | NA | 400 | 0.2 | 22.59 | 1200000
2022-03-27 | 54090 | 54.09 | 7.19 | 7.64 | 140 | 16 | 336 | 36 | 284 | 28 | NA | 500 | 0.3 | 23.95 | 1300000
2022-03-28 | 52210 | 52.21 | 7.15 | 7.68 | 150 | 18 | 316 | 40 | 254 | 24 | NA | 700 | 0.3 | 22.84 | 1200000
2022-03-29 | 52540 | 52.54 | 7.24 | 7.66 | 145 | 15 | 308 | 36 | 280 | 26 | NA | 500 | 0.2 | 22.44 | 1300000
2022-03-30 | 61900 | 61.9 | 7.28 | 7.76 | 140 | 17 | 312 | 48 | 250 | 24 | NA | 700 | 0.2 | 23.98 | 1700000
2022-03-31 | 64080 | 64.08 | 7.16 | 7.8 | 135 | 13 | 328 | 40 | 265 | 28 | NA | 400 | 0.3 | 23.03 | 1400000
Average | 61057.4194 | 61.0574 | 7.2181 | 7.7235 | 142.6774 | 15.5484 | 320.2581 | 40 | 262.2581 | 25.4194 | NA | 538.7097 | 0.24839 | 23.5287 | 1374193.5484
1892.78
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 52100 | 52.1 | 7.14 | 7.54 | 130 | 12 | 304 | 32 | 228 | 22 |  | 400 | 0.2 | 21.52 | 1200000
Max | 72020 | 72.02 | 7.35 | 7.89 | 152 | 18 | 336 | 48 | 288 | 28 |  | 900 | 0.3 | 25.3 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-03-01 | 32040 | 32.04 | 7.42 | 7.63 | 157 | 24 | 364 | 44 | 317 | 37 | NA | 500 | 0.3 | 23.4 | 1300000
2022-03-02 | 33110 | 33.11 | 7.35 | 7.52 | 142 | 21 | 356 | 40 | 326 | 36 | NA | 700 | 0.2 | 22.5 | 1100000
2022-03-03 | 33480 | 33.48 | 7.4 | 7.55 | 153 | 23 | 352 | 44 | 329 | 40 | NA | 800 | 0.2 | 23.6 | 1400000
2022-03-04 | 33260 | 33.26 | 7.22 | 7.39 | 160 | 24 | 356 | 40 | 315 | 38 | NA | 500 | 0.3 | 24.1 | 1200000
2022-03-05 | 33070 | 33.07 | 7.3 | 7.45 | 166 | 26 | 348 | 36 | 309 | 34 | NA | 600 | 0.3 | 24.7 | 1600000
2022-03-06 | 34470 | 34.47 | 7.28 | 7.69 | 156 | 22 | 360 | 32 | 320 | 30 | NA | 700 | 0.2 | 25 | 1200000
2022-03-07 | 32470 | 32.47 | 7.34 | 7.53 | 153 | 25 | 356 | 40 | 312 | 36 | NA | 800 | 0.2 | 23.2 | 1100000
2022-03-08 | 31530 | 31.53 | 7.37 | 7.56 | 159 | 23 | 340 | 36 | 298 | 32 | NA | 500 | 0.3 | 22.7 | 1300000
2022-03-09 | 31150 | 31.15 | 7.25 | 7.48 | 147 | 24 | 352 | 32 | 323 | 31 | NA | 600 | 0.2 | 21.9 | 1400000
2022-03-10 | 32180 | 32.18 | 7.31 | 7.64 | 156 | 25 | 364 | 44 | 308 | 35 | NA | 400 | 0.3 | 24.4 | 1200000
2022-03-11 | 33110 | 33.11 | 7.4 | 7.58 | 150 | 23 | 360 | 36 | 316 | 39 | NA | 700 | 0.2 | 22.3 | 1100000
2022-03-12 | 33210 | 33.21 | 7.29 | 7.52 | 159 | 24 | 348 | 40 | 296 | 33 | NA | 600 | 0.2 | 21.8 | 1300000
2022-03-13 | 31790 | 31.79 | 7.33 | 7.57 | 153 | 25 | 344 | 44 | 314 | 37 | NA | 500 | 0.3 | 23.5 | 1200000
2022-03-14 | 33420 | 33.42 | 7.23 | 7.5 | 156 | 23 | 356 | 36 | 320 | 34 | NA | 700 | 0.2 | 24.2 | 1400000
2022-03-15 | 31500 | 31.5 | 7.37 | 7.65 | 162 | 25 | 340 | 40 | 308 | 36 | NA | 400 | 0.3 | 23.7 | 1600000
2022-03-16 | 33940 | 33.94 | 7.19 | 7.56 | 153 | 24 | 348 | 44 | 325 | 38 | NA | 500 | 0.2 | 23.3 | 1200000
2022-03-17 | 38770 | 38.77 | 7.29 | 7.51 | 165 | 26 | 356 | 36 | 316 | 33 | NA | 600 | 0.3 | 23.9 | 1300000
2022-03-18 | 35300 | 35.3 | 7.34 | 7.63 | 159 | 23 | 344 | 40 | 327 | 35 | NA | 700 | 0.2 | 24.1 | 1400000
2022-03-19 | 36340 | 36.34 | 7.25 | 7.54 | 153 | 22 | 360 | 44 | 320 | 40 | NA | 500 | 0.3 | 23.2 | 1600000
2022-03-20 | 33230 | 33.23 | 7.37 | 7.69 | 144 | 21 | 348 | 48 | 314 | 37 | NA | 800 | 0.2 | 22.8 | 1300000
2022-03-21 | 32090 | 32.09 | 7.41 | 7.58 | 156 | 24 | 340 | 44 | 324 | 34 | NA | 600 | 0.2 | 23.5 | 1400000
2022-03-22 | 32430 | 32.43 | 7.21 | 7.53 | 162 | 25 | 352 | 40 | 308 | 38 | NA | 400 | 0.3 | 22.7 | 1200000
2022-03-23 | 32540 | 32.54 | 7.32 | 7.64 | 153 | 23 | 344 | 44 | 316 | 36 | NA | 700 | 0.2 | 23.2 | 1300000
2022-03-24 | 33350 | 33.35 | 7.27 | 7.56 | 159 | 24 | 356 | 40 | 328 | 33 | NA | 800 | 0.3 | 22.5 | 1100000
2022-03-25 | 32310 | 32.31 | 7.38 | 7.72 | 156 | 22 | 348 | 36 | 312 | 35 | NA | 500 | 0.2 | 22.9 | 1200000
2022-03-26 | 32440 | 32.44 | 7.36 | 7.62 | 162 | 25 | 352 | 44 | 304 | 42 | NA | 700 | 0.2 | 23.3 | 1400000
2022-03-27 | 33980 | 33.98 | 7.25 | 7.68 | 153 | 23 | 344 | 40 | 320 | 39 | NA | 600 | 0.3 | 22.7 | 1300000
2022-03-28 | 38310 | 38.31 | 7.31 | 7.59 | 147 | 26 | 360 | 44 | 308 | 36 | NA | 400 | 0.2 | 22.9 | 1100000
2022-03-29 | 36690 | 36.69 | 7.36 | 7.68 | 156 | 24 | 340 | 36 | 314 | 31 | NA | 500 | 0.3 | 23.6 | 1200000
2022-03-30 | 34180 | 34.18 | 7.23 | 7.55 | 165 | 23 | 352 | 40 | 306 | 34 | NA | 800 | 0.2 | 23.9 | 1400000
2022-03-31 | 33540 | 33.54 | 7.34 | 7.63 | 159 | 25 | 344 | 44 | 318 | 37 | NA | 700 | 0.2 | 23.2 | 1300000
Average | 33523.5484 | 33.5235 | 7.3142 | 7.5797 | 155.8387 | 23.7742 | 351.0968 | 40.2581 | 315.1935 | 35.6774 | NA | 606.4516 | 0.24194 | 23.3129 | 1293548.3871
1039.23
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 31150 | 31.15 | 7.19 | 7.39 | 142 | 21 | 340 | 32 | 296 | 30 |  | 400 | 0.2 | 21.8 | 1100000
Max | 38770 | 38.77 | 7.42 | 7.72 | 166 | 26 | 364 | 48 | 329 | 42 |  | 800 | 0.3 | 25 | 1600000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-03-01 | 28900 | 28.9 | 7.35 | 7.62 | 141 | 12 | 304 | 32 | 272 | 21 | NA | 400 | 0.2 | 23.13 | 1200000
2022-03-02 | 28620 | 28.62 | 7.21 | 7.74 | 147 | 14 | 320 | 36 | 266 | 19 | NA | 600 | 0.3 | 22.47 | 1300000
2022-03-03 | 25710 | 25.71 | 7.31 | 7.69 | 138 | 13 | 312 | 44 | 285 | 22 | NA | 500 | 0.2 | 22.81 | 1200000
2022-03-04 | 27250 | 27.25 | 7.26 | 7.81 | 144 | 12 | 308 | 40 | 276 | 20 | NA | 700 | 0.3 | 23.07 | 1400000
2022-03-05 | 25770 | 25.77 | 7.38 | 7.62 | 135 | 11 | 324 | 48 | 282 | 21 | NA | 400 | 0.2 | 22.43 | 1300000
2022-03-06 | 28430 | 28.43 | 7.23 | 7.56 | 153 | 15 | 316 | 44 | 268 | 19 | NA | 500 | 0.3 | 23.11 | 1200000
2022-03-07 | 27300 | 27.3 | 7.32 | 7.69 | 144 | 14 | 304 | 36 | 279 | 22 | NA | 600 | 0.2 | 23.32 | 1400000
2022-03-08 | 25880 | 25.88 | 7.38 | 7.76 | 138 | 13 | 312 | 40 | 264 | 20 | NA | 700 | 0.2 | 22.81 | 1300000
2022-03-09 | 26710 | 26.71 | 7.27 | 7.65 | 147 | 14 | 324 | 44 | 259 | 21 | NA | 400 | 0.3 | 23.24 | 1200000
2022-03-10 | 27740 | 27.74 | 7.42 | 7.85 | 140 | 15 | 308 | 48 | 274 | 24 | NA | 600 | 0.2 | 22.71 | 1400000
2022-03-11 | 28090 | 28.09 | 7.35 | 7.58 | 145 | 14 | 328 | 44 | 268 | 23 | NA | 500 | 0.3 | 23.29 | 1300000
2022-03-12 | 27750 | 27.75 | 7.27 | 7.69 | 141 | 13 | 320 | 48 | 284 | 24 | NA | 400 | 0.2 | 22.61 | 1200000
2022-03-13 | 27590 | 27.59 | 7.32 | 7.63 | 135 | 14 | 308 | 40 | 277 | 22 | NA | 500 | 0.3 | 23.01 | 1400000
2022-03-14 | 26860 | 26.86 | 7.38 | 7.76 | 140 | 16 | 316 | 44 | 286 | 23 | NA | 600 | 0.2 | 22.5 | 1600000
2022-03-15 | 27440 | 27.44 | 7.24 | 7.56 | 132 | 15 | 304 | 40 | 266 | 21 | NA | 700 | 0.3 | 22.56 | 1400000
2022-03-16 | 26580 | 26.58 | 7.18 | 7.68 | 142 | 16 | 312 | 44 | 280 | 24 | NA | 500 | 0.3 | 23.17 | 1700000
2022-03-17 | 26660 | 26.66 | 7.29 | 7.59 | 150 | 15 | 320 | 40 | 275 | 22 | NA | 600 | 0.2 | 23.45 | 1600000
2022-03-18 | 30870 | 30.87 | 7.27 | 7.64 | 145 | 14 | 308 | 36 | 264 | 23 | NA | 500 | 0.2 | 22.14 | 1300000
2022-03-19 | 27890 | 27.89 | 7.36 | 7.71 | 155 | 16 | 328 | 44 | 286 | 25 | NA | 600 | 0.3 | 23.26 | 1400000
2022-03-20 | 27010 | 27.01 | 7.23 | 7.57 | 148 | 15 | 316 | 40 | 270 | 22 | NA | 700 | 0.2 | 22.61 | 1200000
2022-03-21 | 25570 | 25.57 | 7.28 | 7.66 | 142 | 13 | 324 | 36 | 281 | 20 | NA | 500 | 0.3 | 21.44 | 1600000
2022-03-22 | 26140 | 26.14 | 7.17 | 7.61 | 135 | 14 | 308 | 40 | 273 | 21 | NA | 400 | 0.3 | 23.31 | 1300000
2022-03-23 | 26280 | 26.28 | 7.26 | 7.51 | 140 | 13 | 320 | 36 | 264 | 23 | NA | 600 | 0.2 | 22.63 | 1600000
2022-03-24 | 27230 | 27.23 | 7.34 | 7.68 | 136 | 14 | 312 | 44 | 276 | 24 | NA | 400 | 0.3 | 21.56 | 1400000
2022-03-25 | 27620 | 27.62 | 7.21 | 7.56 | 130 | 13 | 304 | 36 | 259 | 20 | NA | 500 | 0.2 | 23.16 | 1700000
2022-03-26 | 27050 | 27.05 | 7.29 | 7.63 | 138 | 12 | 316 | 32 | 267 | 18 | NA | 600 | 0.2 | 23.47 | 1600000
2022-03-27 | 26220 | 26.22 | 7.38 | 7.74 | 144 | 14 | 300 | 36 | 280 | 19 | NA | 500 | 0.3 | 21.36 | 1400000
2022-03-28 | 25440 | 25.44 | 7.25 | 7.58 | 138 | 16 | 328 | 40 | 271 | 21 | NA | 400 | 0.2 | 22.43 | 1300000
2022-03-29 | 26910 | 26.91 | 7.31 | 7.66 | 140 | 13 | 312 | 36 | 268 | 20 | NA | 700 | 0.3 | 23.29 | 1400000
2022-03-30 | 27380 | 27.38 | 7.27 | 7.48 | 145 | 12 | 320 | 32 | 258 | 18 | NA | 500 | 0.3 | 22.76 | 1200000
2022-03-31 | 26960 | 26.96 | 7.39 | 7.72 | 135 | 14 | 308 | 40 | 265 | 20 | NA | 600 | 0.2 | 23.37 | 1400000
Average | 27156.4516 | 27.1565 | 7.2958 | 7.6526 | 141.3871 | 13.8387 | 314.3226 | 40 | 272.3548 | 21.3548 | NA | 538.7097 | 0.24839 | 22.7897 | 1383870.9677
841.85
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 25440 | 25.44 | 7.17 | 7.48 | 130 | 11 | 300 | 32 | 258 | 18 |  | 400 | 0.2 | 21.36 | 1200000
Max | 30870 | 30.87 | 7.42 | 7.85 | 155 | 16 | 328 | 48 | 286 | 25 |  | 700 | 0.3 | 23.47 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-03-01 | 12750 | 12.75 | 7.2 | 7.64 | 145 | 15 | 312 | 44 | 258 | 22 | NA | 600 | 0.2 | 21.44 | 1400000 | Plant availability is 100%
2022-03-02 | 11190 | 11.19 | 7.33 | 7.76 | 150 | 14 | 320 | 40 | 267 | 24 | NA | 500 | 0.3 | 22.34 | 1300000
2022-03-03 | 12100 | 12.1 | 7.25 | 7.56 | 140 | 13 | 304 | 36 | 276 | 21 | NA | 600 | 0.2 | 21.56 | 1400000
2022-03-04 | 12270 | 12.27 | 7.18 | 7.48 | 146 | 14 | 316 | 40 | 261 | 23 | NA | 400 | 0.3 | 21.16 | 1600000
2022-03-05 | 12460 | 12.46 | 7.29 | 7.64 | 152 | 15 | 324 | 44 | 273 | 22 | NA | 500 | 0.3 | 21.63 | 1300000
2022-03-06 | 12690 | 12.69 | 7.36 | 7.79 | 148 | 14 | 312 | 38 | 260 | 20 | NA | 600 | 0.3 | 22.18 | 1400000
2022-03-07 | 12380 | 12.38 | 7.26 | 7.53 | 140 | 15 | 308 | 40 | 253 | 24 | NA | 500 | 0.2 | 21.88 | 1200000
2022-03-08 | 11760 | 11.76 | 7.14 | 7.38 | 135 | 16 | 300 | 44 | 270 | 26 | NA | 400 | 0.2 | 22.4 | 1400000
2022-03-09 | 12180 | 12.18 | 7.3 | 7.58 | 142 | 15 | 320 | 36 | 266 | 23 | NA | 600 | 0.2 | 23.12 | 1600000
2022-03-10 | 12300 | 12.3 | 7.19 | 7.46 | 138 | 14 | 304 | 40 | 258 | 21 | NA | 500 | 0.3 | 22.58 | 1300000
2022-03-11 | 12140 | 12.14 | 7.41 | 7.77 | 145 | 15 | 316 | 44 | 247 | 22 | NA | 600 | 0.2 | 21.35 | 1400000
2022-03-12 | 11840 | 11.84 | 7.34 | 7.63 | 140 | 16 | 328 | 48 | 261 | 25 | NA | 500 | 0.2 | 21.74 | 1200000
2022-03-13 | 12350 | 12.35 | 7.26 | 7.68 | 138 | 14 | 312 | 44 | 243 | 23 | NA | 400 | 0.3 | 22.2 | 1400000
2022-03-14 | 12100 | 12.1 | 7.18 | 7.39 | 142 | 15 | 320 | 40 | 254 | 22 | NA | 500 | 0.2 | 21.47 | 1300000
2022-03-15 | 11280 | 11.28 | 7.25 | 7.47 | 135 | 14 | 308 | 36 | 265 | 20 | NA | 600 | 0.3 | 21.78 | 1500000
2022-03-16 | 11310 | 11.31 | 7.31 | 7.55 | 145 | 16 | 324 | 40 | 277 | 21 | NA | 500 | 0.3 | 22.61 | 1600000
2022-03-17 | 11410 | 11.41 | 7.35 | 7.63 | 155 | 14 | 336 | 36 | 283 | 24 | NA | 700 | 0.2 | 21.57 | 1400000
2022-03-18 | 12760 | 12.76 | 7.28 | 7.54 | 150 | 15 | 320 | 32 | 292 | 28 | NA | 600 | 0.3 | 23.62 | 1700000
2022-03-19 | 13180 | 13.18 | 7.22 | 7.58 | 153 | 16 | 328 | 40 | 271 | 26 | NA | 500 | 0.2 | 21.38 | 1300000
2022-03-20 | 13380 | 13.38 | 7.34 | 7.67 | 148 | 17 | 316 | 44 | 280 | 25 | NA | 600 | 0.3 | 22.41 | 1600000
2022-03-21 | 12340 | 12.34 | 7.17 | 7.48 | 155 | 15 | 324 | 36 | 264 | 23 | NA | 500 | 0.2 | 23.31 | 1400000
2022-03-22 | 11380 | 11.38 | 7.26 | 7.56 | 146 | 16 | 312 | 40 | 276 | 24 | NA | 700 | 0.2 | 22.64 | 1700000
2022-03-23 | 11630 | 11.63 | 7.23 | 7.61 | 153 | 17 | 320 | 44 | 285 | 21 | NA | 500 | 0.3 | 21.58 | 1200000
2022-03-24 | 11480 | 11.48 | 7.31 | 7.71 | 160 | 16 | 332 | 40 | 256 | 25 | NA | 600 | 0.2 | 21.4 | 1300000
2022-03-25 | 12250 | 12.25 | 7.27 | 7.68 | 152 | 14 | 316 | 36 | 273 | 22 | NA | 400 | 0.3 | 23.2 | 1400000
2022-03-26 | 11540 | 11.54 | 7.24 | 7.51 | 145 | 15 | 304 | 40 | 261 | 21 | NA | 500 | 0.2 | 22.37 | 1600000
2022-03-27 | 12760 | 12.76 | 7.18 | 7.63 | 140 | 16 | 312 | 44 | 281 | 19 | NA | 600 | 0.2 | 21.66 | 1400000
2022-03-28 | 11100 | 11.1 | 7.25 | 7.55 | 150 | 15 | 324 | 40 | 274 | 23 | NA | 500 | 0.3 | 21.81 | 1300000
2022-03-29 | 12520 | 12.52 | 7.33 | 7.73 | 142 | 14 | 308 | 36 | 268 | 20 | NA | 700 | 0.2 | 22.14 | 1600000
2022-03-30 | 11090 | 11.09 | 7.23 | 7.69 | 155 | 15 | 320 | 40 | 251 | 22 | NA | 600 | 0.3 | 23.16 | 1400000
2022-03-31 | 12260 | 12.26 | 7.15 | 7.49 | 146 | 16 | 304 | 44 | 266 | 21 | NA | 500 | 0.3 | 22.43 | 1700000
Average | 12070.3226 | 12.0703 | 7.26 | 7.5926 | 146.1613 | 15.0323 | 316.2581 | 40.1935 | 266.7742 | 22.6774 | NA | 541.9355 | 0.24839 | 22.1329 | 1429032.2581
374.18
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11090 | 11.09 | 7.14 | 7.38 | 135 | 13 | 300 | 32 | 243 | 19 |  | 400 | 0.2 | 21.16 | 1200000
Max | 13380 | 13.38 | 7.41 | 7.79 | 160 | 17 | 336 | 48 | 292 | 28 |  | 700 | 0.3 | 23.62 | 1700000