## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-03-01 | 57350 | 57.35 | 7.25 | 7.7 | 135 | 13 | 300 | 36 | 285 | 24 | NA | 500 | 0.3 | 24.01 | 1400000
2024-03-02 | 55900 | 55.9 | 7.25 | 7.85 | 140 | 16 | 308 | 44 | 269 | 26 | NA | 500 | 0.2 | 23.68 | 1300000
2024-03-03 | 59110 | 59.11 | 7.18 | 7.78 | 140 | 18 | 332 | 40 | 286 | 29 | NA | 600 | 0.3 | 23.78 | 1700000
2024-03-04 | 58850 | 58.85 | 7.22 | 7.77 | 145 | 16 | 320 | 44 | 298 | 26 | NA | 400 | 0.3 | 24.02 | 1100000
2024-03-05 | 53630 | 53.63 | 7.24 | 7.75 | 140 | 14 | 312 | 40 | 302 | 24 | NA | 500 | 0.2 | 23.67 | 1400000
2024-03-06 | 48900 | 48.9 | 7.25 | 7.58 | 130 | 16 | 308 | 40 | 296 | 26 | NA | 600 | 0.2 | 22.69 | 1400000 | Due to power cut in local area of Ghagharnalla area for 7-8 hour, raw sewage received in Ghagarnalla MPS from local area is less. Hence, raw sewage received at Numayadahi STP is less than normal
2024-03-07 | 53040 | 53.04 | 7.32 | 7.71 | 140 | 16 | 308 | 40 | 281 | 27 | NA | 400 | 0.3 | 23.67 | 1200000
2024-03-08 | 57880 | 57.88 | 7.12 | 7.81 | 145 | 14 | 328 | 44 | 281 | 26 | NA | 400 | 0.3 | 21.59 | 1400000
2024-03-09 | 56280 | 56.28 | 7.26 | 7.78 | 135 | 15 | 316 | 44 | 268 | 27 | NA | 500 | 0.2 | 24.01 | 1300000
2024-03-10 | 56150 | 56.15 | 7.35 | 7.69 | 140 | 17 | 308 | 40 | 302 | 26 | NA | 400 | 0.3 | 21.59 | 1400000
2024-03-11 | 55970 | 55.97 | 7.22 | 7.74 | 130 | 16 | 328 | 40 | 290 | 27 | NA | 500 | 0.3 | 23.01 | 1200000
2024-03-12 | 59270 | 59.27 | 7.28 | 7.68 | 140 | 14 | 328 | 40 | 281 | 25 | NA | 600 | 0.2 | 22.87 | 1700000
2024-03-13 | 58940 | 58.94 | 7.24 | 7.73 | 130 | 15 | 320 | 40 | 287 | 26 | NA | 700 | 0.2 | 21.16 | 1400000
2024-03-14 | 59520 | 59.52 | 7.22 | 7.8 | 145 | 15 | 324 | 44 | 280 | 27 | NA | 600 | 0.3 | 23.01 | 1300000
2024-03-15 | 57700 | 57.7 | 7.32 | 7.55 | 140 | 17 | 340 | 40 | 283 | 28 | NA | 500 | 0.3 | 22.76 | 1400000
2024-03-16 | 59130 | 59.13 | 7.36 | 7.65 | 145 | 16 | 300 | 44 | 264 | 25 | NA | 700 | 0.3 | 23.69 | 1400000
2024-03-17 | 56890 | 56.89 | 7.18 | 7.76 | 135 | 17 | 320 | 40 | 270 | 26 | NA | 500 | 0.2 | 24.01 | 1300000
2024-03-18 | 60010 | 60.01 | 7.3 | 7.82 | 130 | 16 | 308 | 44 | 281 | 27 | NA | 400 | 0.2 | 21.7 | 1200000
2024-03-19 | 58540 | 58.54 | 7.17 | 7.68 | 140 | 18 | 300 | 40 | 265 | 25 | NA | 600 | 0.3 | 23.5 | 1700000
2024-03-20 | 57950 | 57.95 | 7.2 | 7.71 | 150 | 15 | 316 | 40 | 295 | 26 | NA | 500 | 0.3 | 24.06 | 1100000
2024-03-21 | 57050 | 57.05 | 7.35 | 7.8 | 145 | 14 | 308 | 36 | 278 | 25 | NA | 700 | 0.2 | 23.5 | 1400000
2024-03-22 | 59550 | 59.55 | 7.26 | 7.86 | 130 | 16 | 312 | 44 | 280 | 27 | NA | 500 | 0.2 | 24.55 | 1300000
2024-03-23 | 59850 | 59.85 | 7.25 | 7.78 | 145 | 17 | 300 | 40 | 270 | 25 | NA | 400 | 0.3 | 22.35 | 1700000
2024-03-24 | 60100 | 60.1 | 7.35 | 7.75 | 130 | 16 | 320 | 44 | 282 | 28 | NA | 500 | 0.3 | 23.7 | 1100000
2024-03-25 | 63070 | 63.07 | 7.25 | 7.8 | 140 | 17 | 300 | 40 | 275 | 27 | NA | 700 | 0.2 | 23.98 | 1300000
2024-03-26 | 63650 | 63.65 | 7.32 | 7.68 | 135 | 14 | 340 | 36 | 289 | 25 | NA | 400 | 0.3 | 24.56 | 1200000
2024-03-27 | 59850 | 59.85 | 7.25 | 7.7 | 140 | 15 | 336 | 44 | 278 | 24 | NA | 500 | 0.2 | 22.35 | 1400000
2024-03-28 | 59730 | 59.73 | 7.2 | 7.78 | 150 | 18 | 320 | 40 | 272 | 26 | NA | 400 | 0.3 | 24 | 1100000
2024-03-29 | 61430 | 61.43 | 7.22 | 7.82 | 130 | 16 | 304 | 44 | 280 | 27 | NA | 700 | 0.3 | 23.13 | 1300000
2024-03-30 | 59950 | 59.95 | 7.85 | 7.83 | 135 | 17 | 300 | 40 | 298 | 28 | NA | 500 | 0.3 | 23.68 | 1400000
2024-03-31 | 60000 | 60 | 7.3 | 7.84 | 140 | 18 | 320 | 44 | 274 | 30 | NA | 600 | 0.2 | 22.34 | 1700000
Average | 58233.5484 | 58.2335 | 7.2752 | 7.7477 | 138.5484 | 15.871 | 315.6129 | 41.1613 | 281.9355 | 26.2903 |  | 525.8065 | 0.25806 | 23.2458 | 1361290.3226
1805.24
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 48900 | 48.9 | 7.12 | 7.55 | 130 | 13 | 300 | 36 | 264 | 24 |  | 400 | 0.2 | 21.16 | 1100000
Max | 63650 | 63.65 | 7.85 | 7.86 | 150 | 18 | 340 | 44 | 302 | 30 |  | 700 | 0.3 | 24.56 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-03-01 | 36870 | 36.87 | 7.34 | 7.46 | 160 | 22 | 356 | 36 | 330 | 34 | NA | 600 | 0.3 | 24.2 | 1700000
2024-03-02 | 35920 | 35.92 | 7.3 | 7.41 | 155 | 23 | 340 | 40 | 326 | 36 | NA | 700 | 0.3 | 23.07 | 1400000
2024-03-03 | 40100 | 40.1 | 7.32 | 7.44 | 145 | 22 | 336 | 44 | 357 | 39 | NA | 500 | 0.2 | 24.49 | 1200000
2024-03-04 | 39170 | 39.17 | 7.34 | 7.42 | 155 | 25 | 344 | 40 | 346 | 37 | NA | 400 | 0.3 | 22.23 | 1100000
2024-03-05 | 37810 | 37.81 | 7.37 | 7.46 | 160 | 24 | 356 | 44 | 339 | 34 | NA | 600 | 0.3 | 24.18 | 1400000
2024-03-06 | 39020 | 39.02 | 7.38 | 7.43 | 165 | 27 | 364 | 44 | 336 | 35 | NA | 700 | 0.3 | 23.92 | 1300000
2024-03-07 | 38770 | 38.77 | 7.41 | 7.46 | 160 | 28 | 364 | 48 | 341 | 36 | NA | 400 | 0.2 | 24.79 | 1700000
2024-03-08 | 38640 | 38.64 | 7.36 | 7.4 | 155 | 26 | 356 | 40 | 353 | 34 | NA | 500 | 0.3 | 24.94 | 1100000
2024-03-09 | 39520 | 39.52 | 7.37 | 7.42 | 150 | 25 | 360 | 44 | 332 | 33 | NA | 600 | 0.3 | 24.51 | 1400000
2024-03-10 | 37650 | 37.65 | 7.38 | 7.34 | 160 | 27 | 364 | 48 | 344 | 35 | NA | 500 | 0.2 | 23.77 | 1200000
2024-03-11 | 36980 | 36.98 | 7.36 | 7.29 | 155 | 26 | 356 | 44 | 336 | 37 | NA | 700 | 0.3 | 24.2 | 1300000
2024-03-12 | 39030 | 39.03 | 7.32 | 7.37 | 155 | 23 | 344 | 40 | 340 | 35 | NA | 600 | 0.3 | 23.83 | 1100000
2024-03-13 | 39450 | 39.45 | 7.35 | 7.4 | 160 | 25 | 356 | 44 | 339 | 33 | NA | 400 | 0.3 | 23 | 1400000
2024-03-14 | 38960 | 38.96 | 7.33 | 7.37 | 150 | 22 | 352 | 40 | 342 | 29 | NA | 500 | 0.3 | 23.84 | 1700000
2024-03-15 | 37720 | 37.72 | 7.36 | 7.42 | 155 | 24 | 360 | 44 | 351 | 32 | NA | 700 | 0.2 | 23.65 | 1200000
2024-03-16 | 37530 | 37.53 | 7.34 | 7.4 | 160 | 27 | 364 | 48 | 348 | 34 | NA | 600 | 0.3 | 24.85 | 1300000
2024-03-17 | 37730 | 37.73 | 7.33 | 7.42 | 155 | 25 | 368 | 44 | 332 | 36 | NA | 700 | 0.3 | 22.84 | 1700000
2024-03-18 | 37480 | 37.48 | 7.31 | 7.41 | 150 | 22 | 360 | 40 | 337 | 35 | NA | 400 | 0.2 | 22.36 | 1100000
2024-03-19 | 38830 | 38.83 | 7.34 | 7.42 | 160 | 23 | 356 | 36 | 347 | 33 | NA | 500 | 0.3 | 24.22 | 1200000
2024-03-20 | 37510 | 37.51 | 7.28 | 7.36 | 155 | 24 | 344 | 40 | 340 | 34 | NA | 600 | 0.3 | 22.66 | 1400000
2024-03-21 | 37120 | 37.12 | 7.32 | 7.38 | 160 | 25 | 352 | 40 | 355 | 35 | NA | 500 | 0.3 | 23.58 | 1700000
2024-03-22 | 37560 | 37.56 | 7.28 | 7.37 | 165 | 26 | 360 | 44 | 345 | 32 | NA | 500 | 0.2 | 24.23 | 1700000
2024-03-23 | 36430 | 36.43 | 7.26 | 7.35 | 160 | 24 | 356 | 40 | 338 | 33 | NA | 700 | 0.3 | 23.92 | 1200000
2024-03-24 | 34580 | 34.58 | 7.24 | 7.34 | 155 | 22 | 360 | 36 | 343 | 35 | NA | 400 | 0.3 | 23.21 | 1100000
2024-03-25 | 39160 | 39.16 | 7.28 | 7.43 | 150 | 23 | 364 | 40 | 336 | 32 | NA | 500 | 0.2 | 23.37 | 1700000
2024-03-26 | 37340 | 37.34 | 7.17 | 7.46 | 155 | 24 | 352 | 44 | 335 | 38 | NA | 600 | 0.3 | 23.21 | 1300000
2024-03-27 | 35660 | 35.66 | 7.21 | 7.43 | 160 | 25 | 356 | 40 | 344 | 35 | NA | 700 | 0.2 | 23.37 | 1300000
2024-03-28 | 35080 | 35.08 | 7.22 | 7.45 | 165 | 27 | 364 | 44 | 346 | 32 | NA | 600 | 0.3 | 22.8 | 1700000
2024-03-29 | 37110 | 37.11 | 7.16 | 7.38 | 155 | 25 | 360 | 44 | 334 | 33 | NA | 500 | 0.3 | 23.57 | 1400000
2024-03-30 | 36780 | 36.78 | 7.2 | 7.48 | 160 | 26 | 356 | 40 | 349 | 36 | NA | 700 | 0.2 | 22.35 | 1200000
2024-03-31 | 36520 | 36.52 | 7.21 | 7.46 | 155 | 23 | 352 | 36 | 362 | 35 | NA | 700 | 0.3 | 23.19 | 1100000
Average | 37678.3871 | 37.6784 | 7.3045 | 7.4074 | 156.7742 | 24.5161 | 355.871 | 41.8065 | 342.0323 | 34.4194 |  | 567.7419 | 0.27097 | 23.6242 | 1364516.129
1168.03
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 34580 | 34.58 | 7.16 | 7.29 | 145 | 22 | 336 | 36 | 326 | 29 |  | 400 | 0.2 | 22.23 | 1100000
Max | 40100 | 40.1 | 7.41 | 7.48 | 165 | 28 | 368 | 48 | 362 | 39 |  | 700 | 0.3 | 24.94 | 1700000

## Kodra
kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-03-01 | 27740 | 27.74 | 7.29 | 7.59 | 135 | 14 | 312 | 40 | 282 | 15 | NA | 500 | 0.3 | 24.32 | 1200000
2024-03-02 | 28680 | 28.68 | 7.23 | 7.52 | 140 | 15 | 304 | 44 | 263 | 16 | NA | 700 | 0.3 | 22.64 | 1700000
2024-03-03 | 33960 | 33.96 | 7.15 | 7.47 | 135 | 14 | 324 | 40 | 278 | 18 | NA | 500 | 0.2 | 23.29 | 1300000
2024-03-04 | 28860 | 28.86 | 7.35 | 7.26 | 130 | 15 | 336 | 36 | 287 | 16 | NA | 400 | 0.3 | 22.27 | 1400000
2024-03-05 | 27800 | 27.8 | 7.32 | 7.28 | 135 | 16 | 312 | 44 | 274 | 17 | NA | 500 | 0.3 | 24.14 | 1100000
2024-03-06 | 26670 | 26.67 | 7.2 | 7.27 | 140 | 13 | 300 | 36 | 266 | 15 | NA | 400 | 0.3 | 22.65 | 1200000
2024-03-07 | 28240 | 28.24 | 7.13 | 7.29 | 130 | 14 | 316 | 40 | 278 | 14 | NA | 500 | 0.2 | 23.5 | 1400000
2024-03-08 | 28600 | 28.6 | 7.15 | 7.33 | 135 | 13 | 308 | 36 | 272 | 16 | NA | 600 | 0.2 | 23.02 | 1300000
2024-03-09 | 26980 | 26.98 | 7.2 | 7.35 | 130 | 11 | 300 | 32 | 280 | 15 | NA | 500 | 0.3 | 23.95 | 1700000
2024-03-10 | 28520 | 28.52 | 7.08 | 7.39 | 140 | 12 | 316 | 36 | 269 | 16 | NA | 700 | 0.2 | 22.7 | 1200000
2024-03-11 | 28720 | 28.72 | 6.95 | 7.33 | 130 | 13 | 304 | 40 | 274 | 15 | NA | 400 | 0.3 | 23.62 | 1700000
2024-03-12 | 27500 | 27.5 | 7.16 | 7.31 | 135 | 14 | 312 | 40 | 279 | 16 | NA | 600 | 0.3 | 23.71 | 1300000
2024-03-13 | 27540 | 27.54 | 7.25 | 7.32 | 140 | 13 | 300 | 36 | 262 | 15 | NA | 500 | 0.2 | 22.33 | 1100000
2024-03-14 | 27210 | 27.21 | 7.23 | 7.29 | 145 | 14 | 320 | 40 | 280 | 17 | NA | 400 | 0.2 | 21.82 | 1400000
2024-03-15 | 27990 | 27.99 | 7.35 | 7.26 | 140 | 13 | 332 | 36 | 272 | 16 | NA | 500 | 0.2 | 22.63 | 1700000
2024-03-16 | 28290 | 28.29 | 7.3 | 7.35 | 130 | 14 | 300 | 40 | 260 | 15 | NA | 600 | 0.3 | 23.75 | 1300000
2024-03-17 | 29070 | 29.07 | 7.1 | 7.32 | 135 | 12 | 316 | 36 | 275 | 16 | NA | 400 | 0.2 | 22.47 | 1200000
2024-03-18 | 28320 | 28.32 | 7.12 | 7.38 | 140 | 14 | 312 | 44 | 268 | 17 | NA | 600 | 0.2 | 22.73 | 1400000
2024-03-19 | 27740 | 27.74 | 7.22 | 7.29 | 130 | 13 | 304 | 40 | 258 | 16 | NA | 700 | 0.3 | 23.42 | 1100000
2024-03-20 | 28570 | 28.57 | 7.34 | 7.19 | 135 | 12 | 308 | 36 | 265 | 15 | NA | 500 | 0.3 | 21.84 | 1300000
2024-03-21 | 28290 | 28.29 | 7.51 | 7.23 | 140 | 13 | 296 | 40 | 260 | 17 | NA | 400 | 0.3 | 23.7 | 1400000
2024-03-22 | 29900 | 29.9 | 7.67 | 7.41 | 135 | 15 | 312 | 44 | 278 | 16 | NA | 600 | 0.2 | 24.67 | 1100000
2024-03-23 | 28930 | 28.93 | 7.43 | 7.38 | 130 | 13 | 304 | 40 | 281 | 17 | NA | 700 | 0.3 | 23.05 | 1300000
2024-03-24 | 28370 | 28.37 | 7.12 | 7.42 | 135 | 12 | 308 | 36 | 260 | 15 | NA | 400 | 0.2 | 23.54 | 1400000
2024-03-25 | 29550 | 29.55 | 7.13 | 7.2 | 145 | 13 | 300 | 40 | 272 | 16 | NA | 700 | 0.3 | 24.43 | 1200000
2024-03-26 | 30920 | 30.92 | 7.18 | 7.26 | 140 | 15 | 320 | 44 | 287 | 15 | NA | 500 | 0.3 | 22.15 | 1700000
2024-03-27 | 29260 | 29.26 | 7.1 | 7.31 | 145 | 14 | 336 | 36 | 307 | 14 | NA | 400 | 0.2 | 24.4 | 1300000
2024-03-28 | 27230 | 27.23 | 6.8 | 7.29 | 135 | 13 | 312 | 40 | 271 | 16 | NA | 700 | 0.2 | 22.11 | 1200000
2024-03-29 | 28610 | 28.61 | 6.93 | 7.27 | 140 | 14 | 320 | 44 | 287 | 15 | NA | 400 | 0.3 | 23.67 | 1100000
2024-03-30 | 24780 | 24.78 | 7.03 | 7.29 | 130 | 15 | 328 | 40 | 278 | 17 | NA | 600 | 0.2 | 21.58 | 1300000
2024-03-31 | 29900 | 29.9 | 7.06 | 7.32 | 135 | 14 | 316 | 44 | 269 | 15 | NA | 500 | 0.3 | 22.25 | 1400000
Average | 28475.4839 | 28.4755 | 7.1961 | 7.3281 | 136.129 | 13.5484 | 312.5161 | 39.3548 | 273.9355 | 15.7742 |  | 529.0323 | 0.25484 | 23.1081 | 1335483.871
882.74
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 24780 | 24.78 | 6.8 | 7.19 | 130 | 11 | 296 | 32 | 258 | 14 |  | 400 | 0.2 | 21.58 | 1100000
Max | 33960 | 33.96 | 7.67 | 7.59 | 145 | 16 | 336 | 44 | 307 | 18 |  | 700 | 0.3 | 24.67 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-03-01 | 10940 | 10.94 | 6.92 | 7.48 | 135 | 16 | 276 | 36 | 223 | 22 | NA | 400 | 0.2 | 25.35 | 1700000
2024-03-02 | 10010 | 10.01 | 7.08 | 7.5 | 125 | 14 | 308 | 32 | 265 | 18 | NA | 600 | 0.2 | 24.25 | 1400000
2024-03-03 | 13850 | 13.85 | 7.21 | 7.49 | 135 | 15 | 280 | 36 | 226 | 20 | NA | 700 | 0.3 | 23.67 | 1200000
2024-03-04 | 13740 | 13.74 | 7.13 | 7.46 | 145 | 14 | 296 | 32 | 242 | 19 | NA | 500 | 0.2 | 23.15 | 1400000
2024-03-05 | 12890 | 12.89 | 7.24 | 7.5 | 150 | 15 | 304 | 36 | 229 | 17 | NA | 600 | 0.3 | 22.64 | 1300000
2024-03-06 | 13710 | 13.71 | 7.19 | 7.47 | 140 | 16 | 276 | 32 | 211 | 18 | NA | 700 | 0.2 | 23.15 | 1200000
2024-03-07 | 12810 | 12.81 | 7.11 | 7.4 | 130 | 15 | 292 | 36 | 232 | 21 | NA | 500 | 0.2 | 24.15 | 1700000
2024-03-08 | 13120 | 13.12 | 7.13 | 7.45 | 140 | 14 | 284 | 32 | 224 | 17 | NA | 400 | 0.3 | 23.17 | 1400000
2024-03-09 | 12630 | 12.63 | 7.19 | 7.4 | 135 | 15 | 280 | 36 | 208 | 20 | NA | 600 | 0.2 | 23.44 | 1300000
2024-03-10 | 11830 | 11.83 | 7.13 | 7.45 | 140 | 17 | 272 | 36 | 213 | 23 | NA | 400 | 0.3 | 24.44 | 1400000
2024-03-11 | 12450 | 12.45 | 7.04 | 7.42 | 150 | 16 | 292 | 40 | 249 | 22 | NA | 700 | 0.2 | 24.14 | 1200000
2024-03-12 | 13080 | 13.08 | 7.03 | 7.46 | 120 | 18 | 308 | 40 | 265 | 28 | NA | 500 | 0.3 | 23.13 | 1700000
2024-03-13 | 12170 | 12.17 | 6.91 | 7.48 | 125 | 17 | 284 | 36 | 233 | 26 | NA | 400 | 0.2 | 24.14 | 1300000
2024-03-14 | 12840 | 12.84 | 7.01 | 7.51 | 135 | 16 | 296 | 32 | 229 | 19 | NA | 500 | 0.3 | 23.12 | 1700000
2024-03-15 | 13970 | 13.97 | 6.96 | 7.48 | 140 | 17 | 292 | 36 | 238 | 21 | NA | 700 | 0.2 | 22.4 | 1300000
2024-03-16 | 12240 | 12.24 | 6.99 | 7.4 | 165 | 15 | 300 | 40 | 240 | 23 | NA | 600 | 0.3 | 23.05 | 1400000
2024-03-17 | 13580 | 13.58 | 7.02 | 7.43 | 160 | 17 | 308 | 36 | 232 | 22 | NA | 500 | 0.2 | 22.81 | 1200000
2024-03-18 | 12690 | 12.69 | 7.05 | 7.56 | 130 | 16 | 320 | 40 | 246 | 24 | NA | 400 | 0.3 | 23.04 | 1700000
2024-03-19 | 12340 | 12.34 | 7.08 | 7.57 | 155 | 17 | 316 | 36 | 249 | 25 | NA | 700 | 0.2 | 22.96 | 1300000
2024-03-20 | 12110 | 12.11 | 7.12 | 7.59 | 160 | 16 | 312 | 36 | 242 | 22 | NA | 600 | 0.3 | 23.04 | 1400000
2024-03-21 | 13080 | 13.08 | 7.19 | 7.62 | 135 | 17 | 304 | 32 | 239 | 21 | NA | 500 | 0.2 | 24.12 | 1200000
2024-03-22 | 13190 | 13.19 | 7.16 | 7.58 | 140 | 16 | 288 | 36 | 224 | 22 | NA | 400 | 0.3 | 22.37 | 1700000
2024-03-23 | 13210 | 13.21 | 7.24 | 7.56 | 130 | 17 | 296 | 40 | 229 | 21 | NA | 700 | 0.2 | 22.88 | 1300000
2024-03-24 | 12190 | 12.19 | 7.14 | 7.54 | 125 | 16 | 300 | 36 | 232 | 24 | NA | 600 | 0.3 | 23.11 | 1200000
2024-03-25 | 12340 | 12.34 | 7.17 | 7.63 | 130 | 17 | 296 | 40 | 238 | 25 | NA | 500 | 0.2 | 23.42 | 1400000
2024-03-26 | 13050 | 13.05 | 7.22 | 7.61 | 135 | 16 | 300 | 36 | 223 | 23 | NA | 400 | 0.3 | 22.98 | 1700000
2024-03-27 | 12110 | 12.11 | 7.18 | 7.6 | 125 | 15 | 292 | 40 | 229 | 22 | NA | 700 | 0.2 | 23.17 | 1200000
2024-03-28 | 13240 | 13.24 | 7.18 | 7.56 | 135 | 16 | 288 | 36 | 224 | 23 | NA | 600 | 0.3 | 22.36 | 1300000
2024-03-29 | 13010 | 13.01 | 7.26 | 7.54 | 140 | 17 | 308 | 36 | 242 | 22 | NA | 500 | 0.2 | 22.81 | 1400000
2024-03-30 | 12950 | 12.95 | 7.23 | 7.63 | 135 | 15 | 312 | 40 | 234 | 24 | NA | 700 | 0.3 | 23.62 | 1200000
2024-03-31 | 12610 | 12.61 | 7.25 | 7.66 | 145 | 16 | 304 | 32 | 241 | 23 | NA | 600 | 0.2 | 22.17 | 1700000
Average | 12709.0323 | 12.709 | 7.1213 | 7.5171 | 138.3871 | 15.9355 | 296.2581 | 36.129 | 233.9032 | 21.8387 |  | 554.8387 | 0.24516 | 23.2984 | 1403225.8065
393.98
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 10010 | 10.01 | 6.91 | 7.4 | 120 | 14 | 272 | 32 | 208 | 17 |  | 400 | 0.2 | 22.17 | 1200000
Max | 13970 | 13.97 | 7.26 | 7.66 | 165 | 18 | 320 | 40 | 265 | 28 |  | 700 | 0.3 | 25.35 | 1700000