## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-05-01 | 61900 | 61.9 | 7.28 | 7.69 | 140 | 14 | 316 | 36 | 256 | 24 | NA | 600 | 0.2 | 23.44 | 1400000
2023-05-02 | 60580 | 60.85 | 7.36 | 7.74 | 130 | 15 | 328 | 40 | 274 | 26 | NA | 400 | 0.3 | 24.04 | 1300000
2023-05-03 | 62530 | 62.53 | 7.4 | 7.76 | 125 | 14 | 332 | 44 | 281 | 27 | NA | 700 | 0.3 | 24.54 | 1700000
2023-05-04 | 59820 | 59.82 | 7.38 | 7.69 | 140 | 16 | 308 | 40 | 288 | 25 | NA | 600 | 0.2 | 23.55 | 1300000
2023-05-05 | 54320 | 54.32 | 7.42 | 7.81 | 130 | 18 | 320 | 44 | 279 | 27 | NA | 500 | 0.3 | 23.64 | 1400000
2023-05-06 | 58210 | 58.21 | 7.27 | 7.74 | 135 | 15 | 316 | 40 | 283 | 24 | NA | 400 | 0.2 | 23.5 | 1700000
2023-05-07 | 60850 | 60.85 | 7.46 | 7.78 | 150 | 13 | 304 | 36 | 292 | 25 | NA | 600 | 0.2 | 24.47 | 1300000
2023-05-08 | 58750 | 58.75 | 7.28 | 7.58 | 140 | 16 | 320 | 40 | 258 | 26 | NA | 700 | 0.3 | 24.49 | 1300000
2023-05-09 | 60780 | 60.78 | 7.44 | 7.67 | 145 | 15 | 308 | 36 | 244 | 22 | NA | 600 | 0.2 | 23.11 | 1400000
2023-05-10 | 59770 | 59.77 | 7.36 | 7.7 | 150 | 18 | 328 | 40 | 248 | 27 | NA | 500 | 0.2 | 23.84 | 1700000
2023-05-11 | 59250 | 59.25 | 7.19 | 7.64 | 145 | 16 | 320 | 40 | 236 | 28 | NA | 400 | 0.3 | 24.41 | 1300000
2023-05-12 | 58610 | 58.61 | 7.4 | 7.69 | 135 | 13 | 324 | 44 | 252 | 26 | NA | 600 | 0.3 | 23.9 | 1400000
2023-05-13 | 62180 | 62.18 | 7.36 | 7.72 | 140 | 15 | 316 | 36 | 268 | 24 | NA | 400 | 0.2 | 23.78 | 1700000
2023-05-14 | 58720 | 58.72 | 7.48 | 7.76 | 145 | 16 | 312 | 40 | 273 | 26 | NA | 700 | 0.3 | 24.98 | 1400000
2023-05-15 | 60720 | 60.72 | 7.61 | 7.72 | 150 | 17 | 320 | 44 | 286 | 28 | NA | 500 | 0.2 | 24.82 | 1300000
2023-05-16 | 60120 | 60.12 | 7.52 | 7.74 | 140 | 17 | 316 | 40 | 278 | 25 | NA | 400 | 0.3 | 24.23 | 1400000
2023-05-17 | 60580 | 60.58 | 7.48 | 7.76 | 135 | 14 | 308 | 36 | 256 | 24 | NA | 600 | 0.3 | 23.69 | 1700000
2023-05-18 | 58800 | 58.8 | 7.26 | 7.68 | 145 | 16 | 300 | 40 | 261 | 27 | NA | 500 | 0.2 | 23.14 | 1400000
2023-05-19 | 60850 | 60.85 | 7.38 | 7.73 | 140 | 15 | 312 | 36 | 253 | 25 | NA | 700 | 0.3 | 24.04 | 1700000
2023-05-20 | 60700 | 60.7 | 7.42 | 7.71 | 130 | 15 | 308 | 40 | 264 | 24 | NA | 400 | 0.3 | 22.85 | 1300000
2023-05-21 | 61530 | 61.53 | 7.46 | 7.78 | 145 | 17 | 328 | 44 | 273 | 26 | NA | 600 | 0.2 | 23.76 | 1400000
2023-05-22 | 59980 | 59.98 | 7.44 | 7.74 | 140 | 16 | 332 | 40 | 258 | 25 | NA | 500 | 0.3 | 23.26 | 1700000
2023-05-23 | 60780 | 60.78 | 7.38 | 7.67 | 150 | 17 | 316 | 44 | 264 | 24 | NA | 700 | 0.2 | 23.57 | 1400000
2023-05-24 | 55020 | 55.02 | 7.42 | 7.7 | 135 | 14 | 308 | 36 | 268 | 27 | NA | 600 | 0.2 | 24.25 | 1300000
2023-05-25 | 59550 | 59.55 | 7.36 | 7.73 | 145 | 15 | 328 | 40 | 272 | 24 | NA | 400 | 0.3 | 23.5 | 1400000
2023-05-26 | 57760 | 57.76 | 7.28 | 7.66 | 140 | 17 | 324 | 44 | 281 | 26 | NA | 700 | 0.2 | 23.56 | 1700000
2023-05-27 | 56670 | 56.67 | 7.46 | 7.78 | 130 | 16 | 316 | 36 | 256 | 24 | NA | 500 | 0.3 | 24.58 | 1400000
2023-05-28 | 59900 | 59.9 | 7.38 | 7.76 | 145 | 14 | 320 | 40 | 276 | 25 | NA | 400 | 0.3 | 24.37 | 1300000
2023-05-29 | 60990 | 60.99 | 7.32 | 7.69 | 150 | 17 | 324 | 44 | 258 | 26 | NA | 600 | 0.2 | 23.22 | 1700000
2023-05-30 | 60400 | 60.4 | 7.26 | 7.71 | 135 | 13 | 312 | 40 | 284 | 26 | NA | 500 | 0.3 | 23.64 | 1300000
2023-05-31 | 62080 | 62.08 | 7.36 | 7.74 | 150 | 16 | 304 | 44 | 274 | 24 | NA | 700 | 0.2 | 24.79 | 1400000
Average | 59764.5161 | 59.7732 | 7.3829 | 7.7184 | 140.4839 | 15.4839 | 317.0323 | 40.129 | 267.5484 | 25.3871 | NA | 548.3871 | 0.25161 | 23.9019 | 1454838.7097
1852.97
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 54320 | 54.32 | 7.19 | 7.58 | 125 | 13 | 300 | 36 | 236 | 22 |  | 400 | 0.2 | 22.85 | 1300000
Max | 62530 | 62.53 | 7.61 | 7.81 | 150 | 18 | 332 | 44 | 292 | 28 |  | 700 | 0.3 | 24.98 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-05-01 | 35420 | 35.42 | 7.38 | 7.52 | 155 | 21 | 356 | 44 | 298 | 35 | NA | 600 | 0.2 | 24.6 | 1400000
2023-05-02 | 32800 | 32.8 | 7.26 | 7.36 | 150 | 21 | 352 | 44 | 320 | 41 | NA | 400 | 0.3 | 24.8 | 1200000
2023-05-03 | 36690 | 36.69 | 7.3 | 7.33 | 160 | 25 | 356 | 48 | 323 | 40 | NA | 500 | 0.3 | 23.7 | 1300000
2023-05-04 | 36340 | 36.34 | 7.32 | 7.36 | 165 | 27 | 360 | 44 | 316 | 38 | NA | 700 | 0.2 | 25.3 | 1400000
2023-05-05 | 42500 | 42.5 | 7.48 | 7.52 | 160 | 27 | 352 | 44 | 296 | 42 | NA | 600 | 0.3 | 24.5 | 1400000
2023-05-06 | 37120 | 37.12 | 7.23 | 7.29 | 165 | 25 | 356 | 36 | 304 | 29 | NA | 400 | 0.3 | 24.8 | 1300000
2023-05-07 | 40360 | 40.36 | 7.47 | 7.51 | 165 | 26 | 360 | 40 | 290 | 31 | NA | 500 | 0.2 | 23.7 | 1700000
2023-05-08 | 39450 | 39.45 | 7.58 | 7.64 | 160 | 24 | 364 | 40 | 307 | 32 | NA | 700 | 0.3 | 24.6 | 1700000
2023-05-09 | 40960 | 40.96 | 7.53 | 7.59 | 155 | 29 | 368 | 44 | 314 | 34 | NA | 800 | 0.3 | 25.2 | 1400000
2023-05-10 | 41110 | 41.11 | 7.28 | 7.34 | 160 | 30 | 360 | 48 | 309 | 35 | NA | 600 | 0.2 | 24.7 | 1200000
2023-05-11 | 41720 | 41.72 | 7.26 | 7.33 | 165 | 29 | 364 | 44 | 315 | 33 | NA | 700 | 0.3 | 24.4 | 1300000
2023-05-12 | 40750 | 40.75 | 7.24 | 7.31 | 170 | 27 | 368 | 40 | 319 | 32 | NA | 500 | 0.3 | 23.8 | 1100000
2023-05-13 | 41750 | 41.75 | 7.31 | 7.35 | 160 | 26 | 372 | 44 | 324 | 36 | NA | 800 | 0.2 | 25.3 | 1400000
2023-05-14 | 41030 | 41.03 | 7.26 | 7.34 | 165 | 28 | 364 | 48 | 316 | 41 | NA | 700 | 0.3 | 24.1 | 1300000
2023-05-15 | 36730 | 36.73 | 7.2 | 7.36 | 160 | 27 | 360 | 44 | 330 | 38 | NA | 600 | 0.2 | 25.6 | 1700000
2023-05-16 | 34930 | 34.93 | 7.42 | 7.51 | 165 | 26 | 364 | 40 | 332 | 32 | NA | 400 | 0.3 | 24.7 | 1400000
2023-05-17 | 33700 | 33.7 | 7.36 | 7.58 | 160 | 28 | 356 | 40 | 328 | 30 | NA | 600 | 0.3 | 24.9 | 1400000
2023-05-18 | 31220 | 31.22 | 7.49 | 7.53 | 165 | 29 | 360 | 44 | 314 | 33 | NA | 500 | 0.2 | 24.3 | 1200000
2023-05-19 | 31110 | 31.11 | 7.46 | 7.56 | 160 | 29 | 364 | 44 | 333 | 36 | NA | 700 | 0.3 | 23.7 | 1700000
2023-05-20 | 34050 | 34.05 | 7.38 | 7.4 | 165 | 27 | 360 | 48 | 332 | 42 | NA | 600 | 0.3 | 23.8 | 1400000
2023-05-21 | 35030 | 35.03 | 7.35 | 7.41 | 160 | 26 | 368 | 48 | 340 | 43 | NA | 500 | 0.3 | 24.6 | 1400000
2023-05-22 | 37080 | 37.08 | 7.31 | 7.37 | 165 | 25 | 364 | 44 | 335 | 40 | NA | 700 | 0.2 | 24.7 | 1300000
2023-05-23 | 35580 | 35.58 | 7.38 | 7.41 | 160 | 27 | 360 | 40 | 345 | 30 | NA | 600 | 0.3 | 25.3 | 1400000
2023-05-24 | 35680 | 35.68 | 7.43 | 7.49 | 150 | 24 | 372 | 36 | 339 | 29 | NA | 500 | 0.3 | 24.8 | 1200000
2023-05-25 | 40530 | 40.53 | 7.45 | 7.51 | 155 | 25 | 368 | 40 | 342 | 31 | NA | 800 | 0.2 | 24.5 | 1700000
2023-05-26 | 33340 | 33.34 | 7.42 | 7.48 | 160 | 25 | 364 | 40 | 348 | 33 | NA | 400 | 0.3 | 23.7 | 1400000
2023-05-27 | 36920 | 36.92 | 7.44 | 7.52 | 155 | 27 | 368 | 44 | 346 | 35 | NA | 600 | 0.3 | 24.6 | 1300000
2023-05-28 | 36160 | 36.16 | 7.43 | 7.51 | 160 | 26 | 360 | 44 | 327 | 38 | NA | 500 | 0.3 | 25.4 | 1400000
2023-05-29 | 35680 | 35.68 | 7.41 | 7.52 | 150 | 25 | 356 | 40 | 309 | 35 | NA | 800 | 0.2 | 25.2 | 1100000
2023-05-30 | 34530 | 34.53 | 7.2 | 7.28 | 155 | 26 | 364 | 44 | 298 | 37 | NA | 700 | 0.3 | 23.6 | 1300000
2023-05-31 | 36040 | 36.04 | 7.27 | 7.46 | 160 | 27 | 352 | 40 | 289 | 36 | NA | 400 | 0.2 | 23.2 | 1700000
Average | 36977.7419 | 36.9777 | 7.3645 | 7.4416 | 160 | 26.2581 | 361.6774 | 42.8387 | 320.5806 | 35.3871 | NA | 593.5484 | 0.26452 | 24.5194 | 1390322.5806
1146.31
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 31110 | 31.11 | 7.2 | 7.28 | 150 | 21 | 352 | 36 | 289 | 29 |  | 400 | 0.2 | 23.2 | 1100000
Max | 42500 | 42.5 | 7.58 | 7.64 | 170 | 30 | 372 | 48 | 348 | 43 |  | 800 | 0.3 | 25.6 | 1700000

## Kodra
kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-05-01 | 27420 | 27.42 | 7.26 | 7.51 | 145 | 13 | 316 | 36 | 280 | 22 | NA | 500 | 0.2 | 22.47 | 1400000
2023-05-02 | 29600 | 29.6 | 7.29 | 7.56 | 150 | 12 | 324 | 32 | 263 | 23 | NA | 600 | 0.3 | 23.41 | 1700000
2023-05-03 | 29170 | 29.17 | 7.34 | 7.81 | 140 | 13 | 312 | 40 | 271 | 20 | NA | 400 | 0.2 | 24.15 | 1300000
2023-05-04 | 35920 | 35.92 | 7.38 | 7.63 | 135 | 14 | 320 | 44 | 268 | 24 | NA | 500 | 0.2 | 23.73 | 1200000
2023-05-05 | 29230 | 29.23 | 7.27 | 7.61 | 130 | 15 | 308 | 40 | 276 | 23 | NA | 600 | 0.3 | 22.87 | 1400000
2023-05-06 | 28190 | 28.19 | 7.24 | 7.55 | 140 | 13 | 316 | 36 | 265 | 22 | NA | 400 | 0.2 | 23.18 | 1300000
2023-05-07 | 29840 | 29.84 | 7.22 | 7.48 | 145 | 16 | 300 | 40 | 258 | 25 | NA | 700 | 0.3 | 24.26 | 1700000
2023-05-08 | 27760 | 27.76 | 7.25 | 7.53 | 150 | 11 | 312 | 36 | 270 | 21 | NA | 500 | 0.2 | 23.65 | 1400000
2023-05-09 | 28990 | 28.99 | 7.23 | 7.5 | 135 | 13 | 304 | 40 | 281 | 22 | NA | 600 | 0.3 | 23.78 | 1200000
2023-05-10 | 28300 | 28.3 | 7.2 | 7.56 | 145 | 15 | 320 | 44 | 273 | 24 | NA | 700 | 0.2 | 24.21 | 1300000
2023-05-11 | 27230 | 27.23 | 7.18 | 7.54 | 140 | 12 | 316 | 36 | 267 | 21 | NA | 500 | 0.2 | 22.54 | 1700000
2023-05-12 | 25900 | 25.9 | 7.29 | 7.57 | 130 | 13 | 308 | 40 | 278 | 23 | NA | 600 | 0.3 | 23.36 | 1400000
2023-05-13 | 26700 | 26.7 | 7.24 | 7.51 | 135 | 14 | 312 | 44 | 263 | 22 | NA | 500 | 0.2 | 24.29 | 1300000
2023-05-14 | 29150 | 29.15 | 7.21 | 7.55 | 145 | 12 | 324 | 36 | 272 | 20 | NA | 700 | 0.2 | 22.58 | 1200000
2023-05-15 | 28320 | 28.32 | 7.19 | 7.49 | 140 | 13 | 316 | 40 | 264 | 22 | NA | 500 | 0.3 | 23.39 | 1400000
2023-05-16 | 28170 | 28.17 | 7.2 | 7.45 | 135 | 11 | 304 | 36 | 281 | 21 | NA | 600 | 0.2 | 24.11 | 1300000
2023-05-17 | 27600 | 27.6 | 7.22 | 7.43 | 140 | 12 | 300 | 40 | 276 | 23 | NA | 400 | 0.3 | 23.66 | 1200000
2023-05-18 | 25890 | 25.89 | 7.18 | 7.48 | 135 | 13 | 308 | 36 | 268 | 22 | NA | 500 | 0.3 | 24.51 | 1700000
2023-05-19 | 27270 | 27.27 | 7.23 | 7.51 | 145 | 12 | 316 | 40 | 259 | 24 | NA | 600 | 0.2 | 22.81 | 1400000
2023-05-20 | 25910 | 25.91 | 7.26 | 7.5 | 155 | 14 | 324 | 44 | 270 | 25 | NA | 500 | 0.3 | 23.08 | 1200000
2023-05-21 | 26150 | 26.15 | 7.21 | 7.46 | 140 | 15 | 312 | 40 | 266 | 23 | NA | 700 | 0.2 | 24.14 | 1300000
2023-05-22 | 25500 | 25.5 | 7.18 | 7.43 | 135 | 13 | 304 | 36 | 273 | 21 | NA | 600 | 0.2 | 24.25 | 1400000
2023-05-23 | 27050 | 27.05 | 7.16 | 7.42 | 130 | 12 | 316 | 40 | 281 | 24 | NA | 400 | 0.3 | 23.49 | 1700000
2023-05-24 | 26660 | 26.66 | 7.2 | 7.52 | 135 | 15 | 308 | 44 | 269 | 23 | NA | 500 | 0.2 | 23.83 | 1300000
2023-05-25 | 26540 | 26.54 | 7.23 | 7.47 | 145 | 13 | 320 | 40 | 278 | 22 | NA | 600 | 0.3 | 22.19 | 1400000
2023-05-26 | 30310 | 30.31 | 7.24 | 7.49 | 150 | 14 | 312 | 36 | 264 | 20 | NA | 500 | 0.3 | 23.33 | 1700000
2023-05-27 | 27980 | 27.98 | 7.29 | 7.53 | 140 | 15 | 300 | 40 | 283 | 19 | NA | 400 | 0.2 | 24.17 | 1300000
2023-05-28 | 26320 | 26.32 | 7.24 | 7.45 | 135 | 13 | 308 | 36 | 298 | 23 | NA | 500 | 0.3 | 23.42 | 1400000
2023-05-29 | 26900 | 26.9 | 7.22 | 7.48 | 145 | 12 | 316 | 40 | 286 | 21 | NA | 600 | 0.2 | 22.96 | 1200000
2023-05-30 | 27850 | 27.85 | 7.25 | 7.51 | 140 | 14 | 304 | 44 | 271 | 20 | NA | 500 | 0.2 | 23.26 | 1300000
2023-05-31 | 27620 | 27.62 | 7.29 | 7.54 | 150 | 13 | 320 | 40 | 266 | 22 | NA | 400 | 0.3 | 24.28 | 1700000
Average | 27917.4194 | 27.9174 | 7.2384 | 7.5184 | 140.6452 | 13.2258 | 312.2581 | 39.2258 | 272.1935 | 22.1613 | NA | 535.4839 | 0.24516 | 23.5277 | 1400000
865.44
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 25500 | 25.5 | 7.16 | 7.42 | 130 | 11 | 300 | 32 | 258 | 19 |  | 400 | 0.2 | 22.19 | 1200000
Max | 35920 | 35.92 | 7.38 | 7.81 | 155 | 16 | 324 | 44 | 298 | 25 |  | 700 | 0.3 | 24.51 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-05-01 | 12010 | 12.01 | 7.36 | 7.57 | 150 | 18 | 316 | 48 | 272 | 29 | NA | 300 | 0.2 | 24.68 | 1300000
2023-05-02 | 13280 | 12.28 | 7.45 | 7.55 | 135 | 16 | 310 | 44 | 286 | 27 | NA | 500 | 0.3 | 23.31 | 1200000
2023-05-03 | 12610 | 12.61 | 7.39 | 7.58 | 145 | 17 | 312 | 40 | 279 | 26 | NA | 400 | 0.3 | 22.49 | 1400000
2023-05-04 | 13970 | 13.97 | 7.3 | 7.49 | 140 | 16 | 320 | 44 | 294 | 27 | NA | 300 | 0.2 | 23.5 | 1200000
2023-05-05 | 13090 | 13.09 | 7.32 | 7.5 | 150 | 18 | 318 | 48 | 278 | 26 | NA | 600 | 0.3 | 23.72 | 1400000
2023-05-06 | 12840 | 12.84 | 7.35 | 7.52 | 135 | 17 | 298 | 44 | 289 | 29 | NA | 500 | 0.3 | 23.5 | 1300000
2023-05-07 | 12700 | 12.7 | 7.32 | 7.57 | 140 | 16 | 304 | 40 | 282 | 22 | NA | 400 | 0.2 | 23.46 | 1200000
2023-05-08 | 13060 | 13.06 | 7.28 | 7.6 | 130 | 18 | 300 | 44 | 291 | 25 | NA | 500 | 0.3 | 22.82 | 1400000
2023-05-09 | 13400 | 13.4 | 7.16 | 7.61 | 145 | 17 | 312 | 48 | 297 | 24 | NA | 300 | 0.3 | 22.43 | 1200000
2023-05-10 | 12530 | 12.53 | 7.31 | 7.65 | 150 | 16 | 316 | 44 | 293 | 22 | NA | 500 | 0.3 | 22.62 | 1400000
2023-05-11 | 12310 | 12.31 | 7.29 | 7.64 | 140 | 18 | 318 | 48 | 282 | 26 | NA | 400 | 0.2 | 22.21 | 1300000
2023-05-12 | 12640 | 12.64 | 7.34 | 7.67 | 135 | 17 | 302 | 44 | 274 | 24 | NA | 600 | 0.3 | 23.31 | 1400000
2023-05-13 | 13740 | 13.74 | 7.4 | 7.62 | 155 | 18 | 310 | 48 | 298 | 26 | NA | 500 | 0.3 | 23.72 | 1200000
2023-05-14 | 13460 | 13.46 | 7.39 | 7.59 | 140 | 17 | 288 | 44 | 279 | 25 | NA | 400 | 0.3 | 23.18 | 1300000
2023-05-15 | 12320 | 12.32 | 7.42 | 7.63 | 130 | 18 | 312 | 48 | 294 | 28 | NA | 300 | 0.3 | 22.94 | 1200000
2023-05-16 | 12340 | 12.34 | 7.44 | 7.6 | 145 | 16 | 304 | 44 | 300 | 23 | NA | 400 | 0.3 | 23.76 | 1400000
2023-05-17 | 11020 | 11.02 | 7.43 | 7.65 | 135 | 17 | 316 | 48 | 286 | 25 | NA | 500 | 0.2 | 23.5 | 1300000
2023-05-18 | 11700 | 11.7 | 7.4 | 7.66 | 150 | 18 | 308 | 44 | 294 | 24 | NA | 600 | 0.3 | 23.07 | 1400000
2023-05-19 | 12730 | 12.73 | 7.45 | 7.61 | 140 | 19 | 304 | 48 | 289 | 26 | NA | 300 | 0.3 | 22.75 | 1300000
2023-05-20 | 13270 | 13.27 | 7.42 | 7.63 | 135 | 19 | 320 | 48 | 276 | 25 | NA | 400 | 0.3 | 22.26 | 1200000
2023-05-21 | 13720 | 13.72 | 7.43 | 7.58 | 150 | 18 | 308 | 44 | 292 | 23 | NA | 500 | 0.3 | 23.44 | 1400000
2023-05-22 | 13420 | 13.42 | 7.4 | 7.59 | 145 | 17 | 300 | 48 | 284 | 26 | NA | 600 | 0.2 | 23.59 | 1300000
2023-05-23 | 13520 | 13.52 | 7.42 | 7.57 | 140 | 18 | 312 | 44 | 289 | 25 | NA | 400 | 0.3 | 23.72 | 1500000
2023-05-24 | 13760 | 13.76 | 7.4 | 7.63 | 130 | 17 | 304 | 48 | 296 | 24 | NA | 300 | 0.3 | 22.98 | 1300000
2023-05-25 | 12960 | 12.95 | 7.44 | 7.64 | 145 | 19 | 310 | 44 | 286 | 26 | NA | 400 | 0.3 | 23.07 | 1200000
2023-05-26 | 12960 | 12.96 | 7.39 | 7.59 | 135 | 17 | 302 | 48 | 291 | 24 | NA | 500 | 0.2 | 23.71 | 1400000
2023-05-27 | 14080 | 14.08 | 7.36 | 7.65 | 130 | 19 | 308 | 48 | 286 | 25 | NA | 400 | 0.2 | 23.42 | 1300000
2023-05-28 | 14610 | 14.61 | 7.43 | 7.62 | 140 | 16 | 312 | 44 | 294 | 24 | NA | 600 | 0.3 | 23.1 | 1200000
2023-05-29 | 15020 | 15.02 | 7.39 | 7.76 | 150 | 18 | 320 | 48 | 288 | 21 | NA | 500 | 0.3 | 23.74 | 1400000
2023-05-30 | 14550 | 14.55 | 7.43 | 7.79 | 145 | 17 | 304 | 44 | 297 | 25 | NA | 600 | 0.2 | 23.45 | 1300000
2023-05-31 | 13180 | 13.18 | 7.33 | 7.75 | 135 | 18 | 316 | 44 | 276 | 26 | NA | 600 | 0.3 | 22.91 | 1200000
Average | 13122.5806 | 13.09 | 7.3755 | 7.6165 | 140.9677 | 17.4194 | 309.1613 | 45.5484 | 287.4839 | 25.0968 | NA | 454.8387 | 0.27097 | 23.2374 | 1306451.6129
405.79
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11020 | 11.02 | 7.16 | 7.49 | 130 | 16 | 288 | 40 | 272 | 21 |  | 300 | 0.2 | 22.21 | 1200000
Max | 15020 | 15.02 | 7.45 | 7.79 | 155 | 19 | 320 | 48 | 300 | 29 |  | 600 | 0.3 | 24.68 | 1500000