## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-05-01 | 62220 | 62.22 | 7.18 | 7.84 | 125 | 15 | 316 | 40 | 268 | 28 | NA | 700 | 0.2 | 24.91 | 1700000
2022-05-02 | 61780 | 61.78 | 7.15 | 7.64 | 130 | 17 | 344 | 44 | 269 | 26 | NA | 500 | 0.3 | 21.86 | 1300000
2022-05-03 | 68680 | 68.68 | 7.18 | 7.72 | 150 | 18 | 336 | 40 | 265 | 24 | NA | 400 | 0.3 | 22.58 | 1300000
2022-05-04 | 63590 | 63.59 | 7.24 | 7.64 | 140 | 15 | 320 | 40 | 255 | 24 | NA | 600 | 0.2 | 21.92 | 1400000
2022-05-05 | 58110 | 58.11 | 7.26 | 7.61 | 140 | 18 | 348 | 44 | 256 | 26 | NA | 500 | 0.3 | 24.29 | 1700000
2022-05-06 | 65230 | 65.23 | 7.19 | 7.68 | 135 | 17 | 320 | 40 | 240 | 28 | NA | 600 | 0.2 | 24.33 | 1300000
2022-05-07 | 60870 | 60.87 | 7.14 | 7.58 | 135 | 15 | 332 | 40 | 286 | 24 | NA | 400 | 0.2 | 24.02 | 1400000
2022-05-08 | 62990 | 62.99 | 7.16 | 7.77 | 140 | 16 | 316 | 36 | 254 | 26 | NA | 600 | 0.3 | 21.55 | 1300000
2022-05-09 | 59100 | 59.1 | 7.19 | 7.72 | 150 | 17 | 344 | 40 | 294 | 24 | NA | 600 | 0.2 | 24.19 | 1300000
2022-05-10 | 60300 | 60.3 | 7.2 | 7.8 | 140 | 16 | 328 | 36 | 234 | 28 | NA | 400 | 0.3 | 24.25 | 1700000
2022-05-11 | 60310 | 60.31 | 7.38 | 7.52 | 140 | 15 | 340 | 44 | 278 | 24 | NA | 700 | 0.3 | 23.55 | 1300000
2022-05-12 | 59450 | 59.45 | 7.32 | 7.68 | 135 | 14 | 328 | 40 | 247 | 28 | NA | 600 | 0.2 | 24.06 | 1700000
2022-05-13 | 56290 | 56.29 | 7.25 | 7.76 | 130 | 14 | 320 | 40 | 263 | 26 | NA | 600 | 0.2 | 25 | 1300000
2022-05-14 | 61510 | 61.51 | 7.26 | 7.8 | 150 | 16 | 312 | 36 | 268 | 24 | NA | 400 | 0.3 | 23.26 | 1400000
2022-05-15 | 58080 | 58.08 | 7.25 | 7.78 | 140 | 13 | 344 | 40 | 287 | 26 | NA | 600 | 0.3 | 23.53 | 1700000
2022-05-16 | 59050 | 59.05 | 7.14 | 7.64 | 145 | 17 | 340 | 36 | 280 | 24 | NA | 400 | 0.2 | 24.38 | 1300000
2022-05-17 | 59670 | 59.67 | 7.19 | 7.69 | 135 | 14 | 332 | 40 | 265 | 22 | NA | 600 | 0.2 | 24.41 | 1400000
2022-05-18 | 57360 | 57.36 | 7.29 | 7.78 | 150 | 19 | 320 | 36 | 278 | 24 | NA | 400 | 0.3 | 23.02 | 1300000
2022-05-19 | 58650 | 58.65 | 7.19 | 7.64 | 130 | 15 | 312 | 36 | 245 | 26 | NA | 700 | 0.3 | 23.52 | 1700000
2022-05-20 | 53590 | 53.59 | 7.24 | 7.68 | 145 | 14 | 320 | 40 | 246 | 24 | NA | 400 | 0.2 | 22.53 | 1300000
2022-05-21 | 53480 | 53.48 | 7.26 | 7.61 | 135 | 17 | 360 | 36 | 255 | 24 | NA | 700 | 0.3 | 23.39 | 1700000
2022-05-22 | 55760 | 55.76 | 7.25 | 7.58 | 130 | 15 | 324 | 40 | 278 | 26 | NA | 500 | 0.2 | 23.73 | 1400000
2022-05-23 | 56660 | 56.66 | 7.18 | 7.68 | 145 | 18 | 316 | 40 | 280 | 22 | NA | 600 | 0.3 | 21.55 | 1300000
2022-05-24 | 54750 | 54.75 | 7.26 | 7.61 | 135 | 14 | 348 | 40 | 250 | 26 | NA | 400 | 0.2 | 23.54 | 1400000
2022-05-25 | 62320 | 62.32 | 7.2 | 7.64 | 140 | 16 | 312 | 36 | 255 | 27 | NA | 700 | 0.3 | 22.5 | 1700000
2022-05-26 | 63110 | 63.11 | 7.26 | 7.78 | 145 | 15 | 320 | 44 | 252 | 25 | NA | 500 | 0.3 | 22.41 | 1400000
2022-05-27 | 60980 | 60.98 | 7.21 | 7.68 | 135 | 11 | 340 | 40 | 258 | 24 | NA | 400 | 0.2 | 23.45 | 1300000
2022-05-28 | 58030 | 58.03 | 7.18 | 7.72 | 140 | 17 | 348 | 36 | 234 | 26 | NA | 600 | 0.3 | 25.01 | 1700000
2022-05-29 | 55420 | 55.42 | 7.26 | 7.78 | 150 | 16 | 296 | 48 | 265 | 24 | NA | 500 | 0.2 | 24.19 | 1300000
2022-05-30 | 52210 | 52.21 | 7.14 | 7.82 | 145 | 14 | 320 | 40 | 244 | 28 | NA | 600 | 0.3 | 23.53 | 1700000
2022-05-31 | 58960 | 58.96 | 7.27 | 7.78 | 130 | 13 | 344 | 44 | 288 | 26 | NA | 400 | 0.3 | 24.91 | 1400000
Average | 59306.7742 | 59.3068 | 7.2216 | 7.6984 | 139.1935 | 15.5161 | 329.0323 | 39.7419 | 262.4839 | 25.2903 | NA | 535.4839 | 0.25484 | 23.5281 | 1454838.7097
| 1838510 | 1838.51
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 52210 | 52.21 | 7.14 | 7.52 | 125 | 11 | 296 | 36 | 234 | 22 |  | 400 | 0.2 | 21.55 | 1300000
Max | 68680 | 68.68 | 7.38 | 7.84 | 150 | 19 | 360 | 48 | 294 | 28 |  | 700 | 0.3 | 25.01 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-05-01 | 31970 | 31.97 | 7.37 | 7.55 | 157 | 25 | 364 | 44 | 329 | 40 | NA | 600 | 0.2 | 24.1 | 1300000
2022-05-02 | 35350 | 35.35 | 7.25 | 7.64 | 160 | 23 | 340 | 36 | 316 | 31 | NA | 700 | 0.3 | 23.6 | 1700000
2022-05-03 | 35440 | 35.44 | 7.4 | 7.52 | 162 | 24 | 334 | 32 | 312 | 34 | NA | 800 | 0.3 | 23.8 | 1600000
2022-05-04 | 27600 | 27.6 | 7.28 | 7.69 | 154 | 27 | 364 | 48 | 323 | 41 | NA | 700 | 0.2 | 24.8 | 1300000 | From 04.05.2022 to 12.05.2022, plant was in shutdown for doing maintenance works in clarisettler no. 2.
2022-05-05 | 27450 | 27.45 | 7.33 | 7.54 | 165 | 26 | 360 | 44 | 324 | 37 | NA | 500 | 0.3 | 26.6 | 1400000
2022-05-06 | 24430 | 24.43 | 7.3 | 7.57 | 156 | 28 | 352 | 40 | 306 | 38 | NA | 600 | 0.2 | 23.1 | 1200000
2022-05-07 | 20860 | 20.86 | 7.37 | 7.61 | 164 | 27 | 356 | 48 | 298 | 46 | NA | 800 | 0.2 | 24.3 | 1700000
2022-05-08 | 22380 | 22.38 | 7.35 | 7.59 | 158 | 25 | 364 | 44 | 312 | 48 | NA | 700 | 0.3 | 25.1 | 1600000
2022-05-09 | 14800 | 14.8 | 7.41 | 7.61 | 162 | 27 | 360 | 40 | 338 | 44 | NA | 600 | 0.2 | 25.4 | 1300000
2022-05-10 | 17800 | 17.8 | 7.31 | 7.6 | 160 | 24 | 368 | 44 | 316 | 46 | NA | 800 | 0.3 | 24.1 | 1400000
2022-05-11 | 16240 | 16.24 | 7.2 | 7.55 | 164 | 26 | 364 | 48 | 323 | 43 | NA | 500 | 0.3 | 24.8 | 1100000
2022-05-12 | 17640 | 17.64 | 7.3 | 7.58 | 160 | 25 | 360 | 44 | 325 | 42 | NA | 400 | 0.2 | 24.6 | 1200000
2022-05-13 | 19260 | 19.26 | 7.37 | 7.52 | 164 | 28 | 364 | 40 | 334 | 39 | NA | 800 | 0.3 | 25 | 1300000 | From 13.05.2022 to 23.05.2022, plant was in shutdown for doing maintenance works in FAB no. 2.
2022-05-14 | 15730 | 15.73 | 7.32 | 7.47 | 160 | 27 | 356 | 48 | 308 | 45 | NA | 700 | 0.2 | 24.3 | 1600000
2022-05-15 | 17370 | 17.37 | 7.23 | 7.51 | 167 | 28 | 360 | 40 | 329 | 40 | NA | 800 | 0.2 | 25.4 | 1700000
2022-05-16 | 17530 | 17.53 | 7.41 | 7.6 | 160 | 26 | 356 | 44 | 323 | 41 | NA | 700 | 0.3 | 24.5 | 1600000
2022-05-17 | 17400 | 17.4 | 7.39 | 7.55 | 158 | 25 | 360 | 40 | 338 | 44 | NA | 600 | 0.3 | 24.8 | 1300000
2022-05-18 | 15530 | 15.53 | 7.46 | 7.49 | 162 | 27 | 352 | 48 | 310 | 38 | NA | 800 | 0.2 | 25 | 1400000
2022-05-19 | 17650 | 17.65 | 7.42 | 7.63 | 165 | 26 | 356 | 44 | 305 | 42 | NA | 500 | 0.2 | 24.7 | 1700000
2022-05-20 | 16840 | 16.84 | 7.49 | 7.63 | 164 | 28 | 357 | 40 | 325 | 37 | NA | 700 | 0.3 | 24.6 | 1600000
2022-05-21 | 17160 | 17.16 | 7.21 | 7.64 | 160 | 24 | 360 | 44 | 305 | 42 | NA | 600 | 0.2 | 25.1 | 1200000
2022-05-22 | 16260 | 16.26 | 7.23 | 7.59 | 157 | 22 | 364 | 48 | 312 | 40 | NA | 800 | 0.3 | 23.8 | 1300000
2022-05-23 | 29110 | 29.11 | 7.27 | 7.48 | 154 | 20 | 352 | 40 | 320 | 39 | NA | 500 | 0.3 | 24.8 | 1100000
2022-05-24 | 29470 | 29.47 | 7.2 | 7.3 | 158 | 25 | 356 | 44 | 310 | 37 | NA | 600 | 0.2 | 23.9 | 1400000
2022-05-25 | 36130 | 36.13 | 7.3 | 7.39 | 153 | 18 | 364 | 48 | 322 | 38 | NA | 400 | 0.3 | 24.1 | 1200000
2022-05-26 | 33120 | 33.12 | 7.46 | 7.5 | 156 | 22 | 360 | 40 | 318 | 36 | NA | 500 | 0.2 | 23.5 | 1100000
2022-05-27 | 31200 | 31.2 | 7.41 | 7.47 | 164 | 25 | 368 | 36 | 304 | 32 | NA | 700 | 0.3 | 22.9 | 1300000
2022-05-28 | 33110 | 33.11 | 7.4 | 7.51 | 160 | 23 | 352 | 32 | 303 | 35 | NA | 600 | 0.2 | 23.9 | 1600000
2022-05-29 | 29400 | 29.4 | 7.37 | 7.44 | 154 | 20 | 356 | 40 | 284 | 36 | NA | 800 | 0.2 | 23.2 | 1400000
2022-05-30 | 33000 | 33 | 7.39 | 7.49 | 157 | 24 | 344 | 42 | 295 | 34 | NA | 700 | 0.3 | 24.4 | 1100000
2022-05-31 | 30260 | 30.26 | 7.28 | 7.52 | 159 | 21 | 360 | 44 | 302 | 37 | NA | 400 | 0.2 | 22.7 | 1200000
Average | 24112.5806 | 24.1126 | 7.3381 | 7.5413 | 159.8065 | 24.7097 | 357.5161 | 42.3871 | 315.129 | 39.4194 | NA | 641.9355 | 0.24839 | 24.3516 | 1383870.9677
| 747490 | 747.49
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 14800 | 14.8 | 7.2 | 7.3 | 153 | 18 | 334 | 32 | 284 | 31 |  | 400 | 0.2 | 22.7 | 1100000
Max | 36130 | 36.13 | 7.49 | 7.69 | 167 | 28 | 368 | 48 | 338 | 48 |  | 800 | 0.3 | 26.6 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-05-01 | 27950 | 27.95 | 7.34 | 7.68 | 138 | 14 | 316 | 40 | 275 | 20 | NA | 600 | 0.3 | 23.45 | 1400000
2022-05-02 | 28160 | 28.16 | 7.29 | 7.58 | 135 | 12 | 308 | 36 | 266 | 19 | NA | 500 | 0.2 | 22.88 | 1200000
2022-05-03 | 27400 | 27.4 | 7.23 | 7.65 | 143 | 13 | 312 | 40 | 261 | 21 | NA | 700 | 0.3 | 22.19 | 1300000
2022-05-04 | 27610 | 27.61 | 7.37 | 7.69 | 138 | 12 | 304 | 32 | 269 | 18 | NA | 500 | 0.2 | 23.45 | 1600000
2022-05-05 | 27150 | 27.15 | 7.29 | 7.64 | 146 | 14 | 316 | 36 | 276 | 17 | NA | 600 | 0.2 | 23.02 | 1400000
2022-05-06 | 26780 | 26.78 | 7.18 | 7.56 | 136 | 13 | 300 | 40 | 265 | 19 | NA | 400 | 0.3 | 22.65 | 1200000
2022-05-07 | 27550 | 27.55 | 7.27 | 7.41 | 143 | 14 | 320 | 36 | 281 | 21 | NA | 700 | 0.2 | 23.31 | 1400000
2022-05-08 | 28410 | 28.41 | 7.22 | 7.59 | 133 | 12 | 312 | 32 | 273 | 18 | NA | 600 | 0.3 | 23.64 | 1300000
2022-05-09 | 27800 | 27.8 | 7.31 | 7.67 | 140 | 13 | 308 | 40 | 268 | 20 | NA | 400 | 0.2 | 22.93 | 1600000
2022-05-10 | 27190 | 27.19 | 7.24 | 7.56 | 146 | 15 | 316 | 44 | 262 | 21 | NA | 600 | 0.3 | 23.3 | 1400000
2022-05-11 | 27250 | 27.25 | 7.34 | 7.62 | 136 | 14 | 324 | 40 | 274 | 19 | NA | 500 | 0.2 | 22.8 | 1200000
2022-05-12 | 26920 | 26.92 | 7.27 | 7.69 | 143 | 13 | 312 | 36 | 265 | 21 | NA | 700 | 0.2 | 23.24 | 1400000
2022-05-13 | 27460 | 27.46 | 7.2 | 7.58 | 153 | 16 | 320 | 40 | 278 | 18 | NA | 600 | 0.3 | 23.71 | 1300000
2022-05-14 | 26370 | 26.37 | 7.32 | 7.66 | 140 | 14 | 308 | 36 | 269 | 19 | NA | 400 | 0.2 | 22.96 | 1200000
2022-05-15 | 27420 | 27.42 | 7.25 | 7.62 | 146 | 15 | 316 | 44 | 259 | 17 | NA | 700 | 0.3 | 22.45 | 1400000
2022-05-16 | 26120 | 26.12 | 7.17 | 7.54 | 133 | 12 | 312 | 40 | 264 | 19 | NA | 600 | 0.2 | 23.4 | 1200000
2022-05-17 | 26240 | 26.24 | 7.29 | 7.67 | 140 | 13 | 324 | 44 | 272 | 18 | NA | 500 | 0.3 | 23.14 | 1300000
2022-05-18 | 27020 | 27.02 | 7.23 | 7.59 | 136 | 12 | 308 | 36 | 261 | 20 | NA | 400 | 0.2 | 22.79 | 1600000
2022-05-19 | 25790 | 25.79 | 7.34 | 7.64 | 143 | 14 | 312 | 40 | 268 | 19 | NA | 600 | 0.3 | 23.55 | 1400000
2022-05-20 | 25260 | 25.26 | 7.2 | 7.56 | 140 | 13 | 320 | 44 | 276 | 21 | NA | 700 | 0.2 | 22.46 | 1300000
2022-05-21 | 25030 | 25.03 | 7.12 | 7.37 | 146 | 11 | 328 | 36 | 264 | 17 | NA | 500 | 0.3 | 22.87 | 1600000
2022-05-22 | 26370 | 26.37 | 7.17 | 7.44 | 149 | 13 | 316 | 32 | 258 | 16 | NA | 400 | 0.3 | 23.25 | 1200000
2022-05-23 | 28960 | 28.96 | 7.09 | 7.39 | 157 | 14 | 320 | 36 | 270 | 17 | NA | 700 | 0.2 | 23.39 | 1400000
2022-05-24 | 26820 | 26.82 | 7.14 | 7.49 | 146 | 12 | 312 | 40 | 262 | 18 | NA | 600 | 0.3 | 22.96 | 1300000
2022-05-25 | 26370 | 26.37 | 7.19 | 7.46 | 140 | 10 | 308 | 36 | 276 | 16 | NA | 400 | 0.2 | 23.66 | 1600000
2022-05-26 | 27690 | 27.69 | 7.12 | 7.41 | 136 | 11 | 316 | 40 | 268 | 17 | NA | 500 | 0.3 | 23.36 | 1200000
2022-05-27 | 26800 | 26.8 | 7.21 | 7.53 | 143 | 13 | 320 | 36 | 274 | 16 | NA | 700 | 0.2 | 22.91 | 1400000
2022-05-28 | 27110 | 27.11 | 7.16 | 7.47 | 133 | 12 | 328 | 44 | 265 | 17 | NA | 400 | 0.3 | 24.08 | 1200000
2022-05-29 | 27360 | 27.36 | 7.24 | 7.58 | 146 | 14 | 312 | 40 | 279 | 18 | NA | 600 | 0.2 | 23.42 | 1300000
2022-05-30 | 25820 | 25.82 | 7.19 | 7.54 | 140 | 11 | 324 | 44 | 269 | 16 | NA | 500 | 0.3 | 22.88 | 1600000
2022-05-31 | 27040 | 27.04 | 7.27 | 7.62 | 136 | 12 | 316 | 48 | 258 | 18 | NA | 700 | 0.2 | 23.17 | 1400000
Average | 27007.0968 | 27.0071 | 7.2339 | 7.5645 | 141.2903 | 12.9355 | 315.0968 | 38.9677 | 268.5484 | 18.4194 | NA | 558.0645 | 0.24839 | 23.1377 | 1364516.129
| 837220 | 837.22
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 25030 | 25.03 | 7.09 | 7.37 | 133 | 10 | 300 | 32 | 258 | 16 |  | 400 | 0.2 | 22.19 | 1200000
Max | 28960 | 28.96 | 7.37 | 7.69 | 157 | 16 | 328 | 48 | 281 | 21 |  | 700 | 0.3 | 24.08 | 1600000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-05-01 | 14770 | 14.77 | 7.28 | 7.62 | 145 | 15 | 320 | 44 | 264 | 24 | NA | 600 | 0.2 | 22.19 | 1400000
2022-05-02 | 13940 | 13.94 | 7.35 | 7.68 | 135 | 14 | 308 | 36 | 275 | 22 | NA | 500 | 0.3 | 23.35 | 1700000
2022-05-03 | 14520 | 14.52 | 7.24 | 7.63 | 148 | 16 | 324 | 40 | 286 | 25 | NA | 700 | 0.2 | 22.62 | 1300000
2022-05-04 | 15500 | 15.5 | 7.18 | 7.56 | 150 | 17 | 312 | 44 | 271 | 23 | NA | 600 | 0.2 | 21.46 | 1600000
2022-05-05 | 13330 | 13.33 | 7.31 | 7.73 | 140 | 15 | 304 | 40 | 261 | 21 | NA | 500 | 0.3 | 22.53 | 1400000
2022-05-06 | 13370 | 13.37 | 7.26 | 7.51 | 145 | 18 | 320 | 36 | 280 | 24 | NA | 400 | 0.2 | 21.85 | 1300000
2022-05-07 | 14280 | 14.28 | 7.21 | 7.64 | 153 | 16 | 328 | 40 | 258 | 22 | NA | 600 | 0.3 | 23.21 | 1600000
2022-05-08 | 14790 | 14.79 | 7.16 | 7.48 | 142 | 17 | 316 | 36 | 266 | 20 | NA | 500 | 0.2 | 22.32 | 1700000
2022-05-09 | 13610 | 13.61 | 7.33 | 7.71 | 155 | 16 | 324 | 44 | 270 | 21 | NA | 400 | 0.3 | 22.69 | 1400000
2022-05-10 | 13550 | 13.55 | 7.25 | 7.54 | 146 | 15 | 312 | 40 | 268 | 23 | NA | 600 | 0.2 | 22.86 | 1200000
2022-05-11 | 13240 | 13.24 | 7.15 | 7.41 | 156 | 14 | 332 | 36 | 278 | 25 | NA | 700 | 0.2 | 23.24 | 1600000
2022-05-12 | 13090 | 13.09 | 7.27 | 7.66 | 140 | 16 | 308 | 40 | 263 | 22 | NA | 500 | 0.3 | 21.56 | 1400000
2022-05-13 | 13100 | 13.1 | 7.36 | 7.75 | 145 | 15 | 320 | 44 | 254 | 24 | NA | 600 | 0.2 | 22.37 | 1300000
2022-05-14 | 12030 | 12.03 | 7.22 | 7.55 | 135 | 16 | 304 | 48 | 269 | 26 | NA | 400 | 0.3 | 23.29 | 1600000
2022-05-15 | 12780 | 12.78 | 7.29 | 7.49 | 143 | 17 | 316 | 40 | 275 | 23 | NA | 500 | 0.2 | 21.78 | 1400000
2022-05-16 | 13130 | 13.13 | 7.17 | 7.61 | 137 | 15 | 300 | 36 | 254 | 21 | NA | 600 | 0.2 | 20.71 | 1700000
2022-05-17 | 12980 | 12.98 | 7.24 | 7.56 | 146 | 18 | 312 | 44 | 267 | 25 | NA | 500 | 0.3 | 23.38 | 1300000
2022-05-18 | 13250 | 13.25 | 7.33 | 7.68 | 140 | 16 | 324 | 36 | 248 | 22 | NA | 700 | 0.2 | 22.14 | 1400000
2022-05-19 | 13150 | 13.15 | 7.26 | 7.51 | 133 | 17 | 308 | 40 | 273 | 20 | NA | 500 | 0.2 | 21.94 | 1600000
2022-05-20 | 13410 | 13.41 | 7.19 | 7.62 | 145 | 15 | 316 | 36 | 264 | 23 | NA | 600 | 0.3 | 22.71 | 1200000
2022-05-21 | 13250 | 13.25 | 7.25 | 7.46 | 155 | 16 | 320 | 44 | 251 | 21 | NA | 700 | 0.2 | 22.54 | 1300000
2022-05-22 | 12450 | 12.45 | 7.16 | 7.53 | 148 | 14 | 304 | 40 | 285 | 24 | NA | 500 | 0.3 | 21.77 | 1600000
2022-05-23 | 11190 | 11.19 | 7.21 | 7.43 | 135 | 13 | 312 | 36 | 272 | 22 | NA | 600 | 0.2 | 22.26 | 1400000
2022-05-24 | 11790 | 11.79 | 7.31 | 7.66 | 140 | 15 | 320 | 40 | 269 | 23 | NA | 500 | 0.3 | 23.25 | 1300000
2022-05-25 | 12970 | 12.97 | 7.23 | 7.49 | 131 | 13 | 300 | 36 | 258 | 21 | NA | 400 | 0.2 | 21.56 | 1200000
2022-05-26 | 11980 | 11.98 | 7.18 | 7.57 | 138 | 14 | 316 | 32 | 276 | 19 | NA | 500 | 0.2 | 22.1 | 1400000
2022-05-27 | 11640 | 11.64 | 7.34 | 7.72 | 130 | 15 | 304 | 36 | 265 | 22 | NA | 600 | 0.3 | 21.67 | 1600000
2022-05-28 | 11390 | 11.39 | 7.24 | 7.61 | 142 | 14 | 324 | 32 | 283 | 20 | NA | 700 | 0.2 | 23.12 | 1700000
2022-05-29 | 13630 | 13.63 | 7.29 | 7.58 | 135 | 16 | 308 | 40 | 271 | 23 | NA | 500 | 0.3 | 22.19 | 1400000
2022-05-30 | 13310 | 13.31 | 7.36 | 7.69 | 145 | 13 | 328 | 36 | 280 | 21 | NA | 600 | 0.2 | 22.76 | 1300000
2022-05-31 | 13400 | 13.4 | 7.26 | 7.51 | 136 | 15 | 316 | 44 | 260 | 24 | NA | 500 | 0.2 | 21.35 | 1600000
Average | 13187.7419 | 13.1877 | 7.2542 | 7.5868 | 142.3871 | 15.3548 | 314.8387 | 39.2258 | 268.1935 | 22.4516 | NA | 551.6129 | 0.23871 | 22.3474 | 1448387.0968
| 408820 | 408.82
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11190 | 11.19 | 7.15 | 7.41 | 130 | 13 | 300 | 32 | 248 | 19 |  | 400 | 0.2 | 20.71 | 1200000
Max | 15500 | 15.5 | 7.36 | 7.75 | 156 | 18 | 332 | 48 | 286 | 26 |  | 700 | 0.3 | 23.38 | 1700000