## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-05-01 | 41260 | 41.26 | 7.29 | 7.68 | 135 | 17 | 312 | 40 | 280 | 25 | NA | 700 | 0.2 | 23.43 | 1400000 | Due to leakage in rising main to Numayadahi STP, Ghagharnalla MPS was shutdown from 1 PM on date 29/04/2024. Subsequently, Numayadahi STP & Sasurkadheri SPS were also stopped. Plant was started at 6:00 AM on 01.05.2024 after completion of work.
2024-05-02 | 58330 | 58.33 | 7.25 | 7.72 | 130 | 14 | 328 | 36 | 305 | 24 | NA | 400 | 0.3 | 22.35 | 1200000
2024-05-03 | 58200 | 58.2 | 7.28 | 7.62 | 135 | 14 | 344 | 44 | 348 | 26 | NA | 700 | 0.3 | 22.33 | 1300000
2024-05-04 | 58150 | 58.15 | 7.3 | 7.66 | 140 | 16 | 352 | 40 | 389 | 25 | NA | 500 | 0.2 | 21.93 | 1100000
2024-05-05 | 58600 | 58.6 | 7.3 | 7.69 | 130 | 15 | 320 | 44 | 300 | 27 | NA | 600 | 0.2 | 22.11 | 1200000
2024-05-06 | 58000 | 58 | 7.32 | 7.7 | 135 | 16 | 308 | 40 | 290 | 28 | NA | 700 | 0.2 | 22.33 | 1400000
2024-05-07 | 60300 | 60.3 | 7.28 | 7.69 | 140 | 15 | 304 | 44 | 285 | 26 | NA | 400 | 0.3 | 22.88 | 1300000
2024-05-08 | 59130 | 59.13 | 7.32 | 7.65 | 145 | 17 | 308 | 40 | 280 | 25 | NA | 400 | 0.3 | 23.31 | 1100000
2024-05-09 | 58700 | 58.7 | 7.35 | 7.78 | 140 | 16 | 328 | 44 | 298 | 28 | NA | 500 | 0.2 | 21.58 | 1200000
2024-05-10 | 58750 | 58.75 | 7.45 | 7.7 | 135 | 15 | 312 | 40 | 295 | 24 | NA | 600 | 0.2 | 22.33 | 1400000
2024-05-11 | 59130 | 59.13 | 7.15 | 7.87 | 150 | 17 | 340 | 40 | 264 | 29 | NA | 500 | 0.3 | 21.95 | 1300000
2024-05-12 | 57660 | 57.66 | 7.57 | 7.84 | 135 | 16 | 352 | 44 | 305 | 30 | NA | 400 | 0.2 | 22.47 | 1100000
2024-05-13 | 58770 | 58.77 | 7.45 | 7.68 | 145 | 17 | 340 | 40 | 272 | 26 | NA | 500 | 0.3 | 21.98 | 1400000
2024-05-14 | 58790 | 58.79 | 7.29 | 7.77 | 140 | 15 | 360 | 44 | 312 | 28 | NA | 600 | 0.2 | 22.03 | 1200000
2024-05-15 | 59250 | 59.25 | 7.27 | 7.79 | 145 | 16 | 352 | 40 | 335 | 27 | NA | 700 | 0.2 | 21.97 | 1700000
2024-05-16 | 58850 | 58.85 | 7.34 | 7.8 | 140 | 17 | 328 | 44 | 289 | 30 | NA | 400 | 0.3 | 22.14 | 1400000
2024-05-17 | 57190 | 57.19 | 7.65 | 7.85 | 130 | 16 | 340 | 44 | 310 | 28 | NA | 600 | 0.2 | 22.33 | 1100000
2024-05-18 | 60120 | 60.12 | 7.75 | 7.86 | 130 | 15 | 336 | 36 | 300 | 24 | NA | 500 | 0.2 | 22.55 | 1300000
2024-05-19 | 55980 | 55.98 | 7.64 | 7.77 | 145 | 16 | 320 | 44 | 296 | 27 | NA | 600 | 0.3 | 21.93 | 1400000
2024-05-20 | 53180 | 53.18 | 7.45 | 7.8 | 140 | 15 | 304 | 40 | 260 | 26 | NA | 700 | 0.2 | 22.37 | 1200000
2024-05-21 | 56700 | 56.7 | 7.3 | 7.78 | 145 | 17 | 320 | 44 | 294 | 28 | NA | 500 | 0.2 | 22.05 | 1300000
2024-05-22 | 58750 | 58.75 | 7.28 | 7.74 | 145 | 16 | 304 | 40 | 304 | 27 | NA | 600 | 0.3 | 22.23 | 1200000
2024-05-23 | 58150 | 58.15 | 7.23 | 7.78 | 140 | 15 | 332 | 44 | 316 | 28 | NA | 500 | 0.2 | 22.33 | 1100000
2024-05-24 | 60000 | 60 | 7.26 | 7.78 | 135 | 16 | 340 | 40 | 305 | 27 | NA | 700 | 0.3 | 22.41 | 1400000
2024-05-25 | 59800 | 59.8 | 7.28 | 7.77 | 140 | 14 | 344 | 36 | 312 | 25 | NA | 400 | 0.3 | 23.08 | 1300000
2024-05-26 | 53930 | 53.93 | 7.29 | 7.68 | 145 | 17 | 360 | 44 | 325 | 29 | NA | 600 | 0.3 | 22.57 | 1200000
2024-05-27 | 57340 | 57.34 | 7.25 | 7.77 | 140 | 16 | 312 | 40 | 298 | 26 | NA | 500 | 0.2 | 22.61 | 1100000
2024-05-28 | 54610 | 54.61 | 7.2 | 7.72 | 145 | 18 | 316 | 44 | 290 | 27 | NA | 700 | 0.3 | 22.43 | 1700000
2024-05-29 | 55010 | 55.01 | 7.22 | 7.8 | 145 | 17 | 300 | 40 | 218 | 28 | NA | 600 | 0.2 | 22.84 | 1700000
2024-05-30 | 55150 | 55.15 | 7.21 | 7.78 | 145 | 15 | 304 | 44 | 217 | 29 | NA | 500 | 0.2 | 22.53 | 1300000
2024-05-31 | 57990 | 57.99 | 7.2 | 7.74 | 140 | 14 | 312 | 36 | 216 | 26 | NA | 400 | 0.3 | 21.93 | 1400000
Average | 57282.9032 | 57.2829 | 7.3361 | 7.7503 | 139.6774 | 15.8065 | 326.8387 | 41.2903 | 293.8065 | 26.871 |  | 548.3871 | 0.24516 | 22.3648 | 1303225.8065
1775.77
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 41260 | 41.26 | 7.15 | 7.62 | 130 | 14 | 300 | 36 | 216 | 24 |  | 400 | 0.2 | 21.58 | 1100000
Max | 60300 | 60.3 | 7.75 | 7.87 | 150 | 18 | 360 | 44 | 389 | 30 |  | 700 | 0.3 | 23.43 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-05-01 | 35820 | 35.82 | 7.26 | 7.73 | 160 | 24 | 368 | 40 | 354 | 34 | NA | 700 | 0.3 | 23.92 | 1200000
2024-05-02 | 37760 | 37.76 | 7.14 | 7.71 | 155 | 23 | 360 | 36 | 360 | 37 | NA | 600 | 0.3 | 22.32 | 1300000
2024-05-03 | 36970 | 36.97 | 7.06 | 7.79 | 150 | 24 | 364 | 40 | 366 | 36 | NA | 400 | 0.3 | 23.14 | 1700000
2024-05-04 | 37920 | 37.92 | 7.05 | 7.64 | 165 | 25 | 344 | 44 | 345 | 39 | NA | 500 | 0.3 | 24.87 | 1400000
2024-05-05 | 38070 | 38.07 | 7.08 | 7.73 | 155 | 26 | 364 | 48 | 367 | 42 | NA | 600 | 0.3 | 23.12 | 1200000
2024-05-06 | 37310 | 37.31 | 6.97 | 7.65 | 160 | 22 | 368 | 40 | 356 | 38 | NA | 700 | 0.3 | 23.62 | 1400000
2024-05-07 | 37890 | 37.89 | 6.79 | 7.82 | 165 | 23 | 360 | 36 | 358 | 33 | NA | 400 | 0.3 | 22.22 | 1200000
2024-05-08 | 33270 | 33.27 | 7.14 | 7.55 | 150 | 24 | 352 | 44 | 314 | 35 | NA | 600 | 0.3 | 24.52 | 1100000
2024-05-09 | 37070 | 37.07 | 7.34 | 7.57 | 160 | 25 | 344 | 40 | 308 | 45 | NA | 700 | 0.3 | 22.73 | 1300000
2024-05-10 | 36460 | 36.46 | 7.31 | 7.43 | 155 | 24 | 336 | 36 | 305 | 32 | NA | 500 | 0.3 | 22.9 | 1200000
2024-05-11 | 37150 | 37.15 | 7.27 | 7.41 | 150 | 23 | 348 | 44 | 300 | 37 | NA | 500 | 0.3 | 22.44 | 1400000
2024-05-12 | 38650 | 38.65 | 7.22 | 7.48 | 165 | 26 | 344 | 48 | 304 | 40 | NA | 400 | 0.3 | 24.58 | 1700000
2024-05-13 | 37640 | 37.64 | 7.16 | 7.52 | 155 | 25 | 364 | 44 | 360 | 39 | NA | 700 | 0.3 | 23.01 | 1300000
2024-05-14 | 36530 | 36.53 | 7.13 | 7.49 | 160 | 24 | 360 | 44 | 368 | 46 | NA | 500 | 0.3 | 22.97 | 1200000
2024-05-15 | 36700 | 36.7 | 7.17 | 7.5 | 150 | 22 | 356 | 40 | 346 | 35 | NA | 600 | 0.3 | 23.78 | 1700000
2024-05-16 | 36520 | 36.52 | 7.11 | 7.46 | 145 | 24 | 364 | 36 | 370 | 38 | NA | 600 | 0.3 | 24.09 | 1100000
2024-05-17 | 36780 | 36.78 | 7.09 | 7.59 | 160 | 22 | 360 | 40 | 348 | 35 | NA | 400 | 0.3 | 22.55 | 1700000
2024-05-18 | 37960 | 37.96 | 7.1 | 7.43 | 160 | 23 | 356 | 48 | 336 | 40 | NA | 700 | 0.3 | 23.28 | 1300000
2024-05-19 | 39070 | 39.07 | 7.05 | 7.53 | 165 | 22 | 336 | 36 | 308 | 35 | NA | 500 | 0.3 | 24.39 | 1400000
2024-05-20 | 38690 | 38.69 | 7.07 | 7.47 | 155 | 24 | 360 | 44 | 342 | 40 | NA | 400 | 0.3 | 24.25 | 1700000
2024-05-21 | 35670 | 35.67 | 7.05 | 7.45 | 160 | 23 | 364 | 36 | 369 | 37 | NA | 600 | 0.3 | 23.55 | 1400000
2024-05-22 | 35030 | 35.03 | 7.04 | 7.58 | 165 | 25 | 368 | 44 | 360 | 40 | NA | 700 | 0.3 | 24.8 | 1300000
2024-05-23 | 35620 | 35.62 | 7.06 | 7.59 | 160 | 23 | 360 | 40 | 370 | 37 | NA | 400 | 0.3 | 23.63 | 1700000
2024-05-24 | 39210 | 39.21 | 7.04 | 7.62 | 155 | 22 | 356 | 36 | 362 | 39 | NA | 600 | 0.3 | 23.15 | 1200000
2024-05-25 | 38040 | 38.04 | 7.08 | 7.68 | 165 | 23 | 356 | 40 | 368 | 35 | NA | 700 | 0.3 | 23.84 | 1700000
2024-05-26 | 36960 | 36.96 | 6.98 | 7.71 | 155 | 24 | 360 | 44 | 370 | 39 | NA | 600 | 0.3 | 24.27 | 1400000
2024-05-27 | 35240 | 35.24 | 6.96 | 7.6 | 140 | 22 | 316 | 36 | 317 | 40 | NA | 400 | 0.3 | 23.19 | 1700000
2024-05-28 | 36960 | 36.96 | 6.91 | 7.75 | 155 | 23 | 348 | 44 | 366 | 39 | NA | 700 | 0.3 | 24.32 | 1300000
2024-05-29 | 35380 | 35.38 | 6.97 | 7.81 | 160 | 21 | 368 | 40 | 328 | 38 | NA | 500 | 0.3 | 24.24 | 1200000
2024-05-30 | 35710 | 35.71 | 7.14 | 7.76 | 155 | 24 | 364 | 44 | 326 | 37 | NA | 600 | 0.3 | 24.29 | 1400000
2024-05-31 | 36690 | 36.69 | 7.23 | 7.78 | 165 | 23 | 356 | 36 | 342 | 35 | NA | 400 | 0.3 | 23.84 | 1100000
Average | 36927.0968 | 36.9271 | 7.0958 | 7.6074 | 157.2581 | 23.4839 | 355.6129 | 40.9032 | 344.9355 | 37.8065 |  | 554.8387 | 0.3 | 23.6071 | 1383870.9677
1144.74
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 33270 | 33.27 | 6.79 | 7.41 | 140 | 21 | 316 | 36 | 300 | 32 |  | 400 | 0.3 | 22.22 | 1100000
Max | 39210 | 39.21 | 7.34 | 7.82 | 165 | 26 | 368 | 48 | 370 | 46 |  | 700 | 0.3 | 24.87 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-05-01 | 28600 | 28.6 | 7.22 | 7.27 | 145 | 13 | 332 | 36 | 295 | 17 | NA | 400 | 0.3 | 24.45 | 1400000
2024-05-02 | 28650 | 28.65 | 7.05 | 7.2 | 140 | 12 | 324 | 40 | 288 | 18 | NA | 700 | 0.2 | 24.1 | 1200000
2024-05-03 | 30090 | 30.09 | 6.85 | 7.19 | 135 | 13 | 316 | 36 | 276 | 15 | NA | 500 | 0.2 | 23.91 | 1100000
2024-05-04 | 29350 | 29.35 | 6.82 | 7.18 | 140 | 14 | 320 | 40 | 282 | 17 | NA | 400 | 0.3 | 23.54 | 1400000
2024-05-05 | 28450 | 28.45 | 6.97 | 7.22 | 145 | 15 | 328 | 44 | 289 | 16 | NA | 600 | 0.3 | 22.72 | 1700000
2024-05-06 | 28500 | 28.5 | 6.87 | 7.24 | 135 | 13 | 312 | 36 | 275 | 18 | NA | 500 | 0.2 | 23.37 | 1200000
2024-05-07 | 28890 | 28.89 | 6.71 | 7.27 | 140 | 14 | 320 | 40 | 283 | 17 | NA | 600 | 0.3 | 23.67 | 1300000
2024-05-08 | 30110 | 30.11 | 6.63 | 7.28 | 130 | 15 | 336 | 44 | 295 | 16 | NA | 400 | 0.3 | 22.8 | 1700000
2024-05-09 | 29900 | 29.9 | 6.92 | 7.32 | 135 | 12 | 316 | 32 | 279 | 17 | NA | 500 | 0.2 | 24.22 | 1400000
2024-05-10 | 29730 | 29.73 | 7.11 | 7.28 | 130 | 11 | 324 | 36 | 283 | 18 | NA | 400 | 0.3 | 24.3 | 1300000
2024-05-11 | 30360 | 30.36 | 7.21 | 7.32 | 135 | 14 | 312 | 40 | 286 | 16 | NA | 700 | 0.3 | 23.92 | 1200000
2024-05-12 | 29550 | 29.55 | 7.5 | 7.31 | 140 | 15 | 320 | 44 | 274 | 18 | NA | 600 | 0.3 | 22.74 | 1300000
2024-05-13 | 28220 | 28.22 | 7.43 | 7.34 | 135 | 14 | 316 | 40 | 281 | 17 | NA | 400 | 0.3 | 23.09 | 1400000
2024-05-14 | 28790 | 28.79 | 7.49 | 7.32 | 130 | 12 | 308 | 36 | 267 | 18 | NA | 800 | 0.2 | 23.46 | 1400000
2024-05-15 | 29280 | 29.28 | 7.38 | 7.33 | 135 | 13 | 312 | 40 | 262 | 17 | NA | 600 | 0.2 | 24.31 | 1300000
2024-05-16 | 28520 | 28.52 | 7.26 | 7.31 | 130 | 14 | 324 | 44 | 283 | 16 | NA | 400 | 0.3 | 24.14 | 1400000
2024-05-17 | 29940 | 29.94 | 7.23 | 7.35 | 130 | 13 | 316 | 36 | 274 | 17 | NA | 700 | 0.3 | 22.71 | 1100000
2024-05-18 | 30060 | 30.06 | 7.26 | 7.31 | 135 | 15 | 308 | 40 | 280 | 18 | NA | 600 | 0.3 | 21.87 | 1400000
2024-05-19 | 29220 | 29.22 | 7.28 | 7.32 | 130 | 16 | 300 | 44 | 257 | 16 | NA | 500 | 0.3 | 22.35 | 1200000
2024-05-20 | 29460 | 29.46 | 7.3 | 7.34 | 140 | 15 | 308 | 40 | 261 | 17 | NA | 400 | 0.3 | 23.08 | 1300000
2024-05-21 | 30020 | 30.02 | 7.47 | 7.38 | 130 | 13 | 320 | 36 | 276 | 16 | NA | 600 | 0.3 | 21.65 | 1700000
2024-05-22 | 28340 | 28.34 | 7.45 | 7.32 | 135 | 15 | 316 | 44 | 272 | 17 | NA | 500 | 0.3 | 22.81 | 1200000
2024-05-23 | 29350 | 29.35 | 7.43 | 7.37 | 140 | 13 | 308 | 40 | 268 | 15 | NA | 700 | 0.3 | 23.66 | 1300000
2024-05-24 | 30140 | 30.14 | 7.37 | 7.45 | 135 | 14 | 312 | 36 | 279 | 16 | NA | 600 | 0.3 | 23.45 | 1200000
2024-05-25 | 29100 | 29.1 | 7.44 | 7.32 | 140 | 13 | 324 | 40 | 282 | 15 | NA | 400 | 0.3 | 24.26 | 1100000
2024-05-26 | 30420 | 30.42 | 7.63 | 7.37 | 135 | 15 | 316 | 36 | 277 | 17 | NA | 500 | 0.3 | 24 | 1400000
2024-05-27 | 29880 | 29.88 | 7.64 | 7.35 | 145 | 14 | 328 | 44 | 292 | 16 | NA | 700 | 0.3 | 23.61 | 1300000
2024-05-28 | 31330 | 31.33 | 7.2 | 7.42 | 135 | 13 | 320 | 40 | 287 | 17 | NA | 400 | 0.2 | 23.27 | 1200000
2024-05-29 | 30380 | 30.38 | 6.96 | 7.4 | 140 | 14 | 332 | 36 | 295 | 16 | NA | 600 | 0.3 | 22.14 | 1700000
2024-05-30 | 28870 | 28.87 | 6.93 | 7.42 | 130 | 16 | 324 | 40 | 283 | 17 | NA | 700 | 0.3 | 24.32 | 1200000
2024-05-31 | 29990 | 29.99 | 7.05 | 7.43 | 135 | 15 | 316 | 44 | 278 | 17 | NA | 400 | 0.3 | 24.13 | 1400000
Average | 29467.4194 | 29.4674 | 7.1955 | 7.3203 | 135.9677 | 13.8065 | 318.3226 | 39.4839 | 279.3226 | 16.7097 |  | 541.9355 | 0.27742 | 23.421 | 1335483.871
913.49
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 28220 | 28.22 | 6.63 | 7.18 | 130 | 11 | 300 | 32 | 257 | 15 |  | 400 | 0.2 | 21.65 | 1100000
Max | 31330 | 31.33 | 7.64 | 7.45 | 145 | 16 | 336 | 44 | 295 | 18 |  | 800 | 0.3 | 24.45 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-05-01 | 13790 | 13.79 | 7.47 | 7.63 | 135 | 17 | 288 | 40 | 218 | 24 | NA | 600 | 0.2 | 23.89 | 1200000
2024-05-02 | 12840 | 12.84 | 7.42 | 7.66 | 140 | 16 | 296 | 36 | 232 | 21 | NA | 500 | 0.3 | 22.98 | 1700000
2024-05-03 | 13210 | 13.21 | 7.37 | 7.69 | 145 | 17 | 304 | 40 | 243 | 26 | NA | 400 | 0.2 | 22.34 | 1300000
2024-05-04 | 14190 | 14.19 | 7.44 | 7.65 | 130 | 16 | 292 | 36 | 221 | 24 | NA | 700 | 0.2 | 23.05 | 1400000
2024-05-05 | 13770 | 13.77 | 7.46 | 7.67 | 140 | 18 | 308 | 44 | 258 | 28 | NA | 600 | 0.3 | 22.38 | 1700000
2024-05-06 | 13210 | 13.21 | 7.48 | 7.68 | 145 | 15 | 316 | 40 | 256 | 29 | NA | 500 | 0.3 | 23.03 | 1200000
2024-05-07 | 13910 | 13.91 | 7.61 | 7.54 | 135 | 16 | 300 | 36 | 228 | 27 | NA | 700 | 0.2 | 23.95 | 1300000
2024-05-08 | 13170 | 13.17 | 7.59 | 7.52 | 130 | 15 | 296 | 32 | 236 | 22 | NA | 400 | 0.3 | 24.08 | 1400000
2024-05-09 | 14140 | 14.14 | 7.48 | 7.66 | 140 | 17 | 304 | 36 | 239 | 26 | NA | 600 | 0.2 | 23.76 | 1200000
2024-05-10 | 13590 | 13.59 | 7.44 | 7.63 | 135 | 16 | 308 | 40 | 248 | 27 | NA | 500 | 0.3 | 22.13 | 1700000
2024-05-11 | 13630 | 13.63 | 7.54 | 7.68 | 140 | 15 | 296 | 32 | 233 | 22 | NA | 700 | 0.2 | 21.94 | 1300000
2024-05-12 | 14110 | 14.11 | 7.46 | 7.7 | 130 | 14 | 300 | 36 | 235 | 20 | NA | 400 | 0.3 | 23.02 | 1200000
2024-05-13 | 15010 | 15.01 | 7.48 | 7.67 | 135 | 15 | 304 | 32 | 247 | 22 | NA | 600 | 0.2 | 22.87 | 1400000
2024-05-14 | 12900 | 12.9 | 7.5 | 7.72 | 140 | 16 | 292 | 36 | 232 | 21 | NA | 400 | 0.3 | 23.66 | 1300000
2024-05-15 | 12340 | 12.34 | 7.57 | 7.69 | 130 | 15 | 296 | 36 | 244 | 24 | NA | 700 | 0.2 | 23.18 | 1200000
2024-05-16 | 12660 | 12.66 | 7.56 | 7.63 | 140 | 16 | 284 | 32 | 231 | 23 | NA | 600 | 0.3 | 22.83 | 1400000
2024-05-17 | 12960 | 12.96 | 7.53 | 7.61 | 145 | 15 | 276 | 36 | 219 | 22 | NA | 500 | 0.3 | 22.15 | 1700000
2024-05-18 | 14050 | 14.05 | 7.52 | 7.66 | 135 | 17 | 284 | 44 | 213 | 27 | NA | 400 | 0.3 | 22.43 | 1300000
2024-05-19 | 12530 | 12.53 | 7.37 | 7.72 | 140 | 16 | 292 | 32 | 234 | 23 | NA | 700 | 0.2 | 22.39 | 1400000
2024-05-20 | 12900 | 12.9 | 7.58 | 7.69 | 130 | 17 | 308 | 36 | 247 | 24 | NA | 600 | 0.3 | 22.98 | 1200000
2024-05-21 | 13790 | 13.79 | 7.62 | 7.71 | 135 | 16 | 296 | 36 | 223 | 26 | NA | 400 | 0.2 | 23.27 | 1700000
2024-05-22 | 13740 | 13.74 | 7.54 | 7.68 | 145 | 14 | 312 | 32 | 254 | 23 | NA | 700 | 0.3 | 23.67 | 1300000
2024-05-23 | 13790 | 13.79 | 7.57 | 7.66 | 140 | 16 | 300 | 36 | 226 | 24 | NA | 500 | 0.2 | 23.92 | 1400000
2024-05-24 | 13260 | 13.26 | 7.59 | 7.72 | 125 | 18 | 292 | 40 | 221 | 28 | NA | 600 | 0.3 | 22.13 | 1700000
2024-05-25 | 13820 | 13.82 | 7.48 | 7.67 | 135 | 16 | 312 | 32 | 256 | 26 | NA | 400 | 0.2 | 24.08 | 1200000
2024-05-26 | 12840 | 12.84 | 7.51 | 7.65 | 145 | 15 | 308 | 36 | 248 | 24 | NA | 700 | 0.3 | 23.8 | 1300000
2024-05-27 | 13050 | 13.05 | 7.58 | 7.66 | 135 | 14 | 296 | 32 | 232 | 21 | NA | 400 | 0.2 | 24.11 | 1700000
2024-05-28 | 13210 | 13.21 | 7.59 | 7.68 | 140 | 16 | 292 | 36 | 227 | 26 | NA | 500 | 0.3 | 22.63 | 1400000
2024-05-29 | 11920 | 11.92 | 7.54 | 7.71 | 130 | 15 | 212 | 36 | 200 | 29 | NA | 600 | 0.2 | 22.47 | 1200000
2024-05-30 | 13540 | 13.54 | 7.56 | 7.68 | 135 | 16 | 288 | 36 | 221 | 25 | NA | 700 | 0.3 | 24.13 | 1700000
2024-05-31 | 12700 | 12.7 | 7.52 | 7.65 | 125 | 14 | 292 | 32 | 226 | 26 | NA | 400 | 0.2 | 22.78 | 1300000
Average | 13373.2258 | 13.3732 | 7.5152 | 7.6635 | 136.4516 | 15.7742 | 294.9677 | 36 | 233.8065 | 24.5161 |  | 548.3871 | 0.25161 | 23.0977 | 1400000
414.57
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11920 | 11.92 | 7.37 | 7.52 | 125 | 14 | 212 | 32 | 200 | 20 |  | 400 | 0.2 | 21.94 | 1200000
Max | 15010 | 15.01 | 7.62 | 7.72 | 145 | 18 | 316 | 44 | 258 | 29 |  | 700 | 0.3 | 24.13 | 1700000