## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-11-01 | 56440 | 56.44 | 7.21 | 7.67 | 140 | 16 | 324 | 40 | 316 | 20 | NA | 600 | 0.3 | 24.1 | 1400000
2022-11-02 | 57370 | 57.37 | 7.28 | 7.62 | 135 | 17 | 328 | 36 | 293 | 22 | NA | 400 | 0.3 | 22.51 | 1200000
2022-11-03 | 57010 | 57.01 | 7.18 | 7.36 | 145 | 16 | 320 | 40 | 258 | 24 | NA | 600 | 0.2 | 22.41 | 1300000
2022-11-04 | 59780 | 59.78 | 7.14 | 7.68 | 125 | 17 | 324 | 43 | 274 | 19 | NA | 800 | 0.3 | 23.7 | 1700000
2022-11-05 | 60020 | 60.02 | 7.24 | 7.64 | 135 | 18 | 320 | 32 | 289 | 22 | NA | 600 | 0.2 | 23.66 | 1400000
2022-11-06 | 53020 | 53.02 | 7.39 | 7.57 | 140 | 16 | 316 | 44 | 288 | 22 | NA | 800 | 0.3 | 23.89 | 1700000
2022-11-07 | 50400 | 50.4 | 7.26 | 7.48 | 145 | 17 | 308 | 36 | 279 | 21 | NA | 600 | 0.2 | 24.35 | 1400000
2022-11-08 | 54720 | 54.72 | 7.32 | 7.59 | 135 | 15 | 316 | 40 | 285 | 20 | NA | 700 | 0.3 | 24.63 | 1700000
2022-11-09 | 20010 | 20.01 | 7.19 | 7.64 | 140 | 16 | 328 | 32 | 274 | 22 | NA | 600 | 0.2 | 22.41 | 1300000 | Ghagharnala MPS and Sasur Kadheri SPS were in shutdown due to damage of rising main from Ghagharnalla MPS to Numayadahi STP dated 09.11.2022 at 9:50 AM to 17.11.2022 at 8:30 PM.
2022-11-10 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-11-11 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-11-12 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-11-13 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-11-14 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-11-15 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-11-16 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-11-17 | 5500 | 5.55 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-11-18 | 49250 | 49.25 | 7.28 | 7.65 | 135 | 16 | 324 | 36 | 274 | 23 | NA | 600 | 0.2 | 23.9 | 1700000
2022-11-19 | 56900 | 56.9 | 7.45 | 7.73 | 130 | 15 | 316 | 40 | 265 | 25 | NA | 400 | 0.3 | 22.61 | 1300000
2022-11-20 | 59200 | 59.2 | 7.38 | 7.75 | 140 | 13 | 324 | 36 | 272 | 25 | NA | 700 | 0.2 | 23.94 | 1400000
2022-11-21 | 58650 | 58.65 | 7.17 | 7.67 | 139 | 17 | 332 | 36 | 248 | 23 | NA | 600 | 0.3 | 21.77 | 1400000
2022-11-22 | 57120 | 57.12 | 7.22 | 7.64 | 143 | 15 | 340 | 40 | 282 | 20 | NA | 500 | 0.2 | 24.09 | 1700000
2022-11-23 | 58140 | 58.14 | 7.2 | 7.74 | 146 | 14 | 320 | 36 | 265 | 22 | NA | 600 | 0.3 | 24.23 | 1400000
2022-11-24 | 59720 | 59.72 | 7.24 | 7.69 | 136 | 16 | 312 | 32 | 246 | 19 | NA | 500 | 0.2 | 23.64 | 1700000
2022-11-25 | 59320 | 59.32 | 7.18 | 7.74 | 126 | 14 | 328 | 36 | 288 | 18 | NA | 400 | 0.3 | 22.54 | 1300000
2022-11-26 | 55750 | 55.75 | 7.19 | 7.62 | 129 | 13 | 336 | 40 | 296 | 24 | NA | 600 | 0.3 | 24.23 | 1400000
2022-11-27 | 50260 | 50.26 | 7.22 | 7.7 | 146 | 15 | 328 | 36 | 282 | 20 | NA | 400 | 0.3 | 23.89 | 1200000
2022-11-28 | 52880 | 52.88 | 7.34 | 7.6 | 136 | 13 | 320 | 40 | 256 | 19 | NA | 500 | 0.3 | 23.56 | 1700000
2022-11-29 | 52070 | 52.07 | 7.17 | 7.69 | 143 | 17 | 344 | 36 | 284 | 21 | NA | 400 | 0.3 | 25 | 1400000
2022-11-30 | 51000 | 51 | 7.14 | 7.6 | 146 | 16 | 320 | 40 | 258 | 17 | NA | 600 | 0.3 | 23.53 | 1200000
Average | 39817.6667 | 39.8193 | 7.245 | 7.6395 | 137.9545 | 15.5455 | 324 | 37.5909 | 276 | 21.2727 | NA | 568.1818 | 0.26364 | 23.5723 | 1450000
| 1194530 | 1194.58
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.14 | 7.36 | 125 | 13 | 308 | 32 | 246 | 17 |  | 400 | 0.2 | 21.77 | 1200000
Max | 60020 | 60.02 | 7.45 | 7.75 | 146 | 18 | 344 | 44 | 316 | 25 |  | 800 | 0.3 | 25 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-11-01 | 36120 | 36.12 | 7.12 | 7.22 | 159 | 25 | 336 | 40 | 315 | 28 | NA | 600 | 0.3 | 24 | 1300000
2022-11-02 | 34790 | 34.79 | 7.1 | 7.25 | 162 | 24 | 328 | 36 | 309 | 25 | NA | 500 | 0.2 | 25.2 | 1100000
2022-11-03 | 35840 | 35.84 | 7.3 | 7.59 | 156 | 24 | 348 | 40 | 312 | 27 | NA | 700 | 0.3 | 24.4 | 1400000
2022-11-04 | 34870 | 34.87 | 7.27 | 7.48 | 153 | 26 | 352 | 44 | 327 | 30 | NA | 400 | 0.3 | 25.1 | 1700000
2022-11-05 | 34230 | 34.23 | 7.41 | 7.49 | 155 | 25 | 356 | 40 | 332 | 28 | NA | 600 | 0.2 | 25.4 | 1200000
2022-11-06 | 36150 | 36.15 | 7.26 | 7.42 | 160 | 23 | 348 | 44 | 305 | 25 | NA | 800 | 0.2 | 24.6 | 1400000
2022-11-07 | 36670 | 36.67 | 7.18 | 7.45 | 165 | 21 | 336 | 40 | 315 | 27 | NA | 700 | 0.3 | 25.2 | 1300000
2022-11-08 | 35510 | 35.51 | 7.38 | 7.46 | 160 | 22 | 352 | 48 | 312 | 29 | NA | 500 | 0.2 | 22.9 | 1400000
2022-11-09 | 35310 | 35.31 | 7.32 | 7.43 | 155 | 24 | 348 | 44 | 318 | 28 | NA | 600 | 0.3 | 25.5 | 1700000
2022-11-10 | 37420 | 37.42 | 7.27 | 7.46 | 160 | 23 | 340 | 40 | 314 | 26 | NA | 500 | 0.2 | 24.3 | 1100000
2022-11-11 | 3406 | 34.06 | 7.22 | 7.48 | 155 | 21 | 344 | 36 | 317 | 27 | NA | 400 | 0.3 | 25.1 | 1200000
2022-11-12 | 34330 | 34.33 | 7.35 | 7.57 | 165 | 22 | 348 | 40 | 323 | 28 | NA | 500 | 0.3 | 24.4 | 1400000
2022-11-13 | 35220 | 35.22 | 7.31 | 7.46 | 120 | 31 | 368 | 44 | 310 | 25 | NA | 700 | 0.2 | 24.6 | 1300000
2022-11-14 | 34360 | 34.36 | 7.26 | 7.43 | 145 | 24 | 344 | 40 | 312 | 28 | NA | 600 | 0.3 | 24.8 | 1200000
2022-11-15 | 35060 | 35.06 | 7.29 | 7.52 | 155 | 26 | 352 | 36 | 298 | 30 | NA | 800 | 0.3 | 24.3 | 1100000
2022-11-16 | 33350 | 33.35 | 7.22 | 7.48 | 160 | 25 | 340 | 44 | 292 | 31 | NA | 500 | 0.3 | 25.5 | 1400000
2022-11-17 | 33440 | 33.44 | 7.28 | 7.46 | 155 | 24 | 348 | 40 | 327 | 30 | NA | 400 | 0.2 | 24.9 | 1700000
2022-11-18 | 33310 | 33.31 | 7.26 | 7.51 | 155 | 25 | 344 | 36 | 318 | 29 | NA | 600 | 0.2 | 24.4 | 1300000
2022-11-19 | 34410 | 34.41 | 7.31 | 7.53 | 160 | 24 | 352 | 40 | 322 | 27 | NA | 700 | 0.3 | 23.8 | 1400000
2022-11-20 | 33510 | 33.51 | 7.27 | 7.41 | 165 | 25 | 344 | 36 | 316 | 27 | NA | 500 | 0.2 | 23.1 | 1100000
2022-11-21 | 32280 | 32.28 | 7.3 | 7.42 | 155 | 23 | 348 | 44 | 332 | 29 | NA | 800 | 0.3 | 25.2 | 1200000
2022-11-22 | 31410 | 31.41 | 7.37 | 7.49 | 160 | 24 | 340 | 40 | 298 | 33 | NA | 600 | 0.2 | 24.8 | 1700000
2022-11-23 | 36250 | 36.25 | 7.42 | 7.59 | 155 | 25 | 360 | 44 | 336 | 37 | NA | 700 | 0.3 | 25.5 | 1300000
2022-11-24 | 32410 | 32.41 | 7.33 | 7.4 | 160 | 22 | 356 | 36 | 324 | 38 | NA | 400 | 0.3 | 25.7 | 1200000
2022-11-25 | 33690 | 33.69 | 7.39 | 7.37 | 165 | 24 | 364 | 40 | 332 | 37 | NA | 500 | 0.2 | 24.2 | 1400000
2022-11-26 | 34960 | 34.96 | 7.31 | 7.39 | 160 | 26 | 368 | 48 | 340 | 41 | NA | 700 | 0.2 | 24 | 1100000
2022-11-27 | 34460 | 34.46 | 7.39 | 7.42 | 165 | 25 | 356 | 44 | 318 | 36 | NA | 600 | 0.3 | 24.1 | 1300000
2022-11-28 | 32580 | 32.58 | 7.3 | 7.51 | 155 | 23 | 352 | 36 | 304 | 28 | NA | 800 | 0.3 | 23.7 | 1700000
2022-11-29 | 37600 | 37.6 | 7.41 | 7.5 | 155 | 25 | 376 | 40 | 297 | 28 | NA | 600 | 0.2 | 23.4 | 1400000
2022-11-30 | 35070 | 35.07 | 7.38 | 7.53 | 160 | 24 | 340 | 36 | 290 | 27 | NA | 700 | 0.3 | 23.9 | 1300000
Average | 33600.5333 | 34.6223 | 7.2993 | 7.4573 | 157 | 24.1667 | 349.6 | 40.5333 | 315.5 | 29.6333 | NA | 600 | 0.25667 | 24.5333 | 1343333.3333
1038.67
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 3406 | 31.41 | 7.1 | 7.22 | 120 | 21 | 328 | 36 | 290 | 25 |  | 400 | 0.2 | 22.9 | 1100000
Max | 37600 | 37.6 | 7.42 | 7.59 | 165 | 31 | 376 | 48 | 340 | 41 |  | 800 | 0.3 | 25.7 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-11-01 | 25450 | 25.45 | 7.26 | 7.33 | 130 | 14 | 316 | 40 | 287 | 23 | NA | 600 | 0.3 | 23.64 | 1300000
2022-11-02 | 25880 | 25.88 | 7.29 | 7.39 | 135 | 15 | 312 | 44 | 292 | 22 | NA | 400 | 0.2 | 23.87 | 1700000
2022-11-03 | 25090 | 25.09 | 7.27 | 7.35 | 140 | 16 | 296 | 32 | 301 | 19 | NA | 700 | 0.2 | 23.5 | 1400000
2022-11-04 | 25670 | 25.67 | 7.33 | 7.28 | 130 | 15 | 308 | 40 | 285 | 21 | NA | 500 | 0.3 | 24.12 | 1200000
2022-11-05 | 24560 | 24.56 | 7.25 | 7.36 | 135 | 14 | 300 | 36 | 296 | 23 | NA | 600 | 0.3 | 24.36 | 1400000 | Retaining wall for nearby nalla is broken hence raw sewage was goiing directly into the river
2022-11-06 | 25920 | 25.92 | 7.18 | 7.32 | 140 | 15 | 312 | 44 | 278 | 19 | NA | 400 | 0.2 | 23.46 | 1700000
2022-11-07 | 25470 | 25.47 | 7.31 | 7.46 | 145 | 14 | 304 | 40 | 291 | 20 | NA | 800 | 0.3 | 23.74 | 1400000
2022-11-08 | 21980 | 21.98 | 7.29 | 7.41 | 135 | 16 | 316 | 36 | 286 | 22 | NA | 600 | 0.2 | 23.92 | 1700000 | 1) Retaining wall for nearby nalla is broken hence raw sewage was goiing directly into the river. 2) Construction of retaining wall was completed on 19.11.2022 at 5:30 PM. 3) Maintenance for diffusers on Aeration tank no. 1 was started on 18.11.2022.
2022-11-09 | 21320 | 21.32 | 7.22 | 7.54 | 140 | 14 | 324 | 44 | 302 | 24 | NA | 500 | 0.3 | 24.43 | 1300000
2022-11-10 | 19890 | 19.89 | 7.36 | 7.48 | 130 | 15 | 312 | 44 | 275 | 25 | NA | 700 | 0.4 | 24.19 | 1400000
2022-11-11 | 19720 | 19.72 | 7.44 | 7.56 | 135 | 13 | 320 | 36 | 294 | 23 | NA | 800 | 0.4 | 23.76 | 1700000
2022-11-12 | 19100 | 19.1 | 7.31 | 7.49 | 145 | 15 | 308 | 44 | 283 | 22 | NA | 600 | 0.3 | 23.94 | 1300000
2022-11-13 | 19910 | 19.91 | 7.26 | 7.42 | 140 | 17 | 316 | 40 | 268 | 21 | NA | 500 | 0.3 | 24.21 | 1400000
2022-11-14 | 18670 | 18.67 | 7.41 | 7.53 | 135 | 16 | 304 | 36 | 273 | 23 | NA | 700 | 0.4 | 23.64 | 1700000
2022-11-15 | 20140 | 20.14 | 7.25 | 7.34 | 120 | 14 | 256 | 36 | 253 | 20 | NA | 800 | 0.3 | 24.08 | 1400000
2022-11-16 | 19480 | 19.48 | 7.19 | 7.39 | 130 | 15 | 272 | 40 | 261 | 22 | NA | 600 | 0.4 | 23.89 | 1300000
2022-11-17 | 18820 | 18.82 | 7.33 | 7.46 | 135 | 17 | 296 | 40 | 272 | 23 | NA | 700 | 0.3 | 23.03 | 1400000
2022-11-18 | 21760 | 21.76 | 7.26 | 7.35 | 135 | 16 | 284 | 44 | 259 | 20 | NA | 500 | 0.4 | 23.68 | 1700000
2022-11-19 | 22520 | 22.52 | 7.14 | 7.29 | 140 | 18 | 292 | 48 | 266 | 22 | NA | 800 | 0.3 | 24.21 | 1400000
2022-11-20 | 26970 | 26.97 | 7.31 | 7.43 | 130 | 16 | 288 | 40 | 281 | 18 | NA | 600 | 0.4 | 23.84 | 1300000 | Maintenance for diffusers on Aeration tank no. 1 was completed on 20.11.2022.
2022-11-21 | 16820 | 26.82 | 7.22 | 7.38 | 135 | 14 | 300 | 36 | 275 | 17 | NA | 600 | 0.3 | 24.13 | 1700000 | Maintenance for diffusers on Aeration tank no. 2 was started on 21.11.2022.
2022-11-22 | 27400 | 27.4 | 7.29 | 7.47 | 145 | 17 | 284 | 40 | 292 | 19 | NA | 800 | 0.4 | 23.46 | 1400000
2022-11-23 | 27520 | 27.52 | 7.26 | 7.21 | 140 | 15 | 320 | 36 | 303 | 22 | NA | 700 | 0.5 | 24.31 | 1300000 | Maintenance for diffusers on Aeration tank no. 2 was completed on 23.11.2022.
2022-11-24 | 27130 | 27.13 | 7.32 | 7.39 | 135 | 16 | 312 | 40 | 286 | 18 | NA | 500 | 0.4 | 23.74 | 1400000
2022-11-25 | 26820 | 26.82 | 7.19 | 7.28 | 130 | 12 | 316 | 36 | 296 | 20 | NA | 600 | 0.3 | 24.03 | 1700000
2022-11-26 | 25530 | 25.53 | 7.37 | 7.45 | 140 | 14 | 308 | 40 | 291 | 19 | NA | 800 | 0.4 | 23.58 | 1400000
2022-11-27 | 29180 | 29.18 | 7.24 | 7.36 | 145 | 15 | 324 | 44 | 284 | 22 | NA | 700 | 0.5 | 24.18 | 1300000
2022-11-28 | 28650 | 28.65 | 7.29 | 7.34 | 135 | 14 | 316 | 40 | 276 | 21 | NA | 500 | 0.4 | 23.84 | 1700000
2022-11-29 | 26060 | 26.06 | 7.09 | 7.51 | 140 | 11 | 304 | 36 | 284 | 23 | NA | 600 | 0.5 | 23.42 | 1400000
2022-11-30 | 26450 | 26.45 | 7.15 | 7.4 | 130 | 13 | 312 | 32 | 272 | 20 | NA | 800 | 0.4 | 24.09 | 1700000
Average | 23662.6667 | 23.996 | 7.2693 | 7.399 | 136 | 14.8667 | 304.4 | 39.4667 | 282.0667 | 21.1 | NA | 633.3333 | 0.34333 | 23.8763 | 1470000
719.88
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 16820 | 18.67 | 7.09 | 7.21 | 120 | 11 | 256 | 32 | 253 | 17 |  | 400 | 0.2 | 23.03 | 1200000
Max | 29180 | 29.18 | 7.44 | 7.56 | 145 | 18 | 324 | 48 | 303 | 25 |  | 800 | 0.5 | 24.43 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-11-01 | 12300 | 12.3 | 7.31 | 7.45 | 136 | 16 | 312 | 44 | 268 | 21 | NA | 800 | 0.3 | 22.96 | 1700000
2022-11-02 | 12530 | 12.53 | 7.26 | 7.37 | 133 | 15 | 304 | 40 | 279 | 24 | NA | 600 | 0.2 | 23.39 | 1400000
2022-11-03 | 12970 | 12.97 | 7.21 | 7.32 | 140 | 17 | 316 | 44 | 284 | 22 | NA | 700 | 0.3 | 23.54 | 1300000
2022-11-04 | 13040 | 13.04 | 7.69 | 7.55 | 145 | 16 | 328 | 40 | 235 | 23 | NA | 600 | 0.2 | 22.87 | 1400000
2022-11-05 | 13300 | 13.3 | 7.49 | 7.58 | 135 | 17 | 312 | 44 | 259 | 22 | NA | 800 | 0.3 | 23.27 | 1700000
2022-11-06 | 13090 | 13.09 | 7.45 | 7.61 | 130 | 15 | 320 | 48 | 269 | 24 | NA | 700 | 0.2 | 23.68 | 1400000
2022-11-07 | 13420 | 13.42 | 7.38 | 7.54 | 140 | 16 | 316 | 44 | 262 | 23 | NA | 500 | 0.3 | 22.39 | 1300000
2022-11-08 | 12810 | 12.81 | 7.28 | 7.45 | 145 | 14 | 312 | 36 | 306 | 21 | NA | 800 | 0.2 | 25.03 | 1400000
2022-11-09 | 13900 | 13.9 | 7.34 | 7.59 | 135 | 17 | 308 | 40 | 285 | 24 | NA | 700 | 0.3 | 24.67 | 1700000
2022-11-10 | 13310 | 12.31 | 7.46 | 7.55 | 140 | 16 | 320 | 44 | 294 | 22 | NA | 600 | 0.3 | 23.94 | 1400000
2022-11-11 | 12780 | 12.78 | 7.53 | 7.63 | 130 | 14 | 312 | 40 | 276 | 20 | NA | 800 | 0.4 | 23.36 | 1700000
2022-11-12 | 11640 | 11.64 | 7.37 | 7.58 | 135 | 16 | 304 | 44 | 281 | 22 | NA | 600 | 0.3 | 23.74 | 1200000
2022-11-13 | 13150 | 13.15 | 7.28 | 7.45 | 145 | 14 | 316 | 36 | 264 | 19 | NA | 700 | 0.2 | 23.52 | 1400000
2022-11-14 | 12550 | 12.55 | 7.41 | 7.53 | 135 | 16 | 308 | 44 | 286 | 21 | NA | 500 | 0.3 | 23.27 | 1300000
2022-11-15 | 11860 | 11.86 | 6.95 | 7.4 | 210 | 14 | 288 | 44 | 262 | 19 | NA | 600 | 0.4 | 24.19 | 1400000
2022-11-16 | 12380 | 12.38 | 7.16 | 7.31 | 145 | 16 | 296 | 40 | 278 | 23 | NA | 800 | 0.3 | 23.51 | 1700000
2022-11-17 | 12210 | 12.21 | 7.39 | 7.44 | 140 | 17 | 284 | 40 | 271 | 23 | NA | 700 | 0.4 | 22.86 | 1300000
2022-11-18 | 12790 | 12.79 | 7.24 | 7.37 | 135 | 15 | 292 | 44 | 284 | 21 | NA | 500 | 0.3 | 23.16 | 1400000
2022-11-19 | 12280 | 12.28 | 7.31 | 7.46 | 145 | 16 | 312 | 40 | 294 | 23 | NA | 800 | 0.2 | 23.43 | 1700000
2022-11-20 | 13020 | 13.02 | 7.13 | 7.38 | 140 | 14 | 320 | 44 | 279 | 22 | NA | 600 | 0.3 | 23.75 | 1200000
2022-11-21 | 12190 | 12.19 | 7.24 | 7.32 | 130 | 16 | 304 | 48 | 268 | 23 | NA | 700 | 0.4 | 24.17 | 1400000
2022-11-22 | 12240 | 12.24 | 7.18 | 7.43 | 135 | 15 | 296 | 40 | 274 | 21 | NA | 500 | 0.3 | 23.41 | 1700000
2022-11-23 | 11660 | 11.66 | 7.27 | 7.35 | 145 | 16 | 288 | 32 | 346 | 26 | NA | 800 | 0.4 | 23.67 | 1400000
2022-11-24 | 12310 | 12.31 | 7.21 | 7.48 | 135 | 15 | 316 | 40 | 307 | 25 | NA | 600 | 0.3 | 24.08 | 1300000
2022-11-25 | 12700 | 12.7 | 7.32 | 7.44 | 130 | 14 | 304 | 44 | 289 | 23 | NA | 700 | 0.4 | 23.67 | 1700000
2022-11-26 | 13320 | 13.32 | 7.27 | 7.35 | 140 | 14 | 324 | 40 | 301 | 21 | NA | 500 | 0.3 | 23.37 | 1400000
2022-11-27 | 13940 | 13.94 | 7.21 | 7.41 | 130 | 16 | 312 | 44 | 294 | 24 | NA | 400 | 0.4 | 23.58 | 1300000
2022-11-28 | 13400 | 13.4 | 7.31 | 7.38 | 147 | 17 | 300 | 40 | 285 | 22 | NA | 600 | 0.3 | 24.01 | 1200000
2022-11-29 | 13950 | 13.95 | 7.18 | 7.46 | 135 | 16 | 312 | 36 | 278 | 21 | NA | 600 | 0.4 | 24.32 | 1400000
2022-11-30 | 13790 | 13.79 | 7.24 | 7.53 | 140 | 14 | 304 | 40 | 290 | 23 | NA | 700 | 0.3 | 23.75 | 1700000
Average | 12827.6667 | 12.7943 | 7.3023 | 7.457 | 140.2 | 15.4667 | 308 | 41.4667 | 281.6 | 22.2667 | NA | 650 | 0.30667 | 23.6187 | 1450000
383.83
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11640 | 11.64 | 6.95 | 7.31 | 130 | 14 | 284 | 32 | 235 | 19 |  | 400 | 0.2 | 22.39 | 1200000
Max | 13950 | 13.95 | 7.69 | 7.63 | 210 | 17 | 328 | 48 | 346 | 26 |  | 800 | 0.4 | 25.03 | 1700000