## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-10-01 | 59930 | 59.93 | 7.32 | 7.71 | 133 | 15 | 300 | 40 | 263 | 26 | NA | 700 | 0.2 | 22.85 | 1200000
2022-10-02 | 59400 | 59.4 | 7.22 | 7.64 | 143 | 15 | 308 | 32 | 282 | 23 | NA | 500 | 0.3 | 23.89 | 1700000
2022-10-03 | 59420 | 59.42 | 7.27 | 7.62 | 149 | 16 | 292 | 40 | 276 | 26 | NA | 400 | 0.2 | 24.37 | 1700000
2022-10-04 | 56880 | 56.38 | 7.18 | 7.68 | 133 | 14 | 320 | 36 | 255 | 22 | NA | 600 | 0.2 | 23.8 | 1400000
2022-10-05 | 58540 | 58.54 | 7.14 | 7.67 | 139 | 17 | 300 | 32 | 278 | 24 | NA | 700 | 0.3 | 23.36 | 1200000
2022-10-06 | 60240 | 60.24 | 7.26 | 7.72 | 146 | 15 | 328 | 40 | 248 | 23 | NA | 400 | 0.3 | 22.85 | 1300000
2022-10-07 | 59220 | 59.22 | 7.14 | 7.68 | 129 | 17 | 336 | 32 | 254 | 20 | NA | 500 | 0.3 | 22.41 | 1300000
2022-10-08 | 59240 | 59.24 | 7.12 | 7.64 | 143 | 16 | 312 | 40 | 265 | 22 | NA | 600 | 0.2 | 25.47 | 1400000
2022-10-09 | 58000 | 58 | 7.21 | 7.68 | 149 | 14 | 296 | 32 | 280 | 24 | NA | 400 | 0.3 | 23.34 | 1200000
2022-10-10 | 59270 | 59.27 | 7.17 | 7.61 | 126 | 15 | 328 | 40 | 255 | 22 | NA | 600 | 0.3 | 22.33 | 1200000
2022-10-11 | 58180 | 58.18 | 7.26 | 7.54 | 133 | 16 | 336 | 36 | 289 | 23 | NA | 400 | 0.3 | 24.26 | 1300000
2022-10-12 | 61780 | 61.78 | 7.18 | 7.56 | 146 | 14 | 320 | 40 | 300 | 21 | NA | 600 | 0.3 | 23.15 | 1700000
2022-10-13 | 62760 | 62.76 | 7.16 | 7.64 | 143 | 16 | 336 | 36 | 258 | 23 | NA | 400 | 0.2 | 24.25 | 1200000
2022-10-14 | 63390 | 63.39 | 7.18 | 7.6 | 139 | 14 | 332 | 40 | 288 | 22 | NA | 500 | 0.3 | 24.47 | 1300000
2022-10-15 | 59890 | 59.89 | 7.24 | 7.67 | 143 | 12 | 320 | 36 | 259 | 20 | NA | 400 | 0.3 | 23.16 | 1200000
2022-10-16 | 63100 | 63.1 | 7.16 | 7.54 | 146 | 16 | 312 | 40 | 284 | 23 | NA | 600 | 0.3 | 24.04 | 1400000
2022-10-17 | 57340 | 57.34 | 7.19 | 7.89 | 143 | 13 | 328 | 36 | 294 | 20 | NA | 500 | 0.2 | 24.63 | 1700000
2022-10-18 | 54150 | 54.15 | 7.16 | 7.64 | 146 | 16 | 336 | 32 | 259 | 24 | NA | 400 | 0.3 | 23.3 | 1200000
2022-10-19 | 57860 | 57.86 | 7.19 | 7.54 | 139 | 16 | 360 | 40 | 268 | 22 | NA | 600 | 0.2 | 23.78 | 1300000
2022-10-20 | 61490 | 61.49 | 7.28 | 7.64 | 143 | 17 | 312 | 36 | 282 | 25 | NA | 500 | 0.2 | 24.84 | 1400000
2022-10-21 | 61320 | 61.32 | 7.23 | 7.56 | 133 | 16 | 316 | 40 | 262 | 23 | NA | 600 | 0.3 | 24.37 | 1400000
2022-10-22 | 58380 | 58.38 | 7.21 | 7.66 | 139 | 14 | 328 | 36 | 288 | 25 | NA | 400 | 0.2 | 23.5 | 1200000
2022-10-23 | 60090 | 60.09 | 7.25 | 7.54 | 136 | 15 | 312 | 32 | 256 | 19 | NA | 600 | 0.2 | 23.34 | 1300000
2022-10-24 | 65270 | 65.27 | 7.19 | 7.6 | 149 | 16 | 324 | 40 | 274 | 22 | NA | 500 | 0.3 | 22.41 | 1700000
2022-10-25 | 58550 | 58.55 | 7.18 | 7.64 | 143 | 18 | 320 | 36 | 268 | 21 | NA | 400 | 0.3 | 23.51 | 1400000
2022-10-26 | 60480 | 60.48 | 7.28 | 7.54 | 139 | 16 | 328 | 40 | 298 | 20 | NA | 600 | 0.2 | 24.97 | 1200000
2022-10-27 | 61990 | 61.99 | 7.23 | 7.66 | 143 | 17 | 324 | 44 | 303 | 22 | NA | 400 | 0.3 | 24.27 | 1300000
2022-10-28 | 59800 | 59.8 | 7.26 | 7.57 | 136 | 17 | 312 | 40 | 296 | 26 | NA | 600 | 0.3 | 23.22 | 1700000
2022-10-29 | 58810 | 58.81 | 7.28 | 7.64 | 146 | 15 | 320 | 36 | 307 | 23 | NA | 500 | 0.2 | 23.89 | 1400000
2022-10-30 | 60010 | 60.01 | 7.22 | 7.58 | 143 | 18 | 304 | 32 | 288 | 20 | NA | 400 | 0.3 | 24.09 | 1200000
2022-10-31 | 57400 | 57.4 | 7.18 | 7.61 | 145 | 16 | 316 | 40 | 297 | 23 | NA | 500 | 0.2 | 23.69 | 1300000
Average | 59747.7419 | 59.7316 | 7.211 | 7.6294 | 140.7419 | 15.5484 | 319.871 | 37.1613 | 276.5806 | 22.5484 | NA | 509.6774 | 0.25806 | 23.7358 | 1367741.9355
1851.68
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 54150 | 54.15 | 7.12 | 7.54 | 126 | 12 | 292 | 32 | 248 | 19 |  | 400 | 0.2 | 22.33 | 1200000
Max | 65270 | 65.27 | 7.32 | 7.89 | 149 | 18 | 360 | 44 | 307 | 26 |  | 700 | 0.3 | 25.47 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-10-01 | 34620 | 34.62 | 7.22 | 7.39 | 156 | 22 | 356 | 36 | 292 | 28 | NA | 500 | 0.3 | 25.9 | 1200000
2022-10-02 | 33420 | 33.42 | 7.18 | 7.32 | 163 | 20 | 340 | 44 | 304 | 28 | NA | 400 | 0.3 | 25.5 | 1100000
2022-10-03 | 33350 | 33.35 | 7.31 | 7.38 | 159 | 22 | 352 | 36 | 308 | 27 | NA | 700 | 0.2 | 25.3 | 1200000
2022-10-04 | 33770 | 33.77 | 7.22 | 7.43 | 164 | 26 | 356 | 40 | 311 | 24 | NA | 600 | 0.3 | 23.8 | 1300000
2022-10-05 | 33220 | 33.22 | 7.29 | 7.42 | 156 | 23 | 348 | 36 | 306 | 26 | NA | 400 | 0.2 | 25.3 | 1700000
2022-10-06 | 34850 | 34.85 | 7.26 | 7.38 | 159 | 26 | 356 | 40 | 314 | 25 | NA | 700 | 0.3 | 22.7 | 1400000
2022-10-07 | 33420 | 33.42 | 7.23 | 7.56 | 153 | 24 | 348 | 36 | 298 | 27 | NA | 500 | 0.3 | 24.5 | 1200000
2022-10-08 | 33140 | 33.14 | 7.19 | 7.62 | 156 | 21 | 352 | 40 | 304 | 23 | NA | 400 | 0.2 | 25 | 1300000
2022-10-09 | 34430 | 34.43 | 7.26 | 7.59 | 163 | 23 | 360 | 44 | 312 | 27 | NA | 700 | 0.2 | 24.4 | 1400000
2022-10-10 | 33440 | 33.44 | 7.22 | 7.48 | 150 | 21 | 348 | 36 | 306 | 30 | NA | 600 | 0.3 | 24.6 | 1100000
2022-10-11 | 35340 | 35.34 | 7.72 | 7.52 | 153 | 20 | 325 | 44 | 303 | 27 | NA | 400 | 0.2 | 25.3 | 1200000
2022-10-12 | 31520 | 31.52 | 7.32 | 7.59 | 156 | 24 | 356 | 40 | 308 | 31 | NA | 700 | 0.3 | 24.2 | 1200000
2022-10-13 | 10560 | 10.56 | 7.19 | 7.44 | 159 | 22 | 344 | 44 | 294 | 28 | NA | 500 | 0.2 | 25.2 | 1300000 | 1. Tapping point at Amitabh bachchan culvert is closed at 2:30 AM on 13.10.2022 due to increase in river level. 2. Inlet gate for raw sewage from Allahpur drain were closed at 4:30 AM on 13.10.2022 by flood department due to increase in river level. 3. Currently, raw sewage is being received from house connections only.
2022-10-14 | 8470 | 8.47 | 7.27 | 7.56 | 163 | 23 | 356 | 40 | 307 | 26 | NA | 600 | 0.3 | 25 | 1700000
2022-10-15 | 15790 | 15.79 | 7.21 | 7.48 | 153 | 22 | 332 | 36 | 298 | 24 | NA | 400 | 0.3 | 25.4 | 1400000
2022-10-16 | 13640 | 13.64 | 7.28 | 7.54 | 156 | 20 | 344 | 44 | 312 | 27 | NA | 700 | 0.3 | 26.1 | 1400000
2022-10-17 | 9250 | 9.25 | 7.24 | 7.57 | 162 | 19 | 340 | 40 | 296 | 24 | NA | 500 | 0.3 | 26.5 | 1100000
2022-10-18 | 17530 | 17.53 | 7.28 | 7.52 | 159 | 21 | 352 | 36 | 292 | 28 | NA | 400 | 0.2 | 25.4 | 1700000
2022-10-19 | 12270 | 21.27 | 7.18 | 7.43 | 156 | 20 | 360 | 40 | 304 | 25 | NA | 800 | 0.2 | 26.6 | 1300000
2022-10-20 | 34510 | 34.51 | 7.26 | 7.65 | 153 | 22 | 348 | 44 | 315 | 26 | NA | 600 | 0.3 | 25 | 1400000 | 1. Tapping point at Amitabh bachchan culvert is opened at 5:00 AM on 20.10.2022 due to increase in river level. 2. Inlet gate for raw sewage from Allahpur drain was opened at 5:00 AM on 20.10.2022 by flood department due to increase in river level. 3. Currently, complete raw sewage is being received inside STP.
2022-10-21 | 35880 | 35.88 | 7.28 | 7.57 | 156 | 21 | 352 | 40 | 298 | 30 | NA | 700 | 0.2 | 25.3 | 1100000
2022-10-22 | 35140 | 35.14 | 7.31 | 7.43 | 159 | 23 | 356 | 44 | 310 | 28 | NA | 500 | 0.3 | 25.1 | 1200000
2022-10-23 | 35690 | 35.69 | 7.27 | 7.49 | 156 | 22 | 364 | 40 | 304 | 31 | NA | 400 | 0.3 | 23.7 | 1100000
2022-10-24 | 36980 | 36.98 | 7.3 | 7.51 | 162 | 24 | 360 | 36 | 316 | 29 | NA | 600 | 0.2 | 23.8 | 1400000
2022-10-25 | 37910 | 37.91 | 7.26 | 7.56 | 153 | 23 | 364 | 44 | 324 | 28 | NA | 700 | 0.2 | 24.9 | 1300000
2022-10-26 | 36810 | 36.81 | 7.25 | 7.47 | 146 | 21 | 352 | 44 | 312 | 26 | NA | 800 | 0.2 | 25.5 | 1200000
2022-10-27 | 33040 | 33.04 | 7.29 | 7.49 | 156 | 22 | 348 | 40 | 314 | 25 | NA | 500 | 0.3 | 25.4 | 1700000
2022-10-28 | 35510 | 35.51 | 7.26 | 7.59 | 153 | 24 | 320 | 36 | 308 | 27 | NA | 400 | 0.3 | 24.3 | 1100000
2022-10-29 | 34490 | 34.49 | 7.19 | 7.44 | 159 | 23 | 356 | 44 | 294 | 28 | NA | 700 | 0.2 | 25.4 | 1300000
2022-10-30 | 33140 | 33.14 | 7.27 | 7.36 | 156 | 22 | 352 | 36 | 304 | 23 | NA | 600 | 0.3 | 24.2 | 1200000
2022-10-31 | 33860 | 33.86 | 7.18 | 7.43 | 153 | 20 | 316 | 40 | 305 | 27 | NA | 500 | 0.2 | 25.4 | 1400000
Average | 29515.8065 | 29.8061 | 7.2642 | 7.4906 | 156.7097 | 22.129 | 348.8065 | 40 | 305.5806 | 26.871 | NA | 564.5161 | 0.25484 | 24.9903 | 1309677.4194
923.99
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 8470 | 8.47 | 7.18 | 7.32 | 146 | 19 | 316 | 36 | 292 | 23 |  | 400 | 0.2 | 22.7 | 1100000
Max | 37910 | 37.91 | 7.72 | 7.65 | 164 | 26 | 364 | 44 | 324 | 31 |  | 800 | 0.3 | 26.6 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-10-01 | 26830 | 26.83 | 7.19 | 7.36 | 133 | 12 | 324 | 40 | 292 | 23 | NA | 600 | 0.3 | 23.64 | 1400000 | Retaining wall for the nearby nalla at Kodra MPS is broken hence raw sewage is going directly into the river.
2022-10-02 | 27180 | 27.18 | 7.32 | 7.45 | 130 | 13 | 308 | 32 | 276 | 21 | NA | 400 | 0.2 | 22.48 | 1200000
2022-10-03 | 26370 | 26.37 | 7.27 | 7.35 | 136 | 15 | 316 | 36 | 264 | 20 | NA | 700 | 0.3 | 23.79 | 1300000
2022-10-04 | 26800 | 26.8 | 7.24 | 7.31 | 140 | 14 | 304 | 32 | 279 | 22 | NA | 500 | 0.3 | 24.29 | 1700000
2022-10-05 | 26330 | 26.33 | 7.34 | 7.43 | 133 | 12 | 312 | 40 | 282 | 19 | NA | 600 | 0.2 | 23.89 | 1400000
2022-10-06 | 27510 | 27.51 | 7.41 | 7.28 | 143 | 15 | 324 | 36 | 294 | 21 | NA | 400 | 0.3 | 24.37 | 1300000
2022-10-07 | 27560 | 27.56 | 7.32 | 7.39 | 136 | 14 | 316 | 40 | 273 | 18 | NA | 500 | 0.2 | 22.86 | 1200000
2022-10-08 | 26890 | 26.89 | 7.26 | 7.34 | 140 | 12 | 304 | 32 | 287 | 20 | NA | 700 | 0.3 | 24.03 | 1400000
2022-10-09 | 25780 | 25.78 | 7.37 | 7.48 | 133 | 14 | 320 | 36 | 279 | 21 | NA | 600 | 0.2 | 23.57 | 1300000
2022-10-10 | 25840 | 25.84 | 7.29 | 7.37 | 143 | 16 | 324 | 40 | 268 | 19 | NA | 400 | 0.3 | 24.28 | 1700000
2022-10-11 | 26750 | 26.75 | 7.41 | 7.54 | 130 | 12 | 312 | 32 | 286 | 21 | NA | 500 | 0.3 | 23.41 | 1300000
2022-10-12 | 27630 | 27.63 | 7.32 | 7.43 | 136 | 14 | 332 | 36 | 293 | 20 | NA | 800 | 0.2 | 24.31 | 1400000
2022-10-13 | 29770 | 29.77 | 7.26 | 7.38 | 140 | 16 | 324 | 40 | 282 | 18 | NA | 700 | 0.3 | 23.84 | 1300000
2022-10-14 | 27980 | 27.98 | 7.32 | 7.41 | 130 | 15 | 332 | 36 | 279 | 17 | NA | 600 | 0.2 | 24.44 | 1700000
2022-10-15 | 28400 | 28.4 | 7.41 | 7.59 | 136 | 13 | 320 | 40 | 272 | 20 | NA | 400 | 0.3 | 24.14 | 1200000
2022-10-16 | 29250 | 29.25 | 7.28 | 7.38 | 126 | 11 | 312 | 32 | 288 | 22 | NA | 700 | 0.2 | 23.48 | 1400000
2022-10-17 | 28020 | 28.02 | 7.32 | 7.45 | 133 | 12 | 304 | 28 | 268 | 19 | NA | 500 | 0.3 | 23.81 | 1300000
2022-10-18 | 28660 | 28.66 | 7.22 | 7.15 | 130 | 11 | 320 | 32 | 284 | 21 | NA | 800 | 0.3 | 24.29 | 1700000
2022-10-19 | 28390 | 28.39 | 7.18 | 7.28 | 136 | 12 | 312 | 36 | 273 | 20 | NA | 600 | 0.2 | 23.58 | 1400000 | 1. Inlet gate at tapping point for nearby drain is closed at around 8:30 AM on 19.10.2022 due to rise in water level of Yamuna river due to flood. 2. Currently, raw sewage is being received from Vivekanand park SPS and Kalimandir SPS. 3. Retaining wall for the nearby nalla at Kodra MPS is broken hence raw sewage is going directly into the river.
2022-10-20 | 26310 | 26.31 | 7.27 | 7.36 | 133 | 13 | 324 | 32 | 289 | 21 | NA | 500 | 0.3 | 24.46 | 1300000
2022-10-21 | 26970 | 26.97 | 7.14 | 7.22 | 140 | 12 | 316 | 40 | 278 | 22 | NA | 700 | 0.2 | 24.05 | 1400000
2022-10-22 | 26470 | 26.47 | 7.21 | 7.29 | 136 | 14 | 308 | 36 | 282 | 18 | NA | 400 | 0.3 | 23.78 | 1200000
2022-10-23 | 26140 | 26.14 | 7.28 | 7.36 | 143 | 16 | 320 | 44 | 269 | 21 | NA | 700 | 0.2 | 23.94 | 1700000
2022-10-24 | 28840 | 28.84 | 7.26 | 7.41 | 140 | 15 | 312 | 40 | 275 | 19 | NA | 600 | 0.3 | 24.29 | 1300000 | 1. Inlet gate at tapping point for nearby drain is opened at around 11:40 AM on 24.10.2022 after water level has gobe down in Yamuna river due to flood. 2. Currently, complete raw sewage is coming inisde the STP. 3. Retaining wall for the nearby nalla at Kodra MPS is broken hence raw sewage is going directly into the river.
2022-10-25 | 29540 | 29.54 | 7.31 | 7.27 | 146 | 12 | 304 | 36 | 284 | 22 | NA | 500 | 0.3 | 23.64 | 1200000 | Retaining wall for the nearby nalla at Kodra MPS is broken hence raw sewage is going directly into the river.
2022-10-26 | 28230 | 28.23 | 7.22 | 7.36 | 136 | 13 | 300 | 32 | 264 | 21 | NA | 800 | 0.2 | 24.46 | 1400000
2022-10-27 | 28260 | 28.26 | 7.28 | 7.39 | 143 | 15 | 312 | 40 | 278 | 23 | NA | 700 | 0.3 | 23.88 | 1300000
2022-10-28 | 27740 | 27.74 | 7.19 | 7.31 | 140 | 14 | 304 | 36 | 288 | 20 | NA | 400 | 0.2 | 23.53 | 1700000
2022-10-29 | 27410 | 27.41 | 7.25 | 7.43 | 136 | 16 | 312 | 32 | 282 | 23 | NA | 600 | 0.3 | 24.16 | 1400000
2022-10-30 | 25670 | 25.67 | 7.31 | 7.47 | 143 | 14 | 320 | 40 | 265 | 22 | NA | 500 | 0.3 | 23.39 | 1200000
2022-10-31 | 25760 | 25.76 | 7.21 | 7.36 | 136 | 13 | 308 | 44 | 276 | 20 | NA | 800 | 0.2 | 24.37 | 1400000
Average | 27396.129 | 27.3961 | 7.2794 | 7.3742 | 136.6452 | 13.5484 | 314.8387 | 36.3871 | 279 | 20.4516 | NA | 587.0968 | 0.25806 | 23.8855 | 1390322.5806
849.28
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 25670 | 25.67 | 7.14 | 7.15 | 126 | 11 | 300 | 28 | 264 | 17 |  | 400 | 0.2 | 22.48 | 1200000
Max | 29770 | 29.77 | 7.41 | 7.59 | 146 | 16 | 332 | 44 | 294 | 23 |  | 800 | 0.3 | 24.46 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-10-01 | 12870 | 12.78 | 7.25 | 7.51 | 133 | 16 | 308 | 44 | 270 | 24 | NA | 500 | 0.2 | 23.11 | 1400000
2022-10-02 | 9640 | 9.64 | 7.16 | 7.48 | 130 | 15 | 300 | 40 | 264 | 22 | NA | 600 | 0.3 | 22.76 | 1300000 | Raw sewage was bypassed from MPS due to maintenance of gravity main to MPS at 5:00 PM on 02.10.2022
2022-10-03 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | 21.86 | 1700000
2022-10-04 | 2980 | 2.98 | 7.21 | 7.45 | 136 | 16 | 296 | 36 | 268 | 20 | NA | 700 | 0.2 | 21.58 | 1200000 | Raw sewage started coming into the MPS after completion of maintenance work for gravity main to MPS at 5:30 PM on 04.10.2022
2022-10-05 | 8860 | 8.86 | 7.26 | 7.46 | 140 | 14 | 312 | 40 | 274 | 23 | NA | 500 | 0.3 | 22.35 | 1300000
2022-10-06 | 12370 | 12.37 | 7.18 | 7.61 | 146 | 13 | 320 | 36 | 280 | 21 | NA | 600 | 0.2 | 21.44 | 1400000
2022-10-07 | 11450 | 11.45 | 7.29 | 7.49 | 143 | 15 | 308 | 44 | 270 | 24 | NA | 400 | 0.3 | 22.67 | 1700000
2022-10-08 | 13060 | 13.06 | 7.24 | 7.53 | 140 | 14 | 316 | 40 | 266 | 22 | NA | 600 | 0.2 | 23.24 | 1200000
2022-10-09 | 14160 | 14.16 | 7.31 | 7.58 | 136 | 15 | 304 | 36 | 278 | 20 | NA | 500 | 0.3 | 22.89 | 1400000
2022-10-10 | 13980 | 13.98 | 7.36 | 7.43 | 146 | 17 | 312 | 40 | 255 | 24 | NA | 700 | 0.2 | 21.73 | 1300000
2022-10-11 | 13930 | 13.93 | 7.22 | 7.63 | 143 | 16 | 324 | 44 | 261 | 23 | NA | 500 | 0.2 | 21.28 | 1200000
2022-10-12 | 13110 | 13.11 | 7.33 | 7.46 | 133 | 17 | 316 | 40 | 273 | 21 | NA | 600 | 0.3 | 22.53 | 1400000
2022-10-13 | 13390 | 13.39 | 7.27 | 7.54 | 140 | 15 | 320 | 36 | 266 | 22 | NA | 700 | 0.2 | 23.28 | 1300000
2022-10-14 | 13470 | 13.47 | 7.31 | 7.51 | 146 | 16 | 312 | 40 | 281 | 20 | NA | 500 | 0.3 | 22.74 | 1700000
2022-10-15 | 13410 | 13.41 | 7.27 | 7.46 | 153 | 15 | 332 | 48 | 296 | 24 | NA | 400 | 0.2 | 22.15 | 1200000
2022-10-16 | 13150 | 13.15 | 7.24 | 7.48 | 143 | 17 | 324 | 44 | 286 | 22 | NA | 600 | 0.3 | 21.96 | 1400000
2022-10-17 | 13040 | 13.04 | 7.18 | 7.55 | 136 | 16 | 316 | 48 | 271 | 21 | NA | 500 | 0.3 | 22.45 | 1300000
2022-10-18 | 13400 | 13.4 | 7.25 | 7.52 | 130 | 15 | 308 | 44 | 266 | 23 | NA | 700 | 0.2 | 23.18 | 1400000
2022-10-19 | 13200 | 13.2 | 7.28 | 7.47 | 140 | 16 | 320 | 40 | 276 | 22 | NA | 500 | 0.3 | 22.84 | 1200000
2022-10-20 | 13520 | 13.52 | 7.23 | 7.56 | 136 | 14 | 312 | 36 | 270 | 20 | NA | 600 | 0.2 | 21.54 | 1300000
2022-10-21 | 12940 | 12.94 | 7.17 | 7.36 | 143 | 17 | 304 | 40 | 263 | 21 | NA | 400 | 0.3 | 22.36 | 1200000
2022-10-22 | 12780 | 12.78 | 7.22 | 7.32 | 136 | 16 | 316 | 44 | 273 | 22 | NA | 700 | 0.2 | 23.43 | 1400000
2022-10-23 | 14230 | 14.23 | 7.28 | 7.39 | 140 | 17 | 308 | 48 | 281 | 24 | NA | 600 | 0.3 | 23.68 | 1300000
2022-10-24 | 13590 | 13.59 | 7.19 | 7.28 | 133 | 16 | 320 | 44 | 269 | 22 | NA | 400 | 0.2 | 23.28 | 1700000
2022-10-25 | 12540 | 12.54 | 7.24 | 7.43 | 143 | 17 | 308 | 40 | 276 | 23 | NA | 500 | 0.2 | 23.94 | 1200000
2022-10-26 | 13090 | 13.09 | 7.29 | 7.37 | 136 | 15 | 316 | 44 | 265 | 21 | NA | 700 | 0.3 | 23.56 | 1400000
2022-10-27 | 12300 | 12.3 | 7.19 | 7.32 | 140 | 14 | 308 | 40 | 281 | 24 | NA | 600 | 0.2 | 22.78 | 1300000
2022-10-28 | 13140 | 13.14 | 7.31 | 7.42 | 133 | 16 | 312 | 44 | 272 | 23 | NA | 400 | 0.3 | 23.14 | 1700000
2022-10-29 | 12250 | 12.25 | 7.24 | 7.37 | 136 | 15 | 320 | 40 | 289 | 24 | NA | 800 | 0.3 | 22.86 | 1400000
2022-10-30 | 12660 | 12.66 | 7.29 | 7.48 | 143 | 17 | 308 | 44 | 274 | 22 | NA | 500 | 0.2 | 23.3 | 1200000
2022-10-31 | 12580 | 12.58 | 7.14 | 7.29 | 136 | 15 | 316 | 48 | 284 | 23 | NA | 700 | 0.3 | 23.74 | 1400000
Average | 12099.6774 | 12.0968 | 7.2467 | 7.4583 | 138.9667 | 15.5667 | 313.2 | 41.7333 | 273.2667 | 22.2333 | NA | 566.6667 | 0.25 | 22.6984 | 1370967.7419
375
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.14 | 7.28 | 130 | 13 | 296 | 36 | 255 | 20 |  | 400 | 0.2 | 21.28 | 1200000
Max | 14230 | 14.23 | 7.36 | 7.63 | 153 | 17 | 332 | 48 | 296 | 24 |  | 800 | 0.3 | 23.94 | 1700000