## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-10-01 | 61850 | 61.85 | 7.21 | 7.74 | 130 | 16 | 312 | 40 | 262 | 23 | NA | 700 | 0.3 | 24.17 | 1400000
2023-10-02 | 61800 | 61.8 | 7.18 | 7.76 | 140 | 17 | 304 | 44 | 272 | 25 | NA | 600 | 0.3 | 23.78 | 1300000
2023-10-03 | 63700 | 63.7 | 7.28 | 7.67 | 125 | 14 | 316 | 40 | 268 | 24 | NA | 400 | 0.2 | 24.04 | 1400000
2023-10-04 | 66200 | 66.2 | 7.16 | 7.7 | 135 | 16 | 300 | 40 | 258 | 22 | NA | 600 | 0.3 | 22.99 | 1700000
2023-10-05 | 63750 | 63.75 | 7.21 | 7.74 | 130 | 15 | 320 | 44 | 272 | 24 | NA | 500 | 0.2 | 22.88 | 1300000
2023-10-06 | 63260 | 63.26 | 7.24 | 7.8 | 130 | 16 | 312 | 40 | 266 | 25 | NA | 700 | 0.3 | 23.57 | 1700000
2023-10-07 | 60250 | 60.25 | 7.21 | 7.78 | 140 | 18 | 316 | 44 | 278 | 25 | NA | 400 | 0.3 | 22.99 | 1100000
2023-10-08 | 62650 | 62.65 | 7.19 | 7.76 | 135 | 15 | 296 | 36 | 254 | 23 | NA | 600 | 0.2 | 24.37 | 1400000
2023-10-09 | 62750 | 62.75 | 7.26 | 7.82 | 140 | 16 | 304 | 40 | 266 | 24 | NA | 600 | 0.3 | 24.16 | 1700000
2023-10-10 | 62600 | 62.6 | 7.22 | 7.74 | 130 | 16 | 316 | 44 | 272 | 25 | NA | 500 | 0.3 | 23.75 | 1400000
2023-10-11 | 61600 | 61.6 | 7.18 | 7.78 | 145 | 18 | 320 | 44 | 270 | 24 | NA | 400 | 0.2 | 24.5 | 1300000
2023-10-12 | 61320 | 61.32 | 7.21 | 7.76 | 140 | 17 | 308 | 40 | 251 | 22 | NA | 700 | 0.3 | 23.54 | 1400000
2023-10-13 | 62430 | 62.43 | 7.16 | 7.68 | 130 | 15 | 312 | 44 | 272 | 23 | NA | 500 | 0.3 | 22.85 | 1700000
2023-10-14 | 61120 | 61.12 | 7.13 | 7.72 | 145 | 17 | 300 | 40 | 267 | 22 | NA | 600 | 0.3 | 22.99 | 1300000
2023-10-15 | 62500 | 62.5 | 7.16 | 7.78 | 140 | 17 | 320 | 44 | 254 | 24 | NA | 400 | 0.2 | 24.97 | 1400000
2023-10-16 | 61580 | 61.58 | 7.14 | 7.72 | 130 | 15 | 304 | 36 | 258 | 25 | NA | 500 | 0.2 | 24.32 | 1300000
2023-10-17 | 61350 | 61.35 | 7.22 | 7.68 | 135 | 16 | 296 | 40 | 248 | 23 | NA | 700 | 0.3 | 23.8 | 1700000
2023-10-18 | 58800 | 58.8 | 7.19 | 7.74 | 145 | 18 | 324 | 44 | 269 | 24 | NA | 400 | 0.3 | 24.68 | 1300000
2023-10-19 | 61340 | 61.34 | 7.22 | 7.84 | 130 | 16 | 344 | 40 | 280 | 25 | NA | 600 | 0.3 | 22.41 | 1400000
2023-10-20 | 63030 | 63.03 | 7.26 | 7.78 | 140 | 16 | 320 | 36 | 268 | 23 | NA | 500 | 0.2 | 23.64 | 1700000
2023-10-21 | 59390 | 59.39 | 7.22 | 7.67 | 135 | 15 | 324 | 40 | 272 | 25 | NA | 700 | 0.3 | 23.08 | 1400000
2023-10-22 | 59500 | 59.5 | 7.18 | 7.72 | 130 | 16 | 316 | 44 | 282 | 24 | NA | 600 | 0.3 | 24.04 | 1100000
2023-10-23 | 60350 | 60.35 | 7.26 | 7.78 | 130 | 15 | 292 | 36 | 263 | 22 | NA | 400 | 0.2 | 23.78 | 1400000 | Due to malfunctioning in inlet flowmeter, cumulative readings from SCADA reports are considered for calculatiing inlet flow
2023-10-24 | 61200 | 61.2 | 7.22 | 7.66 | 135 | 15 | 300 | 40 | 269 | 23 | NA | 700 | 0.3 | 23.35 | 1300000
2023-10-25 | 61360 | 61.36 | 7.18 | 7.74 | 140 | 17 | 312 | 44 | 273 | 22 | NA | 400 | 0.3 | 24.42 | 1100000
2023-10-26 | 59700 | 59.7 | 7.21 | 7.7 | 130 | 16 | 320 | 44 | 276 | 25 | NA | 600 | 0.2 | 24.4 | 1400000
2023-10-27 | 57620 | 57.62 | 7.26 | 7.74 | 140 | 16 | 316 | 40 | 268 | 24 | NA | 400 | 0.3 | 22.46 | 1400000
2023-10-28 | 58300 | 58.3 | 7.18 | 7.77 | 140 | 17 | 304 | 40 | 262 | 22 | NA | 500 | 0.3 | 24.29 | 1100000
2023-10-29 | 62170 | 62.17 | 7.26 | 7.72 | 130 | 15 | 312 | 44 | 271 | 24 | NA | 700 | 0.3 | 23.24 | 1700000
2023-10-30 | 61300 | 61.3 | 7.21 | 7.76 | 135 | 16 | 300 | 40 | 266 | 23 | NA | 600 | 0.2 | 23.57 | 1300000
2023-10-31 | 60550 | 60.55 | 7.16 | 7.78 | 140 | 17 | 304 | 44 | 258 | 22 | NA | 400 | 0.3 | 24.32 | 1200000
Average | 61461.9355 | 61.4619 | 7.2055 | 7.7429 | 135.4839 | 16.0968 | 311.0968 | 41.1613 | 266.6129 | 23.5806 | NA | 545.1613 | 0.26774 | 23.721 | 1396774.1935
1905.32
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 57620 | 57.62 | 7.13 | 7.66 | 125 | 14 | 292 | 36 | 248 | 22 |  | 400 | 0.2 | 22.41 | 1100000
Max | 66200 | 66.2 | 7.28 | 7.84 | 145 | 18 | 344 | 44 | 282 | 25 |  | 700 | 0.3 | 24.97 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-10-01 | 32730 | 32.73 | 7.29 | 7.42 | 155 | 23 | 332 | 44 | 295 | 31 | NA | 500 | 0.2 | 23.6 | 1400000
2023-10-02 | 37500 | 37.5 | 7.33 | 7.48 | 165 | 24 | 340 | 40 | 305 | 29 | NA | 600 | 0.3 | 24.1 | 1100000
2023-10-03 | 38270 | 38.27 | 7.32 | 7.39 | 160 | 27 | 344 | 40 | 302 | 28 | NA | 700 | 0.2 | 21.1 | 1700000
2023-10-04 | 37890 | 37.89 | 7.28 | 7.35 | 150 | 24 | 352 | 36 | 295 | 30 | NA | 600 | 0.3 | 22.1 | 1300000
2023-10-05 | 41410 | 41.41 | 7.23 | 7.5 | 155 | 21 | 332 | 40 | 308 | 32 | NA | 500 | 0.3 | 23.5 | 1400000
2023-10-06 | 39460 | 39.46 | 7.3 | 7.41 | 160 | 23 | 348 | 36 | 296 | 33 | NA | 400 | 0.2 | 24.9 | 1100000
2023-10-07 | 39920 | 39.92 | 7.18 | 7.27 | 155 | 22 | 328 | 40 | 305 | 30 | NA | 700 | 0.3 | 23.7 | 1300000
2023-10-08 | 40170 | 40.17 | 7.13 | 7.35 | 165 | 27 | 344 | 44 | 314 | 32 | NA | 600 | 0.3 | 24.2 | 1700000
2023-10-09 | 39260 | 39.26 | 7.2 | 7.33 | 160 | 25 | 352 | 40 | 309 | 36 | NA | 400 | 0.3 | 23.5 | 1400000
2023-10-10 | 36350 | 36.35 | 7.09 | 7.22 | 155 | 24 | 344 | 44 | 308 | 35 | NA | 500 | 0.2 | 24.4 | 1100000
2023-10-11 | 36360 | 36.36 | 7.15 | 7.37 | 160 | 23 | 356 | 40 | 292 | 34 | NA | 700 | 0.3 | 24.9 | 1700000
2023-10-12 | 37120 | 37.12 | 7.1 | 7.41 | 150 | 22 | 360 | 36 | 310 | 32 | NA | 500 | 0.2 | 23.2 | 1300000
2023-10-13 | 37070 | 37.07 | 7.21 | 7.38 | 155 | 24 | 352 | 44 | 316 | 36 | NA | 600 | 0.3 | 23.1 | 1400000
2023-10-14 | 38150 | 38.15 | 7.29 | 7.35 | 165 | 23 | 356 | 40 | 335 | 38 | NA | 700 | 0.3 | 23.9 | 1100000
2023-10-15 | 39490 | 39.49 | 7.27 | 7.39 | 160 | 23 | 364 | 40 | 317 | 33 | NA | 400 | 0.2 | 22.9 | 1300000
2023-10-16 | 36470 | 36.47 | 7.31 | 7.42 | 155 | 25 | 360 | 44 | 342 | 35 | NA | 500 | 0.3 | 23.4 | 1400000
2023-10-17 | 38310 | 38.31 | 7.28 | 7.38 | 145 | 24 | 348 | 42 | 326 | 34 | NA | 600 | 0.3 | 23.2 | 1700000
2023-10-18 | 37410 | 37.41 | 7.25 | 7.23 | 160 | 26 | 344 | 42 | 308 | 31 | NA | 400 | 0.2 | 24.4 | 1100000
2023-10-19 | 37390 | 37.39 | 7.06 | 7.35 | 155 | 20 | 368 | 36 | 362 | 30 | NA | 700 | 0.3 | 24.2 | 1300000
2023-10-20 | 38210 | 38.21 | 6.55 | 7.4 | 160 | 24 | 360 | 40 | 342 | 30 | NA | 500 | 0.3 | 24.1 | 1700000
2023-10-21 | 35460 | 35.46 | 6.53 | 7.34 | 155 | 23 | 368 | 36 | 357 | 32 | NA | 400 | 0.2 | 24.4 | 1400000
2023-10-22 | 38040 | 38.04 | 6.7 | 7.36 | 150 | 18 | 364 | 32 | 369 | 31 | NA | 600 | 0.3 | 23.3 | 1300000
2023-10-23 | 38450 | 38.45 | 6.68 | 7.39 | 155 | 22 | 368 | 40 | 346 | 30 | NA | 700 | 0.2 | 22.7 | 1100000
2023-10-24 | 39270 | 39.27 | 6.89 | 7.34 | 165 | 24 | 372 | 36 | 352 | 33 | NA | 500 | 0.3 | 23.4 | 1400000
2023-10-25 | 37500 | 37.5 | 7.32 | 7.36 | 155 | 21 | 360 | 36 | 340 | 29 | NA | 400 | 0.3 | 23.7 | 1100000
2023-10-26 | 37610 | 37.61 | 7.25 | 7.32 | 160 | 25 | 352 | 40 | 315 | 32 | NA | 700 | 0.3 | 24.1 | 1400000
2023-10-27 | 38820 | 38.82 | 7.3 | 7.35 | 165 | 23 | 364 | 36 | 336 | 34 | NA | 500 | 0.2 | 23.8 | 1300000
2023-10-28 | 38580 | 38.58 | 7.11 | 6.75 | 155 | 17 | 356 | 32 | 342 | 31 | NA | 600 | 0.3 | 23.5 | 1700000
2023-10-29 | 36100 | 36.1 | 7.2 | 7.24 | 160 | 19 | 360 | 40 | 332 | 35 | NA | 400 | 0.3 | 24.7 | 1400000
2023-10-30 | 33850 | 33.85 | 7.09 | 7.4 | 155 | 20 | 364 | 44 | 345 | 39 | NA | 700 | 0.2 | 24.2 | 1300000
2023-10-31 | 36820 | 36.82 | 7.27 | 7.44 | 160 | 19 | 368 | 40 | 358 | 36 | NA | 600 | 0.2 | 24.6 | 1100000
Average | 37723.871 | 37.7239 | 7.1342 | 7.3448 | 157.4194 | 22.7419 | 354.1935 | 39.3548 | 325.129 | 32.6129 | NA | 554.8387 | 0.26129 | 23.7032 | 1354838.7097
1169.44
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 32730 | 32.73 | 6.53 | 6.75 | 145 | 17 | 328 | 32 | 292 | 28 |  | 400 | 0.2 | 21.1 | 1100000
Max | 41410 | 41.41 | 7.33 | 7.5 | 165 | 27 | 372 | 44 | 369 | 39 |  | 700 | 0.3 | 24.9 | 1700000

## Kodra
kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-10-01 | 30500 | 30.5 | 7.26 | 7.38 | 130 | 12 | 280 | 36 | 276 | 25 | NA | 500 | 0.2 | 25.44 | 1300000
2023-10-02 | 31830 | 31.83 | 7.22 | 7.33 | 120 | 13 | 272 | 40 | 259 | 23 | NA | 600 | 0.3 | 24.7 | 1700000
2023-10-03 | 30310 | 30.31 | 7.24 | 7.38 | 125 | 12 | 308 | 36 | 304 | 24 | NA | 400 | 0.2 | 24.78 | 1400000
2023-10-04 | 30600 | 30.6 | 7.26 | 7.42 | 120 | 14 | 296 | 40 | 287 | 23 | NA | 600 | 0.3 | 23.87 | 1100000
2023-10-05 | 30410 | 30.41 | 7.15 | 7.39 | 130 | 13 | 292 | 36 | 282 | 26 | NA | 500 | 0.2 | 23.99 | 1200000
2023-10-06 | 30020 | 30.02 | 7.18 | 7.37 | 125 | 12 | 284 | 36 | 278 | 23 | NA | 700 | 0.2 | 24.07 | 1400000
2023-10-07 | 30050 | 30.05 | 7.21 | 7.38 | 130 | 13 | 288 | 40 | 272 | 22 | NA | 400 | 0.2 | 24.56 | 1100000
2023-10-08 | 30590 | 30.59 | 7.18 | 7.39 | 125 | 14 | 304 | 36 | 276 | 23 | NA | 600 | 0.3 | 23.49 | 1300000
2023-10-09 | 29940 | 29.94 | 7.21 | 7.42 | 120 | 11 | 308 | 32 | 282 | 24 | NA | 500 | 0.2 | 24.61 | 1700000
2023-10-10 | 29120 | 29.12 | 7.23 | 7.37 | 130 | 12 | 300 | 36 | 272 | 23 | NA | 600 | 0.2 | 24.9 | 1400000
2023-10-11 | 29780 | 29.78 | 7.2 | 7.34 | 120 | 11 | 304 | 32 | 262 | 22 | NA | 700 | 0.2 | 24.34 | 1300000
2023-10-12 | 28330 | 28.33 | 7.12 | 7.32 | 125 | 12 | 320 | 36 | 248 | 24 | NA | 500 | 0.2 | 23.65 | 1200000
2023-10-13 | 29780 | 29.78 | 7.1 | 7.37 | 130 | 11 | 304 | 36 | 256 | 23 | NA | 400 | 0.3 | 24.24 | 1100000
2023-10-14 | 29420 | 29.42 | 7.27 | 7.35 | 135 | 12 | 312 | 40 | 284 | 24 | NA | 600 | 0.2 | 23.56 | 1200000
2023-10-15 | 29190 | 29.19 | 7.29 | 7.38 | 120 | 11 | 328 | 32 | 314 | 22 | NA | 400 | 0.2 | 25.08 | 1300000
2023-10-16 | 28150 | 28.15 | 7.26 | 7.37 | 125 | 14 | 308 | 40 | 278 | 23 | NA | 500 | 0.3 | 24.4 | 1400000
2023-10-17 | 28410 | 28.41 | 7.22 | 7.35 | 130 | 12 | 296 | 36 | 262 | 21 | NA | 600 | 0.2 | 24.25 | 1700000
2023-10-18 | 29120 | 29.12 | 7.19 | 7.32 | 125 | 11 | 312 | 32 | 282 | 20 | NA | 500 | 0.2 | 23.85 | 1400000
2023-10-19 | 29270 | 29.27 | 7.16 | 7.34 | 120 | 12 | 284 | 36 | 273 | 22 | NA | 700 | 0.2 | 24.41 | 1300000
2023-10-20 | 28710 | 28.71 | 7.04 | 7.26 | 130 | 13 | 304 | 36 | 283 | 23 | NA | 600 | 0.2 | 24.46 | 1100000
2023-10-21 | 28970 | 28.97 | 7.1 | 7.28 | 125 | 12 | 292 | 40 | 267 | 22 | NA | 400 | 0.3 | 24.64 | 1400000
2023-10-22 | 29740 | 29.74 | 7.12 | 7.31 | 135 | 14 | 316 | 36 | 285 | 23 | NA | 500 | 0.3 | 24.43 | 1200000
2023-10-23 | 28620 | 28.62 | 7.16 | 7.28 | 120 | 11 | 308 | 32 | 277 | 24 | NA | 700 | 0.2 | 23.8 | 1100000
2023-10-24 | 30160 | 30.16 | 7.22 | 7.33 | 130 | 12 | 300 | 36 | 269 | 23 | NA | 600 | 0.2 | 24.24 | 1400000
2023-10-25 | 27250 | 27.25 | 7.1 | 7.29 | 125 | 11 | 316 | 32 | 284 | 24 | NA | 400 | 0.2 | 23.73 | 1300000
2023-10-26 | 27710 | 27.71 | 7.14 | 7.31 | 135 | 12 | 304 | 36 | 274 | 25 | NA | 700 | 0.2 | 24.93 | 1700000
2023-10-27 | 28680 | 28.68 | 7.25 | 7.36 | 130 | 13 | 300 | 40 | 263 | 27 | NA | 500 | 0.3 | 24.15 | 1400000
2023-10-28 | 28060 | 28.06 | 7.19 | 7.32 | 120 | 11 | 312 | 32 | 278 | 21 | NA | 400 | 0.2 | 23.56 | 1100000
2023-10-29 | 28900 | 28.9 | 7.21 | 7.28 | 125 | 12 | 324 | 36 | 298 | 22 | NA | 700 | 0.2 | 24.35 | 1400000
2023-10-30 | 29320 | 29.32 | 7.27 | 7.3 | 130 | 13 | 336 | 36 | 323 | 23 | NA | 600 | 0.2 | 23.4 | 1300000
2023-10-31 | 28690 | 28.69 | 7.19 | 7.36 | 135 | 14 | 304 | 40 | 282 | 22 | NA | 400 | 0.3 | 24.28 | 1200000
Average | 29342.9032 | 29.3429 | 7.1916 | 7.3435 | 126.6129 | 12.2581 | 303.7419 | 36.129 | 278.3871 | 23.0968 |  | 541.9355 | 0.22903 | 24.2632 | 1325806.4516
909.63
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 27250 | 27.25 | 7.04 | 7.26 | 120 | 11 | 272 | 32 | 248 | 20 |  | 400 | 0.2 | 23.4 | 1100000
Max | 31830 | 31.83 | 7.29 | 7.42 | 135 | 14 | 336 | 40 | 323 | 27 |  | 700 | 0.3 | 25.44 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-10-01 | 13200 | 13.2 | 7.25 | 7.69 | 125 | 15 | 280 | 32 | 220 | 24 | NA | 500 | 0.3 | 24.15 | 1300000
2023-10-02 | 12900 | 12.9 | 7.14 | 7.73 | 120 | 16 | 276 | 36 | 210 | 25 | NA | 600 | 0.2 | 23.95 | 1400000
2023-10-03 | 12300 | 12.3 | 7.34 | 7.76 | 130 | 15 | 270 | 32 | 198 | 24 | NA | 700 | 0.3 | 24.38 | 1500000
2023-10-04 | 12850 | 12.85 | 7.25 | 7.72 | 135 | 16 | 276 | 36 | 214 | 28 | NA | 400 | 0.3 | 24.27 | 1200000
2023-10-05 | 11400 | 11.4 | 7.19 | 7.78 | 120 | 15 | 292 | 32 | 286 | 26 | NA | 500 | 0.2 | 23.78 | 1400000
2023-10-06 | 13150 | 13.15 | 7.24 | 7.71 | 130 | 16 | 288 | 36 | 265 | 25 | NA | 600 | 0.3 | 23.9 | 1300000
2023-10-07 | 12720 | 12.72 | 7.16 | 7.68 | 125 | 15 | 272 | 32 | 220 | 28 | NA | 400 | 0.3 | 24.3 | 1200000
2023-10-08 | 13150 | 13.15 | 7.26 | 7.72 | 130 | 14 | 296 | 36 | 288 | 27 | NA | 500 | 0.2 | 24.09 | 1500000
2023-10-09 | 12720 | 12.72 | 7.22 | 7.73 | 120 | 16 | 284 | 32 | 250 | 28 | NA | 700 | 0.3 | 23.75 | 1700000
2023-10-10 | 11710 | 11.71 | 7.18 | 7.75 | 125 | 15 | 280 | 36 | 235 | 23 | NA | 600 | 0.2 | 24.46 | 1400000
2023-10-11 | 12100 | 12.1 | 7.23 | 7.69 | 120 | 14 | 276 | 32 | 240 | 22 | NA | 500 | 0.3 | 23.84 | 1200000
2023-10-12 | 13400 | 13.4 | 7.05 | 7.62 | 125 | 16 | 284 | 36 | 256 | 23 | NA | 700 | 0.2 | 24.38 | 1300000
2023-10-13 | 13130 | 13.13 | 7.26 | 7.58 | 120 | 17 | 272 | 40 | 228 | 24 | NA | 600 | 0.3 | 24.62 | 1400000
2023-10-14 | 12780 | 12.78 | 7.18 | 7.64 | 130 | 18 | 280 | 36 | 240 | 22 | NA | 400 | 0.2 | 24.16 | 1500000
2023-10-15 | 13350 | 13.35 | 7.27 | 7.55 | 125 | 19 | 284 | 44 | 260 | 21 | NA | 500 | 0.3 | 23.85 | 1200000
2023-10-16 | 12740 | 12.74 | 7.02 | 7.61 | 130 | 18 | 296 | 40 | 235 | 20 | NA | 700 | 0.2 | 24.44 | 1300000
2023-10-17 | 13150 | 13.15 | 7.08 | 7.64 | 125 | 17 | 288 | 44 | 228 | 22 | NA | 600 | 0.3 | 24.68 | 1400000
2023-10-18 | 13660 | 13.66 | 7.23 | 7.62 | 130 | 18 | 292 | 40 | 235 | 21 | NA | 400 | 0.3 | 23.78 | 1700000
2023-10-19 | 13930 | 13.93 | 7.3 | 7.71 | 125 | 15 | 296 | 32 | 225 | 20 | NA | 500 | 0.2 | 24.05 | 1500000
2023-10-20 | 12960 | 12.96 | 7.34 | 7.52 | 120 | 14 | 284 | 36 | 220 | 22 | NA | 400 | 0.3 | 23.95 | 1200000
2023-10-21 | 13400 | 13.4 | 7.26 | 7.64 | 130 | 16 | 282 | 32 | 210 | 24 | NA | 600 | 0.2 | 24.22 | 1300000
2023-10-22 | 13040 | 13.04 | 7.36 | 7.68 | 135 | 15 | 296 | 36 | 230 | 25 | NA | 500 | 0.3 | 23.9 | 1400000
2023-10-23 | 12730 | 12.73 | 7.3 | 7.62 | 130 | 18 | 304 | 40 | 245 | 28 | NA | 700 | 0.3 | 24.18 | 1500000
2023-10-24 | 12900 | 12.9 | 7.24 | 7.71 | 135 | 16 | 300 | 36 | 235 | 27 | NA | 400 | 0.2 | 23.6 | 1200000
2023-10-25 | 12970 | 12.97 | 7.32 | 7.64 | 125 | 15 | 296 | 32 | 210 | 26 | NA | 600 | 0.3 | 24.32 | 1400000
2023-10-26 | 12620 | 12.62 | 7.25 | 7.68 | 120 | 16 | 280 | 36 | 215 | 25 | NA | 500 | 0.3 | 24.1 | 1700000
2023-10-27 | 13520 | 13.52 | 7.3 | 7.72 | 130 | 15 | 284 | 32 | 220 | 24 | NA | 700 | 0.2 | 23.75 | 1500000
2023-10-28 | 12690 | 12.69 | 7.58 | 7.66 | 125 | 14 | 280 | 36 | 218 | 23 | NA | 400 | 0.3 | 24.28 | 1200000
2023-10-29 | 13550 | 13.55 | 7.6 | 7.65 | 130 | 16 | 292 | 32 | 225 | 25 | NA | 500 | 0.3 | 24.38 | 1300000
2023-10-30 | 13960 | 13.96 | 7.35 | 7.68 | 120 | 15 | 284 | 36 | 210 | 23 | NA | 700 | 0.2 | 23.82 | 1100000
2023-10-31 | 13630 | 13.63 | 7.25 | 7.62 | 125 | 17 | 288 | 40 | 225 | 27 | NA | 600 | 0.3 | 24.45 | 1700000
Average | 12977.7419 | 12.9777 | 7.2581 | 7.6694 | 126.2903 | 15.871 | 285.5484 | 35.7419 | 232.129 | 24.2581 |  | 548.3871 | 0.26129 | 24.1219 | 1383870.9677
402.31
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 11400 | 11.4 | 7.02 | 7.52 | 120 | 14 | 270 | 32 | 198 | 20 |  | 400 | 0.2 | 23.6 | 1100000
Max | 13960 | 13.96 | 7.6 | 7.78 | 135 | 19 | 304 | 44 | 288 | 28 |  | 700 | 0.3 | 24.68 | 1700000