## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-09-01 | 29280 | 29.28 | 7.34 | 7.63 | 130 | 16 | 292 | 36 | 266 | 25 | NA | 400 | 0.2 | 24.16 | 1200000 | 1. Raw sewage pumping from Ghagarnalla MPS is reduced since 18.08.2022 due to flood. 2. Sasur Kadheri SPS is not in operation since 16.08.2022 due to flood.
2022-09-02 | 25530 | 25.53 | 7.28 | 7.72 | 135 | 14 | 288 | 32 | 258 | 22 | NA | 600 | 0.3 | 22.76 | 1300000
2022-09-03 | 31600 | 31.6 | 7.24 | 7.68 | 130 | 15 | 308 | 36 | 264 | 22 | NA | 500 | 0.3 | 23.45 | 1700000
2022-09-04 | 45400 | 45.4 | 7.36 | 7.74 | 140 | 16 | 300 | 40 | 272 | 24 | NA | 900 | 0.2 | 24.54 | 1400000 | 1. Raw sewage pumping from Ghagarnalla MPS is opened 100% since 03:30 PM on 04.09.2022 due to flood. 2. Sasur Kadheri SPS is taken in operation since 03:30 PM on 04.09.2022 due to flood.
2022-09-05 | 61660 | 61.66 | 7.28 | 7.67 | 135 | 13 | 292 | 36 | 276 | 21 | NA | 700 | 0.3 | 22.49 | 1300000
2022-09-06 | 65940 | 65.94 | 7.33 | 7.72 | 140 | 15 | 288 | 32 | 254 | 23 | NA | 400 | 0.3 | 22.58 | 1200000
2022-09-07 | 65360 | 65.36 | 7.27 | 7.6 | 130 | 15 | 304 | 40 | 268 | 25 | NA | 600 | 0.2 | 24.31 | 1400000
2022-09-08 | 58900 | 58.9 | 7.23 | 7.68 | 125 | 12 | 312 | 36 | 272 | 24 | NA | 500 | 0.3 | 23.43 | 1200000
2022-09-09 | 59230 | 59.23 | 7.28 | 7.73 | 135 | 14 | 304 | 40 | 276 | 26 | NA | 600 | 0.2 | 24.34 | 1400000
2022-09-10 | 67840 | 67.84 | 7.34 | 7.76 | 130 | 12 | 296 | 32 | 268 | 23 | NA | 400 | 0.3 | 24.19 | 1300000
2022-09-11 | 62540 | 62.54 | 7.17 | 7.56 | 135 | 15 | 308 | 40 | 240 | 22 | NA | 700 | 0.3 | 23.8 | 1700000
2022-09-12 | 60480 | 60.48 | 7.22 | 7.72 | 125 | 13 | 312 | 36 | 258 | 24 | NA | 500 | 0.2 | 24.37 | 1400000
2022-09-13 | 61610 | 61.61 | 7.36 | 7.64 | 130 | 16 | 304 | 44 | 268 | 26 | NA | 600 | 0.3 | 23.51 | 1200000
2022-09-14 | 66570 | 66.57 | 7.34 | 7.6 | 125 | 14 | 276 | 36 | 247 | 22 | NA | 400 | 0.3 | 23.99 | 1700000
2022-09-15 | 68760 | 68.76 | 7.37 | 7.74 | 135 | 17 | 292 | 40 | 263 | 24 | NA | 700 | 0.2 | 22.85 | 1400000
2022-09-16 | 54620 | 54.62 | 7.28 | 7.67 | 130 | 15 | 304 | 36 | 274 | 26 | NA | 500 | 0.3 | 24.1 | 1300000 | Numayadahi STP is in shutdown from 7:00 PM on 16.09.2022 due to damage in rising main from Ghagharnalla MPS to Numayadahi STP. Subsequently, Sasur Khaderi SPS is also stopped.
2022-09-17 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | 23.5 | 1700000 | Maintenance work for rising main from Ghagharnalla MPS to Numayadahi STP is in progress.
2022-09-18 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | 21.99 | 1400000
2022-09-19 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-09-20 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-09-21 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-09-22 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-09-23 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-09-24 | 12400 | 12.4 | 7.14 | 7.18 | 130 | 14 | 304 | 40 | 268 | 25 | NA | 600 | 0.2 | 22.33 | 1200000 | Maintenance work in rising main from Ghagharnalla MPS to Numayadahi STP was completed on 24.09.2022 at 4 PM. Subsequently, Ghagharnalla MPS, Sasus Khaderi SPS and Numayadahi STP were taken into operation.
2022-09-25 | 53510 | 53.51 | 7.26 | 7.72 | 125 | 16 | 300 | 44 | 258 | 23 | NA | 400 | 0.3 | 24.47 | 1700000
2022-09-26 | 53190 | 53.19 | 7.32 | 7.69 | 130 | 15 | 292 | 36 | 264 | 24 | NA | 700 | 0.2 | 23.22 | 1400000
2022-09-27 | 55380 | 55.38 | 7.27 | 7.54 | 125 | 14 | 308 | 40 | 272 | 26 | NA | 500 | 0.3 | 22.41 | 1300000
2022-09-28 | 56350 | 56.35 | 7.19 | 7.66 | 145 | 17 | 312 | 36 | 292 | 23 | NA | 400 | 0.3 | 22.49 | 1200000
2022-09-29 | 55720 | 55.72 | 7.33 | 7.78 | 140 | 15 | 296 | 32 | 278 | 25 | NA | 600 | 0.2 | 24.47 | 1700000
2022-09-30 | 61970 | 61.97 | 7.28 | 7.67 | 130 | 14 | 304 | 36 | 247 | 22 | NA | 500 | 0.3 | 24.09 | 1400000
Average | 41128 | 41.128 | 7.2817 | 7.6565 | 131.9565 | 14.6522 | 299.8261 | 37.2174 | 265.3478 | 23.7826 | NA | 552.1739 | 0.26087 | 23.5136 | 1404000
1233.84
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.14 | 7.18 | 125 | 12 | 276 | 32 | 240 | 21 |  | 400 | 0.2 | 21.99 | 1200000
Max | 68760 | 68.76 | 7.37 | 7.78 | 145 | 17 | 312 | 44 | 292 | 26 |  | 900 | 0.3 | 24.54 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-09-01 | 12320 | 12.32 | 7.59 | 7.72 | 153 | 16 | 356 | 28 | 317 | 24 | NA | 600 | 0.2 | 24.6 | 1400000 | 1. Tapping point at Amitabh bachchan culvert is closed at 4:15 PM on 16.08.2022 due to increase in river level. 2. Inlet gate for raw sewage from Allahpur drain were closed at 10:15 AM on 16.08.2022 by flood department due to increase in river level. 3. Currently, raw sewage is being received from house connections only.
2022-09-02 | 10540 | 10.54 | 7.4 | 7.45 | 156 | 15 | 348 | 24 | 314 | 23 | NA | 500 | 0.3 | 25.4 | 1200000
2022-09-03 | 13020 | 13.02 | 7.52 | 7.64 | 153 | 17 | 356 | 28 | 309 | 24 | NA | 600 | 0.2 | 24.9 | 1300000
2022-09-04 | 20130 | 20.13 | 7.39 | 7.42 | 159 | 18 | 352 | 32 | 305 | 21 | NA | 400 | 0.3 | 24.6 | 1100000 | 1. Tapping point at Amitabh bachchan culvert is closed at 4:15 PM on 16.08.2022 due to increase in river level. 2. Inlet gate for raw sewage from Allahpur drain was opened at 6:30 PM on 04.09.2022 by flood department due to increase in river level. 3. Currently, raw sewage is being received from Allahapur drain & house connections only.
2022-09-05 | 22870 | 22.87 | 7.37 | 7.51 | 159 | 21 | 356 | 28 | 318 | 22 | NA | 500 | 0.2 | 25.4 | 1400000
2022-09-06 | 31630 | 31.63 | 7.41 | 7.6 | 156 | 22 | 352 | 32 | 325 | 26 | NA | 600 | 0.2 | 24.9 | 1200000 | 1. Tapping point at Amitabh bachchan culvert is opened at 6:30 PM on 06.09.2022 due to increase in river level. 2. Inlet gate for raw sewage from Allahpur drain was opened at 6:30 PM on 04.09.2022 by flood department due to increase in river level. 3. Currently, complete raw sewage is being received inside STP.
2022-09-07 | 33820 | 33.82 | 7.35 | 7.52 | 153 | 24 | 356 | 36 | 310 | 28 | NA | 400 | 0.3 | 25.2 | 1400000
2022-09-08 | 34580 | 34.58 | 7.37 | 7.57 | 156 | 22 | 352 | 40 | 329 | 30 | NA | 700 | 0.2 | 24.6 | 1200000
2022-09-09 | 36760 | 36.76 | 7.39 | 7.54 | 153 | 24 | 356 | 40 | 312 | 33 | NA | 600 | 0.3 | 24.9 | 1300000
2022-09-10 | 32290 | 32.29 | 7.35 | 7.55 | 156 | 21 | 352 | 36 | 325 | 35 | NA | 500 | 0.2 | 25.1 | 1100000
2022-09-11 | 33390 | 33.39 | 7.41 | 7.59 | 156 | 23 | 360 | 40 | 332 | 32 | NA | 400 | 0.2 | 24.7 | 1200000
2022-09-12 | 33830 | 33.83 | 7.39 | 7.48 | 153 | 22 | 356 | 44 | 309 | 35 | NA | 600 | 0.3 | 24.3 | 1400000
2022-09-13 | 34040 | 34.04 | 7.49 | 7.58 | 159 | 24 | 352 | 40 | 316 | 34 | NA | 700 | 0.3 | 25 | 1300000
2022-09-14 | 34620 | 34.62 | 7.35 | 7.47 | 156 | 25 | 356 | 44 | 308 | 36 | NA | 500 | 0.2 | 25.2 | 1200000
2022-09-15 | 34020 | 34.02 | 7.42 | 7.59 | 153 | 23 | 352 | 36 | 323 | 33 | NA | 400 | 0.2 | 24.6 | 1100000
2022-09-16 | 32500 | 32.5 | 7.29 | 7.47 | 156 | 27 | 356 | 40 | 302 | 31 | NA | 600 | 0.3 | 24.5 | 1300000
2022-09-17 | 34650 | 34.65 | 7.33 | 7.49 | 153 | 22 | 352 | 44 | 314 | 34 | NA | 500 | 0.2 | 25.1 | 1200000
2022-09-18 | 34680 | 34.68 | 7.35 | 7.48 | 156 | 21 | 360 | 40 | 310 | 36 | NA | 400 | 0.2 | 24.7 | 1400000
2022-09-19 | 32760 | 33.05 | 7.44 | 7.53 | 147 | 20 | 356 | 36 | 333 | 38 | NA | 600 | 0.3 | 24.2 | 1100000
2022-09-20 | 34630 | 35.16 | 7.22 | 7.35 | 153 | 23 | 352 | 40 | 317 | 34 | NA | 500 | 0.2 | 24.6 | 1300000
2022-09-21 | 32620 | 32.62 | 7.45 | 7.59 | 150 | 19 | 356 | 32 | 312 | 27 | NA | 800 | 0.3 | 25.2 | 1700000
2022-09-22 | 34120 | 34.12 | 7.29 | 7.36 | 156 | 20 | 356 | 36 | 310 | 31 | NA | 400 | 0.2 | 24 | 1400000
2022-09-23 | 33110 | 33.11 | 7.27 | 7.39 | 162 | 22 | 352 | 32 | 305 | 27 | NA | 500 | 0.3 | 24.2 | 1300000
2022-09-24 | 20130 | 20.13 | 7.39 | 7.48 | 159 | 20 | 348 | 36 | 293 | 25 | NA | 400 | 0.3 | 25.4 | 1100000 | 1. Tapping point at Amitabh bachchan culvert is closed at 3 Am on 24.09.2022 due to increase in river level. 2. Inlet gate for raw sewage from Allahpur drain were closed at 9 AM on 24.09.2022 by flood department due to increase in river level. 3. Currently, raw sewage is being received from house connections only.
2022-09-25 | 21170 | 21.17 | 7.41 | 7.53 | 156 | 21 | 356 | 28 | 295 | 23 | NA | 600 | 0.2 | 25.1 | 1400000 | 1. Tapping point at Amitabh bachchan culvert is opened at 10:00 PM on 25.09.2022 due to increase in river level. 2. Inlet gate for raw sewage from Allahpur drain was opened at 6:00 PM on 25.09.2022 by flood department due to increase in river level. 3. Currently, complete raw sewage is being received inside STP.
2022-09-26 | 31680 | 31.68 | 7.12 | 7.22 | 153 | 23 | 352 | 32 | 304 | 25 | NA | 700 | 0.3 | 24.2 | 1200000
2022-09-27 | 32570 | 32.57 | 7.31 | 7.39 | 159 | 22 | 360 | 28 | 300 | 27 | NA | 500 | 0.2 | 24 | 1300000
2022-09-28 | 33310 | 33.31 | 7.35 | 7.42 | 156 | 20 | 356 | 36 | 315 | 28 | NA | 800 | 0.3 | 24.5 | 1400000
2022-09-29 | 33480 | 33.48 | 6.8 | 7.12 | 162 | 23 | 364 | 36 | 312 | 26 | NA | 700 | 0.3 | 23.7 | 1700000
2022-09-30 | 32550 | 32.55 | 7.29 | 7.37 | 159 | 21 | 360 | 40 | 307 | 29 | NA | 400 | 0.2 | 24.3 | 1300000
Average | 29727.3333 | 29.7547 | 7.3503 | 7.4807 | 155.6 | 21.3667 | 354.9333 | 35.4667 | 312.7 | 29.2333 | NA | 546.6667 | 0.24667 | 24.7033 | 1296666.6667
892.64
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 10540 | 10.54 | 6.8 | 7.12 | 147 | 15 | 348 | 24 | 293 | 21 |  | 400 | 0.2 | 23.7 | 1100000
Max | 36760 | 36.76 | 7.59 | 7.72 | 162 | 27 | 364 | 44 | 333 | 38 |  | 800 | 0.3 | 25.4 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-09-01 | 26140 | 26.14 | 7.39 | 7.3 | 116 | 12 | 272 | 36 | 245 | 22 | NA | 500 | 0.3 | 24.14 | 1200000 | 1. Inlet gate at tapping point for nearby drain is closed at around 9:30 AM on 25.08.2022 due to rise in water level of Yamuna river due to flood. 2. Currently, raw sewage is being received from Vivekanand park SPS and Kalimandir SPS.
2022-09-02 | 25810 | 25.81 | 7.36 | 7.27 | 123 | 14 | 296 | 40 | 258 | 19 | NA | 700 | 0.2 | 23.67 | 1400000
2022-09-03 | 28530 | 28.53 | 7.58 | 7.48 | 130 | 15 | 288 | 36 | 265 | 20 | NA | 600 | 0.3 | 24.28 | 1700000 | 1. Inlet gate at tapping point for nearby drain is opened at around 9:36 AM on 03.09.2022 after water level has gobe down in Yamuna river due to flood. 2. Currently, complete raw sewage is coming inisde the STP. 3. Retaining wall for the nearby nalla at Kodra MPS is broken hence raw sewage is going directly into the river.
2022-09-04 | 25900 | 25.9 | 7.31 | 7.54 | 126 | 13 | 304 | 32 | 276 | 22 | NA | 500 | 0.3 | 23.43 | 1300000 | Retaining wall for the nearby nalla at Kodra MPS is constructed hence complete raw sewage is coming into the STP.
2022-09-05 | 25280 | 25.28 | 7.41 | 7.5 | 133 | 16 | 312 | 40 | 268 | 19 | NA | 700 | 0.2 | 23.84 | 1400000
2022-09-06 | 25780 | 25.78 | 7.27 | 7.43 | 130 | 14 | 300 | 32 | 282 | 21 | NA | 400 | 0.3 | 22.78 | 1200000
2022-09-07 | 26960 | 26.96 | 7.36 | 7.54 | 136 | 15 | 336 | 44 | 331 | 19 | NA | 600 | 0.3 | 24.12 | 1400000
2022-09-08 | 27070 | 27.07 | 7.18 | 7.37 | 133 | 13 | 328 | 40 | 310 | 22 | NA | 500 | 0.2 | 23.38 | 1300000
2022-09-09 | 27790 | 27.79 | 7.45 | 7.31 | 140 | 14 | 320 | 36 | 295 | 20 | NA | 700 | 0.3 | 23.89 | 1400000
2022-09-10 | 25600 | 25.6 | 7.28 | 7.39 | 133 | 12 | 324 | 40 | 286 | 21 | NA | 400 | 0.2 | 24.12 | 1700000
2022-09-11 | 28310 | 28.31 | 7.34 | 7.46 | 143 | 15 | 316 | 32 | 301 | 18 | NA | 600 | 0.3 | 22.86 | 1300000
2022-09-12 | 28530 | 28.53 | 7.24 | 7.36 | 136 | 13 | 328 | 40 | 289 | 22 | NA | 500 | 0.2 | 23.95 | 1200000
2022-09-13 | 22480 | 22.48 | 7.41 | 7.53 | 140 | 14 | 324 | 36 | 308 | 20 | NA | 700 | 0.3 | 24.23 | 1400000 | Retaining wall for the nearby nalla at Kodra MPS is broken hence raw sewage is going directly into the river.
2022-09-14 | 27800 | 27.8 | 7.34 | 7.47 | 133 | 12 | 312 | 40 | 278 | 21 | NA | 500 | 0.3 | 23.48 | 1700000
2022-09-15 | 19870 | 19.87 | 7.29 | 7.41 | 143 | 15 | 320 | 32 | 285 | 19 | NA | 600 | 0.2 | 22.67 | 1300000
2022-09-16 | 19820 | 19.82 | 7.39 | 7.58 | 136 | 13 | 328 | 40 | 292 | 22 | NA | 400 | 0.3 | 23.89 | 1200000
2022-09-17 | 18980 | 18.98 | 7.45 | 7.66 | 130 | 14 | 316 | 32 | 274 | 19 | NA | 700 | 0.2 | 22.94 | 1300000
2022-09-18 | 22760 | 22.76 | 7.21 | 7.54 | 140 | 13 | 304 | 36 | 280 | 21 | NA | 500 | 0.3 | 23.58 | 1700000
2022-09-19 | 28150 | 28.15 | 7.34 | 7.49 | 133 | 12 | 320 | 40 | 268 | 18 | NA | 600 | 0.2 | 23.91 | 1400000
2022-09-20 | 30060 | 30.06 | 7.41 | 7.58 | 136 | 14 | 316 | 44 | 288 | 20 | NA | 400 | 0.3 | 24.41 | 1200000
2022-09-21 | 23640 | 23.64 | 7.47 | 7.31 | 130 | 15 | 296 | 40 | 277 | 18 | NA | 500 | 0.3 | 22.86 | 1400000
2022-09-22 | 22390 | 22.39 | 7.36 | 7.48 | 133 | 13 | 288 | 36 | 259 | 21 | NA | 700 | 0.2 | 23.67 | 1300000
2022-09-23 | 27570 | 27.57 | 7.3 | 7.43 | 126 | 12 | 300 | 32 | 267 | 19 | NA | 600 | 0.3 | 24.08 | 1400000
2022-09-24 | 26230 | 26.23 | 7.42 | 7.59 | 130 | 14 | 292 | 36 | 255 | 20 | NA | 400 | 0.3 | 23.38 | 1700000
2022-09-25 | 27340 | 27.34 | 7.36 | 7.49 | 136 | 15 | 284 | 40 | 239 | 19 | NA | 500 | 0.2 | 23.87 | 1200000
2022-09-26 | 27460 | 27.46 | 7.29 | 7.49 | 140 | 12 | 296 | 36 | 259 | 21 | NA | 700 | 0.3 | 22.74 | 1300000
2022-09-27 | 27510 | 27.51 | 7.24 | 7.38 | 133 | 14 | 308 | 32 | 276 | 20 | NA | 600 | 0.2 | 22.18 | 1200000
2022-09-28 | 26900 | 26.9 | 7.42 | 7.03 | 143 | 16 | 320 | 36 | 268 | 18 | NA | 800 | 0.3 | 23.12 | 1400000
2022-09-29 | 26430 | 26.43 | 7.35 | 7.47 | 136 | 13 | 328 | 40 | 286 | 22 | NA | 500 | 0.2 | 23.41 | 1700000
2022-09-30 | 25670 | 25.67 | 7.28 | 7.54 | 140 | 15 | 316 | 32 | 279 | 19 | NA | 700 | 0.3 | 24.08 | 1400000
Average | 25758.6667 | 25.7587 | 7.35 | 7.4473 | 133.9 | 13.7333 | 309.7333 | 36.9333 | 278.1333 | 20.0667 | NA | 570 | 0.26 | 23.5653 | 1390000
772.76
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 18980 | 18.98 | 7.18 | 7.03 | 116 | 12 | 272 | 32 | 239 | 18 |  | 400 | 0.2 | 22.18 | 1200000
Max | 30060 | 30.06 | 7.58 | 7.66 | 143 | 16 | 336 | 44 | 331 | 22 |  | 800 | 0.3 | 24.41 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-09-01 | 12480 | 12.48 | 7.16 | 7.44 | 123 | 14 | 312 | 36 | 266 | 22 | NA | 400 | 0.3 | 22.13 | 1200000
2022-09-02 | 6510 | 6.51 | 7.12 | 7.36 | 130 | 16 | 300 | 40 | 251 | 24 | NA | 700 | 0.2 | 21.88 | 1400000 | Pipe joints in the incoming sewage line are damaged hence raw sewage is going directly to river. Therefore, raw sewage received at STP is less.
2022-09-03 | 5010 | 5.01 | 7.17 | 7.41 | 120 | 15 | 308 | 36 | 257 | 21 | NA | 600 | 0.2 | 22.44 | 1300000 | Pipe joints in the incoming sewage line are damaged hence raw sewage is going directly to river. Therefore, raw sewage received at STP is less. Arrangements for doing maintenance work are in progress.
2022-09-04 | 7600 | 7.6 | 7.24 | 7.47 | 126 | 13 | 316 | 40 | 271 | 23 | NA | 500 | 0.3 | 23.14 | 1700000
2022-09-05 | 8250 | 8.25 | 7.18 | 7.51 | 133 | 15 | 304 | 44 | 263 | 20 | NA | 600 | 0.2 | 22.38 | 1400000
2022-09-06 | 10330 | 10.33 | 7.37 | 7.58 | 139 | 16 | 312 | 40 | 284 | 22 | NA | 700 | 0.3 | 22.78 | 1300000
2022-09-07 | 11370 | 11.37 | 7.29 | 7.48 | 143 | 14 | 308 | 36 | 269 | 19 | NA | 400 | 0.2 | 23.21 | 1700000
2022-09-08 | 9830 | 9.83 | 7.21 | 7.39 | 136 | 15 | 316 | 44 | 276 | 23 | NA | 500 | 0.3 | 23.64 | 1200000
2022-09-09 | 8680 | 8.68 | 7.32 | 7.45 | 130 | 14 | 304 | 40 | 285 | 21 | NA | 700 | 0.3 | 22.67 | 1400000
2022-09-10 | 8930 | 8.93 | 7.27 | 7.52 | 140 | 16 | 312 | 36 | 273 | 22 | NA | 600 | 0.2 | 23.29 | 1300000
2022-09-11 | 13350 | 13.35 | 7.23 | 7.46 | 146 | 15 | 320 | 44 | 265 | 24 | NA | 500 | 0.3 | 21.77 | 1700000
2022-09-12 | 13130 | 13.13 | 7.15 | 7.36 | 139 | 14 | 308 | 40 | 271 | 21 | NA | 400 | 0.2 | 23.28 | 1400000
2022-09-13 | 7880 | 7.88 | 7.22 | 7.41 | 133 | 16 | 300 | 44 | 258 | 23 | NA | 700 | 0.2 | 22.31 | 1300000
2022-09-14 | 10800 | 10.8 | 7.26 | 7.51 | 140 | 13 | 316 | 36 | 269 | 20 | NA | 500 | 0.3 | 21.96 | 1200000
2022-09-15 | 10910 | 10.91 | 7.34 | 7.57 | 136 | 15 | 304 | 40 | 280 | 22 | NA | 600 | 0.3 | 22.67 | 1400000
2022-09-16 | 13520 | 13.52 | 7.28 | 7.61 | 139 | 14 | 312 | 36 | 276 | 24 | NA | 700 | 0.2 | 23.27 | 1300000
2022-09-17 | 11610 | 11.61 | 7.21 | 7.49 | 143 | 15 | 320 | 40 | 261 | 23 | NA | 400 | 0.3 | 22.47 | 1700000
2022-09-18 | 11700 | 11.7 | 7.3 | 7.58 | 133 | 16 | 308 | 44 | 272 | 21 | NA | 500 | 0.2 | 21.58 | 1400000
2022-09-19 | 9380 | 9.38 | 7.33 | 7.66 | 130 | 14 | 300 | 36 | 256 | 23 | NA | 600 | 0.3 | 22.71 | 1200000
2022-09-20 | 12510 | 12.51 | 7.22 | 7.51 | 136 | 15 | 316 | 40 | 264 | 22 | NA | 500 | 0.2 | 21.36 | 1300000
2022-09-21 | 13190 | 13.19 | 7.25 | 7.56 | 133 | 13 | 304 | 36 | 270 | 21 | NA | 700 | 0.2 | 22.53 | 1400000
2022-09-22 | 13000 | 13 | 7.19 | 7.48 | 139 | 15 | 320 | 40 | 260 | 20 | NA | 500 | 0.3 | 23.35 | 1700000
2022-09-23 | 12940 | 12.94 | 7.23 | 7.53 | 136 | 14 | 312 | 44 | 268 | 22 | NA | 600 | 0.3 | 22.44 | 1300000
2022-09-24 | 13300 | 13.3 | 7.27 | 7.42 | 130 | 13 | 308 | 36 | 273 | 24 | NA | 700 | 0.2 | 21.77 | 1200000
2022-09-25 | 13180 | 13.18 | 7.22 | 7.55 | 136 | 14 | 316 | 40 | 266 | 21 | NA | 400 | 0.3 | 23.14 | 1400000
2022-09-26 | 13290 | 13.29 | 7.16 | 7.39 | 133 | 15 | 304 | 44 | 276 | 23 | NA | 500 | 0.2 | 22.29 | 1300000
2022-09-27 | 16320 | 16.32 | 7.24 | 7.64 | 140 | 14 | 320 | 36 | 281 | 22 | NA | 600 | 0.3 | 21.86 | 1200000
2022-09-28 | 13480 | 13.48 | 7.31 | 7.54 | 136 | 16 | 312 | 40 | 292 | 21 | NA | 700 | 0.2 | 22.87 | 1700000
2022-09-29 | 12960 | 12.96 | 7.26 | 7.61 | 143 | 13 | 324 | 36 | 278 | 20 | NA | 500 | 0.2 | 21.56 | 1400000
2022-09-30 | 13660 | 13.66 | 7.18 | 7.59 | 139 | 15 | 316 | 40 | 265 | 22 | NA | 400 | 0.3 | 22.16 | 1200000
Average | 11303.3333 | 11.3033 | 7.2393 | 7.5027 | 135.3333 | 14.5667 | 311.0667 | 39.4667 | 269.8667 | 21.8667 | NA | 556.6667 | 0.25 | 22.497 | 1386666.6667
339.1
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 5010 | 5.01 | 7.12 | 7.36 | 120 | 13 | 300 | 36 | 251 | 19 |  | 400 | 0.2 | 21.36 | 1200000
Max | 16320 | 16.32 | 7.37 | 7.66 | 146 | 16 | 324 | 44 | 292 | 24 |  | 700 | 0.3 | 23.64 | 1700000