## Numayadahi
Numayadahi STP, 50 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-09-01 | 60850 | 60.85 | 7.32 | 7.74 | 130 | 15 | 284 | 40 | 248 | 25 | NA | 400 | 0.3 | 23.57 | 1300000
2023-09-02 | 60520 | 60.52 | 7.38 | 7.67 | 125 | 17 | 312 | 44 | 256 | 27 | NA | 600 | 0.2 | 24.22 | 1400000
2023-09-03 | 60950 | 60.95 | 7.28 | 7.76 | 130 | 16 | 288 | 40 | 248 | 24 | NA | 500 | 0.3 | 23.22 | 1100000
2023-09-04 | 62780 | 62.78 | 7.34 | 7.66 | 140 | 18 | 296 | 40 | 267 | 26 | NA | 700 | 0.3 | 23.54 | 1400000
2023-09-05 | 61300 | 61.3 | 7.33 | 7.78 | 135 | 16 | 308 | 44 | 254 | 24 | NA | 400 | 0.2 | 24.54 | 1400000
2023-09-06 | 56300 | 56.3 | 7.32 | 7.64 | 130 | 15 | 300 | 40 | 261 | 25 | NA | 600 | 0.3 | 22.85 | 1700000
2023-09-07 | 61580 | 61.58 | 7.28 | 7.67 | 135 | 17 | 308 | 44 | 278 | 28 | NA | 500 | 0.2 | 24.5 | 1100000
2023-09-08 | 64570 | 64.57 | 7.21 | 7.71 | 130 | 16 | 312 | 44 | 288 | 26 | NA | 600 | 0.2 | 24.01 | 1400000
2023-09-09 | 61980 | 61.98 | 7.34 | 7.77 | 125 | 14 | 304 | 36 | 283 | 24 | NA | 400 | 0.3 | 23.69 | 1300000
2023-09-10 | 60800 | 60.8 | 7.27 | 7.69 | 130 | 17 | 316 | 40 | 296 | 24 | NA | 600 | 0.3 | 22.99 | 1700000
2023-09-11 | 60960 | 60.96 | 7.31 | 7.73 | 140 | 15 | 296 | 40 | 281 | 25 | NA | 500 | 0.3 | 23.08 | 1400000
2023-09-12 | 64850 | 64.85 | 7.28 | 7.76 | 130 | 14 | 308 | 44 | 264 | 22 | NA | 700 | 0.2 | 24.04 | 1700000
2023-09-13 | 61780 | 61.78 | 7.36 | 7.64 | 145 | 16 | 300 | 40 | 248 | 23 | NA | 500 | 0.3 | 23.64 | 1100000
2023-09-14 | 63880 | 63.88 | 7.32 | 7.71 | 125 | 17 | 308 | 44 | 271 | 25 | NA | 600 | 0.3 | 23.78 | 1400000
2023-09-15 | 61260 | 61.26 | 7.24 | 7.68 | 130 | 16 | 320 | 40 | 280 | 22 | NA | 700 | 0.3 | 23.54 | 1700000
2023-09-16 | 63340 | 63.34 | 7.22 | 7.72 | 145 | 17 | 292 | 44 | 240 | 25 | NA | 500 | 0.3 | 22.46 | 1100000
2023-09-17 | 63050 | 63.05 | 7.32 | 7.83 | 125 | 15 | 324 | 40 | 256 | 24 | NA | 600 | 0.3 | 24.89 | 1700000
2023-09-18 | 65550 | 65.55 | 7.12 | 7.78 | 130 | 15 | 304 | 44 | 265 | 22 | NA | 700 | 0.3 | 24.4 | 1400000
2023-09-19 | 62050 | 62.05 | 7.16 | 7.76 | 130 | 16 | 328 | 40 | 252 | 24 | NA | 400 | 0.2 | 23.12 | 1300000
2023-09-20 | 62650 | 62.65 | 7.14 | 7.69 | 135 | 14 | 320 | 36 | 256 | 25 | NA | 600 | 0.3 | 23.58 | 1400000
2023-09-21 | 63180 | 63.18 | 7.21 | 7.72 | 140 | 16 | 312 | 44 | 268 | 26 | NA | 500 | 0.3 | 24.25 | 1700000
2023-09-22 | 63770 | 63.77 | 7.24 | 7.67 | 145 | 17 | 308 | 40 | 262 | 26 | NA | 700 | 0.2 | 23.54 | 1400000
2023-09-23 | 64180 | 64.18 | 7.18 | 7.7 | 140 | 17 | 300 | 40 | 258 | 27 | NA | 400 | 0.3 | 23.78 | 1100000
2023-09-24 | 64720 | 64.72 | 7.22 | 7.67 | 135 | 18 | 312 | 44 | 264 | 27 | NA | 700 | 0.3 | 24.68 | 1700000
2023-09-25 | 64120 | 64.12 | 7.18 | 7.74 | 130 | 17 | 308 | 44 | 256 | 26 | NA | 500 | 0.3 | 24.16 | 1300000
2023-09-26 | 63920 | 63.92 | 7.28 | 7.71 | 140 | 18 | 296 | 40 | 248 | 26 | NA | 400 | 0.2 | 22.77 | 1400000
2023-09-27 | 59750 | 59.75 | 7.24 | 7.66 | 135 | 17 | 304 | 44 | 256 | 28 | NA | 400 | 0.3 | 23.24 | 1300000
2023-09-28 | 65580 | 65.58 | 7.26 | 7.78 | 130 | 15 | 312 | 40 | 267 | 25 | NA | 600 | 0.3 | 24.42 | 1700000
2023-09-29 | 60480 | 60.48 | 7.23 | 7.64 | 125 | 14 | 300 | 36 | 244 | 24 | NA | 400 | 0.2 | 23.19 | 1100000
2023-09-30 | 62200 | 62.2 | 7.26 | 7.71 | 130 | 16 | 308 | 36 | 271 | 23 | NA | 500 | 0.3 | 24.32 | 1400000
Average | 62430 | 62.43 | 7.2613 | 7.713 | 133.1667 | 16.0333 | 306.2667 | 41.0667 | 262.8667 | 24.9333 | NA | 540 | 0.27 | 23.7337 | 1403333.3333
1872.9
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 56300 | 56.3 | 7.12 | 7.64 | 125 | 14 | 284 | 36 | 240 | 22 |  | 400 | 0.2 | 22.46 | 1100000
Max | 65580 | 65.58 | 7.38 | 7.83 | 145 | 18 | 328 | 44 | 296 | 28 |  | 700 | 0.3 | 24.89 | 1700000

## Salori
Salori STP, 29 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 29 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-09-01 | 39290 | 39.29 | 7.43 | 7.67 | 160 | 27 | 360 | 40 | 334 | 31 | NA | 600 | 0.2 | 23.8 | 1400000
2023-09-02 | 38040 | 38.04 | 7.52 | 7.69 | 155 | 25 | 364 | 44 | 340 | 33 | NA | 700 | 0.3 | 24.9 | 1300000
2023-09-03 | 38520 | 38.52 | 7.43 | 7.66 | 145 | 24 | 356 | 40 | 336 | 35 | NA | 500 | 0.2 | 24.6 | 1100000
2023-09-04 | 37950 | 37.95 | 7.28 | 7.56 | 135 | 23 | 348 | 32 | 340 | 28 | NA | 700 | 0.3 | 25.3 | 1400000
2023-09-05 | 40380 | 40.38 | 7.18 | 7.61 | 155 | 24 | 356 | 36 | 328 | 33 | NA | 600 | 0.2 | 23.8 | 1300000
2023-09-06 | 40370 | 40.37 | 7.24 | 7.59 | 155 | 20 | 352 | 32 | 308 | 30 | NA | 500 | 0.2 | 24.3 | 1700000
2023-09-07 | 42120 | 42.12 | 7.19 | 7.61 | 160 | 21 | 344 | 36 | 302 | 30 | NA | 700 | 0.3 | 24.5 | 1400000
2023-09-08 | 39340 | 39.34 | 7.22 | 7.55 | 135 | 22 | 336 | 34 | 355 | 28 | NA | 600 | 0.3 | 25.1 | 1300000
2023-09-09 | 37080 | 37.08 | 7.29 | 7.61 | 155 | 23 | 356 | 32 | 340 | 26 | NA | 500 | 0.2 | 24.7 | 1100000
2023-09-10 | 42830 | 42.83 | 7.18 | 7.66 | 160 | 24 | 364 | 36 | 329 | 25 | NA | 600 | 0.2 | 24.2 | 1400000
2023-09-11 | 38080 | 38.08 | 7.24 | 7.68 | 155 | 26 | 348 | 34 | 342 | 26 | NA | 400 | 0.3 | 23.4 | 1300000
2023-09-12 | 38880 | 38.88 | 7.15 | 7.59 | 160 | 23 | 328 | 32 | 304 | 28 | NA | 500 | 0.2 | 23.8 | 1100000
2023-09-13 | 37750 | 37.75 | 7.21 | 7.53 | 155 | 24 | 324 | 36 | 313 | 27 | NA | 600 | 0.3 | 24.6 | 1400000
2023-09-14 | 40190 | 40.19 | 7.17 | 7.58 | 160 | 23 | 332 | 40 | 318 | 28 | NA | 700 | 0.2 | 23.7 | 1700000
2023-09-15 | 38820 | 38.82 | 7.23 | 7.64 | 165 | 22 | 340 | 36 | 326 | 27 | NA | 500 | 0.2 | 24.3 | 1300000
2023-09-16 | 40030 | 40.03 | 7.18 | 7.6 | 155 | 24 | 328 | 32 | 312 | 26 | NA | 600 | 0.3 | 24.5 | 1400000
2023-09-17 | 40060 | 40.06 | 7.25 | 7.55 | 160 | 26 | 344 | 36 | 345 | 27 | NA | 400 | 0.2 | 23.8 | 1100000
2023-09-18 | 38610 | 38.61 | 7.2 | 7.57 | 165 | 22 | 352 | 32 | 328 | 28 | NA | 500 | 0.2 | 23.4 | 1300000
2023-09-19 | 38760 | 38.76 | 7.24 | 7.53 | 160 | 25 | 372 | 36 | 342 | 31 | NA | 600 | 0.3 | 24.1 | 1700000
2023-09-20 | 40050 | 40.05 | 7.28 | 7.56 | 165 | 27 | 348 | 40 | 335 | 32 | NA | 700 | 0.2 | 23.5 | 1400000
2023-09-21 | 42580 | 42.58 | 7.3 | 7.59 | 170 | 23 | 336 | 36 | 315 | 30 | NA | 500 | 0.3 | 23.3 | 1100000
2023-09-22 | 40100 | 40.1 | 7.33 | 7.61 | 160 | 21 | 324 | 40 | 318 | 32 | NA | 600 | 0.2 | 24.2 | 1300000
2023-09-23 | 39160 | 39.16 | 7.4 | 7.58 | 155 | 22 | 340 | 44 | 307 | 35 | NA | 400 | 0.3 | 24.8 | 1400000
2023-09-24 | 39070 | 39.07 | 7.35 | 7.53 | 160 | 24 | 348 | 40 | 311 | 33 | NA | 500 | 0.3 | 23.6 | 1700000
2023-09-25 | 38690 | 38.69 | 7.31 | 7.44 | 165 | 26 | 332 | 44 | 306 | 31 | NA | 600 | 0.2 | 23.9 | 1100000
2023-09-26 | 38300 | 38.3 | 7.28 | 7.4 | 155 | 27 | 344 | 40 | 316 | 34 | NA | 500 | 0.3 | 24.1 | 1300000
2023-09-27 | 39630 | 39.63 | 7.32 | 7.46 | 165 | 25 | 328 | 36 | 305 | 32 | NA | 400 | 0.3 | 24.5 | 1400000
2023-09-28 | 37470 | 37.47 | 7.36 | 7.52 | 160 | 22 | 352 | 32 | 322 | 30 | NA | 600 | 0.2 | 23.8 | 1100000
2023-09-29 | 38980 | 38.98 | 7.26 | 7.55 | 155 | 24 | 336 | 40 | 314 | 32 | NA | 500 | 0.3 | 24.7 | 1300000
2023-09-30 | 31750 | 31.75 | 7.23 | 7.53 | 150 | 21 | 324 | 36 | 309 | 33 | NA | 400 | 0.3 | 24.3 | 1700000
Average | 39096 | 39.096 | 7.275 | 7.575 | 157 | 23.6667 | 343.8667 | 36.8 | 323.3333 | 30.0333 | NA | 550 | 0.25 | 24.1833 | 1350000
1172.88
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 31750 | 31.75 | 7.15 | 7.4 | 135 | 20 | 324 | 32 | 302 | 25 |  | 400 | 0.2 | 23.3 | 1100000
Max | 42830 | 42.83 | 7.52 | 7.69 | 170 | 27 | 372 | 44 | 355 | 35 |  | 700 | 0.3 | 25.3 | 1700000

## Kodra
Kodra STP, 25 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-09-01 | 29500 | 29.5 | 7.19 | 7.48 | 105 | 11 | 276 | 32 | 247 | 22 | NA | 600 | 0.3 | 23.26 | 1200000
2023-09-02 | 28530 | 28.53 | 7.22 | 7.45 | 110 | 12 | 260 | 36 | 242 | 21 | NA | 400 | 0.3 | 23.79 | 1300000
2023-09-03 | 28080 | 28.08 | 7.14 | 7.46 | 115 | 14 | 276 | 40 | 258 | 23 | NA | 500 | 0.2 | 23.96 | 1400000
2023-09-04 | 25290 | 25.29 | 7.18 | 7.42 | 110 | 13 | 284 | 36 | 274 | 22 | NA | 600 | 0.3 | 23.68 | 1300000
2023-09-05 | 26710 | 26.71 | 7.16 | 7.47 | 120 | 12 | 288 | 40 | 280 | 23 | NA | 500 | 0.2 | 23.27 | 1700000
2023-09-06 | 29190 | 29.19 | 7.19 | 7.39 | 130 | 11 | 292 | 32 | 268 | 22 | NA | 700 | 0.2 | 23.47 | 1400000
2023-09-07 | 31710 | 31.71 | 7.23 | 7.37 | 125 | 13 | 276 | 36 | 248 | 21 | NA | 500 | 0.3 | 24.5 | 1200000
2023-09-08 | 27390 | 27.39 | 7.21 | 7.37 | 130 | 11 | 260 | 32 | 242 | 22 | NA | 400 | 0.3 | 23.45 | 1400000
2023-09-09 | 32510 | 32.51 | 7.18 | 7.32 | 125 | 10 | 272 | 36 | 239 | 23 | NA | 600 | 0.2 | 24.15 | 1700000
2023-09-10 | 30220 | 30.22 | 7.2 | 7.36 | 120 | 11 | 284 | 32 | 251 | 21 | NA | 400 | 0.2 | 24.35 | 1300000
2023-09-11 | 28770 | 28.77 | 7.16 | 7.32 | 130 | 12 | 296 | 36 | 272 | 22 | NA | 700 | 0.3 | 24.01 | 1200000
2023-09-12 | 32390 | 32.39 | 7.12 | 7.34 | 125 | 13 | 292 | 36 | 278 | 21 | NA | 500 | 0.2 | 24.25 | 1700000
2023-09-13 | 29030 | 29.03 | 7.19 | 7.36 | 135 | 12 | 304 | 40 | 286 | 23 | NA | 600 | 0.2 | 25.02 | 1400000
2023-09-14 | 27390 | 27.39 | 7.17 | 7.42 | 130 | 13 | 312 | 36 | 297 | 22 | NA | 500 | 0.3 | 24.39 | 1300000
2023-09-15 | 29030 | 29.03 | 7.22 | 7.38 | 125 | 15 | 324 | 44 | 309 | 24 | NA | 400 | 0.3 | 23.57 | 1700000
2023-09-16 | 27690 | 27.69 | 7.1 | 7.44 | 130 | 14 | 308 | 40 | 287 | 23 | NA | 600 | 0.3 | 24.11 | 1300000
2023-09-17 | 31800 | 31.8 | 7.16 | 7.47 | 135 | 13 | 284 | 40 | 265 | 22 | NA | 400 | 0.2 | 23.28 | 1400000
2023-09-18 | 28250 | 28.25 | 7.21 | 7.43 | 120 | 14 | 280 | 36 | 246 | 23 | NA | 700 | 0.3 | 23.72 | 1100000
2023-09-19 | 28640 | 28.64 | 7.22 | 7.37 | 125 | 11 | 284 | 32 | 276 | 22 | NA | 500 | 0.3 | 24.31 | 1200000
2023-09-20 | 29440 | 29.44 | 7.2 | 7.43 | 120 | 13 | 272 | 36 | 263 | 23 | NA | 600 | 0.2 | 23.38 | 1300000
2023-09-21 | 28320 | 28.32 | 7.16 | 7.38 | 130 | 12 | 304 | 40 | 298 | 24 | NA | 400 | 0.2 | 24.63 | 1400000
2023-09-22 | 28240 | 28.24 | 7.19 | 7.46 | 125 | 14 | 276 | 40 | 261 | 26 | NA | 700 | 0.2 | 23.96 | 1100000
2023-09-23 | 28360 | 28.36 | 7.13 | 7.42 | 130 | 12 | 268 | 36 | 257 | 22 | NA | 500 | 0.2 | 23.86 | 1300000
2023-09-24 | 30310 | 30.31 | 7.15 | 7.41 | 125 | 15 | 284 | 40 | 282 | 26 | NA | 400 | 0.3 | 24.41 | 1200000
2023-09-25 | 28670 | 28.67 | 7.19 | 7.46 | 135 | 13 | 272 | 36 | 267 | 27 | NA | 600 | 0.2 | 23.7 | 1400000
2023-09-26 | 27410 | 27.41 | 7.17 | 7.39 | 130 | 14 | 288 | 40 | 275 | 24 | NA | 500 | 0.3 | 23.19 | 1200000
2023-09-27 | 27730 | 27.73 | 7.21 | 7.46 | 125 | 12 | 272 | 36 | 268 | 26 | NA | 700 | 0.2 | 23.48 | 1300000
2023-09-28 | 28160 | 28.16 | 7.13 | 7.44 | 120 | 15 | 280 | 40 | 271 | 25 | NA | 600 | 0.3 | 24.5 | 1100000
2023-09-29 | 28320 | 28.32 | 7.16 | 7.37 | 135 | 11 | 268 | 36 | 253 | 22 | NA | 400 | 0.2 | 24.41 | 1400000
2023-09-30 | 29380 | 29.38 | 7.22 | 7.43 | 125 | 13 | 276 | 40 | 269 | 24 | NA | 700 | 0.3 | 24.98 | 1700000
Average | 28882 | 28.882 | 7.1787 | 7.409 | 124.8333 | 12.6333 | 283.7333 | 37.0667 | 267.6333 | 23.0333 | NA | 540 | 0.25 | 23.968 | 1353333.3333
866.46
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 25290 | 25.29 | 7.1 | 7.32 | 105 | 10 | 260 | 32 | 239 | 21 |  | 400 | 0.2 | 23.19 | 1100000
Max | 32510 | 32.51 | 7.23 | 7.48 | 135 | 15 | 324 | 44 | 309 | 27 |  | 700 | 0.3 | 25.02 | 1700000

## Ponghat
Ponghat STP, 10 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-09-01 | 13060 | 13.06 | 7.1 | 7.7 | 120 | 17 | 284 | 48 | 254 | 25 | NA | 600 | 0.3 | 23.85 | 1500000
2023-09-02 | 12790 | 12.79 | 7.24 | 7.62 | 125 | 18 | 290 | 44 | 264 | 23 | NA | 700 | 0.2 | 23.6 | 1400000
2023-09-03 | 12510 | 12.51 | 7.18 | 7.58 | 120 | 17 | 294 | 48 | 256 | 24 | NA | 500 | 0.3 | 24.2 | 1200000
2023-09-04 | 10650 | 10.65 | 7.08 | 7.66 | 125 | 18 | 286 | 44 | 262 | 22 | NA | 400 | 0.2 | 24.48 | 1300000
2023-09-05 | 11710 | 11.71 | 7.02 | 7.68 | 130 | 16 | 270 | 40 | 230 | 26 | NA | 600 | 0.3 | 24.86 | 1500000
2023-09-06 | 11150 | 11.15 | 7.04 | 7.72 | 135 | 17 | 308 | 36 | 270 | 28 | NA | 500 | 0.2 | 24.28 | 1400000
2023-09-07 | 11480 | 11.48 | 6.98 | 7.6 | 125 | 16 | 300 | 32 | 274 | 26 | NA | 400 | 0.3 | 23.88 | 1200000
2023-09-08 | 12300 | 12.3 | 7.01 | 7.59 | 130 | 19 | 288 | 44 | 256 | 29 | NA | 600 | 0.2 | 23.64 | 1300000
2023-09-09 | 12270 | 12.27 | 6.96 | 7.56 | 125 | 18 | 292 | 48 | 262 | 29 | NA | 500 | 0.3 | 23.25 | 1400000
2023-09-10 | 12060 | 12.06 | 6.92 | 7.66 | 130 | 16 | 284 | 36 | 252 | 25 | NA | 400 | 0.3 | 23.76 | 1500000
2023-09-11 | 12560 | 12.56 | 7.04 | 7.75 | 120 | 17 | 308 | 40 | 248 | 24 | NA | 600 | 0.2 | 23.48 | 1300000
2023-09-12 | 13320 | 13.32 | 6.85 | 7.72 | 125 | 16 | 288 | 36 | 255 | 26 | NA | 500 | 0.3 | 23.92 | 1200000
2023-09-13 | 12730 | 12.73 | 6.95 | 7.65 | 130 | 17 | 312 | 40 | 268 | 28 | NA | 400 | 0.2 | 24.25 | 1400000
2023-09-14 | 12760 | 12.76 | 6.9 | 7.78 | 135 | 16 | 296 | 36 | 256 | 27 | NA | 700 | 0.3 | 23.78 | 1500000
2023-09-15 | 13090 | 13.09 | 6.89 | 7.67 | 130 | 17 | 292 | 36 | 265 | 28 | NA | 600 | 0.2 | 23.35 | 1400000
2023-09-16 | 11800 | 11.8 | 6.78 | 7.58 | 135 | 15 | 300 | 40 | 275 | 26 | NA | 500 | 0.3 | 22.96 | 1300000
2023-09-17 | 13760 | 13.76 | 6.77 | 7.69 | 130 | 18 | 288 | 36 | 264 | 29 | NA | 400 | 0.3 | 23.4 | 1200000
2023-09-18 | 14260 | 14.26 | 7.04 | 7.61 | 125 | 15 | 272 | 40 | 220 | 28 | NA | 600 | 0.2 | 24.15 | 1400000
2023-09-19 | 13830 | 13.83 | 7.36 | 7.66 | 130 | 16 | 268 | 36 | 202 | 27 | NA | 700 | 0.3 | 23.78 | 1300000
2023-09-20 | 13310 | 13.31 | 7.21 | 7.53 | 125 | 15 | 276 | 36 | 250 | 28 | NA | 600 | 0.2 | 23.64 | 1400000
2023-09-21 | 12590 | 12.59 | 7.18 | 7.63 | 135 | 16 | 280 | 32 | 262 | 25 | NA | 500 | 0.3 | 24.25 | 1500000
2023-09-22 | 14200 | 14.2 | 7.3 | 7.72 | 125 | 17 | 244 | 40 | 159 | 29 | NA | 400 | 0.3 | 24.05 | 1200000
2023-09-23 | 12560 | 12.56 | 7.12 | 7.58 | 130 | 16 | 268 | 36 | 170 | 24 | NA | 700 | 0.2 | 23.78 | 1300000
2023-09-24 | 12450 | 12.45 | 7.21 | 7.69 | 125 | 17 | 280 | 36 | 200 | 27 | NA | 600 | 0.3 | 24.46 | 1400000
2023-09-25 | 12050 | 12.05 | 7.22 | 7.62 | 135 | 16 | 288 | 40 | 240 | 26 | NA | 500 | 0.3 | 23.75 | 1200000
2023-09-26 | 11430 | 11.43 | 7.15 | 7.65 | 130 | 15 | 292 | 36 | 230 | 24 | NA | 400 | 0.2 | 24.27 | 1500000
2023-09-27 | 11210 | 11.21 | 7.1 | 7.79 | 135 | 16 | 296 | 32 | 265 | 27 | NA | 600 | 0.3 | 24.6 | 1400000
2023-09-28 | 12240 | 12.24 | 7.12 | 7.74 | 130 | 15 | 288 | 36 | 270 | 25 | NA | 700 | 0.2 | 24.18 | 1300000
2023-09-29 | 12470 | 12.47 | 7.15 | 7.69 | 125 | 14 | 292 | 32 | 260 | 23 | NA | 500 | 0.3 | 23.78 | 1200000
2023-09-30 | 12880 | 12.88 | 7.19 | 7.75 | 130 | 15 | 284 | 36 | 264 | 25 | NA | 400 | 0.2 | 23.46 | 1400000
Average | 12516 | 12.516 | 7.0687 | 7.6623 | 128.3333 | 16.3667 | 286.9333 | 38.4 | 246.7667 | 26.1 | NA | 536.6667 | 0.25667 | 23.903 | 1350000
375.48
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 10650 | 10.65 | 6.77 | 7.53 | 120 | 14 | 244 | 32 | 159 | 22 |  | 400 | 0.2 | 22.96 | 1200000
Max | 14260 | 14.26 | 7.36 | 7.79 | 135 | 19 | 312 | 48 | 275 | 29 |  | 700 | 0.3 | 24.86 | 1500000