## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-04-01 | 114090 | 114.09 | 7.31 | 7.53 | 140 | 29 | 346 | 44 | 300 | 37 | NA | 700 | 0.3 | 24.35 | 1300000
2023-04-02 | 121040 | 121.04 | 7.39 | 7.51 | 120 | 30 | 338 | 42 | 298 | 38 | NA | 500 | 0.2 | 25.11 | 1400000
2023-04-03 | 114420 | 114.42 | 7.45 | 7.6 | 130 | 27 | 356 | 44 | 295 | 40 | NA | 700 | 0.2 | 24.4 | 1200000
2023-04-04 | 118180 | 118.18 | 7.53 | 7.62 | 145 | 28 | 352 | 43 | 287 | 36 | NA | 400 | 0.3 | 24.18 | 1700000
2023-04-05 | 116890 | 116.89 | 7.57 | 7.61 | 135 | 27 | 336 | 42 | 301 | 37 | NA | 800 | 0.3 | 25.07 | 1400000
2023-04-06 | 120590 | 120.59 | 7.43 | 7.57 | 145 | 28 | 354 | 44 | 305 | 38 | NA | 600 | 0.2 | 24.51 | 1300000
2023-04-07 | 121560 | 121.56 | 7.52 | 7.6 | 140 | 27 | 338 | 42 | 308 | 36 | NA | 500 | 0.2 | 23.98 | 1200000
2023-04-08 | 123900 | 123.9 | 7.47 | 7.62 | 120 | 26 | 342 | 41 | 300 | 37 | NA | 700 | 0.3 | 25.18 | 1400000
2023-04-09 | 121420 | 121.42 | 7.58 | 7.65 | 145 | 28 | 350 | 40 | 304 | 35 | NA | 400 | 0.3 | 24.45 | 1700000
2023-04-10 | 118180 | 118.18 | 7.6 | 7.63 | 135 | 29 | 340 | 42 | 307 | 38 | NA | 600 | 0.2 | 24.17 | 1300000
2023-04-11 | 115280 | 115.28 | 7.54 | 7.61 | 140 | 27 | 338 | 44 | 302 | 39 | NA | 800 | 0.2 | 25.2 | 1200000
2023-04-12 | 123040 | 123.04 | 7.18 | 7.58 | 130 | 29 | 354 | 48 | 314 | 43 | NA | 700 | 0.3 | 24.76 | 1400000
2023-04-13 | 117570 | 117.57 | 7.41 | 7.56 | 125 | 30 | 322 | 46 | 298 | 41 | NA | 400 | 0.3 | 25.07 | 1700000
2023-04-14 | 122590 | 122.59 | 7.46 | 7.64 | 145 | 27 | 344 | 41 | 314 | 36 | NA | 500 | 0.2 | 25.4 | 1200000
2023-04-15 | 118880 | 118.88 | 7.42 | 7.68 | 125 | 29 | 332 | 43 | 308 | 36 | NA | 600 | 0.2 | 25.1 | 1300000
2023-04-16 | 118480 | 118.48 | 7.48 | 7.62 | 130 | 30 | 336 | 46 | 292 | 47 | NA | 400 | 0.3 | 24.7 | 1400000
2023-04-17 | 115420 | 115.42 | 7.49 | 7.63 | 140 | 29 | 344 | 43 | 301 | 37 | NA | 600 | 0.2 | 25.3 | 1100000
2023-04-18 | 112100 | 112.1 | 7.47 | 7.69 | 145 | 28 | 336 | 45 | 305 | 40 | NA | 800 | 0.3 | 25.2 | 1700000
2023-04-19 | 113880 | 113.88 | 7.25 | 7.75 | 135 | 29 | 328 | 42 | 298 | 36 | NA | 500 | 0.2 | 24.9 | 1200000
2023-04-20 | 118620 | 118.62 | 7.41 | 7.72 | 140 | 30 | 330 | 48 | 294 | 52 | NA | 400 | 0.2 | 24.73 | 1300000
2023-04-21 | 116020 | 116.02 | 7.07 | 6.91 | 145 | 25 | 318 | 38 | 291 | 34 | NA | 600 | 0.3 | 25.11 | 1700000
2023-04-22 | 119980 | 119.98 | 7.48 | 7.67 | 140 | 27 | 340 | 42 | 307 | 38 | NA | 700 | 0.3 | 25.04 | 1300000
2023-04-23 | 115210 | 115.21 | 7.5 | 7.65 | 130 | 28 | 324 | 43 | 305 | 39 | NA | 800 | 0.2 | 24.41 | 1400000
2023-04-24 | 118220 | 118.22 | 7.48 | 7.76 | 135 | 27 | 332 | 42 | 299 | 39 | NA | 700 | 0.3 | 24.8 | 1200000
2023-04-25 | 117480 | 117.48 | 7.46 | 7.79 | 125 | 29 | 328 | 44 | 304 | 40 | NA | 600 | 0.2 | 25.1 | 1700000
2023-04-26 | 116410 | 116.41 | 7.45 | 7.72 | 130 | 28 | 326 | 41 | 307 | 38 | NA | 500 | 0.3 | 24.3 | 1300000
2023-04-27 | 113780 | 113.78 | 7.44 | 7.77 | 125 | 27 | 319 | 43 | 290 | 39 | NA | 700 | 0.2 | 25.4 | 1400000
2023-04-28 | 109360 | 109.36 | 7.43 | 7.69 | 150 | 29 | 336 | 40 | 294 | 37 | NA | 500 | 0.3 | 25.2 | 1200000
2023-04-29 | 108650 | 108.65 | 7.45 | 7.76 | 145 | 25 | 340 | 42 | 307 | 36 | NA | 800 | 0.2 | 24.9 | 1400000
2023-04-30 | 108340 | 108.34 | 7.45 | 7.72 | 130 | 28 | 330 | 44 | 312 | 40 | NA | 700 | 0.2 | 25 | 1300000
Average | 116986 | 116.986 | 7.439 | 7.6287 | 135.5 | 28 | 336.9667 | 42.9667 | 301.5667 | 38.6333 | NA | 606.6667 | 0.24667 | 24.834 | 1376666.6667
3509.58
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 108340 | 108.34 | 7.07 | 6.91 | 120 | 25 | 318 | 38 | 287 | 34 |  | 400 | 0.2 | 23.98 | 1100000
Max | 123900 | 123.9 | 7.6 | 7.79 | 150 | 30 | 356 | 48 | 314 | 52 |  | 800 | 0.3 | 25.4 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-04-01 | 81420 | 81.42 | 7.33 | 7.67 | 125 | 16 | 332 | 44 | 307 | 26 | NA | 600 | 0.3 | 23.65 | 1700000
2023-04-02 | 70590 | 70.59 | 7.31 | 7.62 | 135 | 18 | 324 | 48 | 298 | 25 | NA | 700 | 0.2 | 23.89 | 1400000
2023-04-03 | 70760 | 70.76 | 7.28 | 7.61 | 130 | 16 | 336 | 44 | 291 | 26 | NA | 500 | 0.3 | 23.93 | 1700000
2023-04-04 | 68850 | 68.85 | 7.35 | 7.6 | 135 | 17 | 316 | 40 | 287 | 27 | NA | 600 | 0.2 | 23.22 | 1400000
2023-04-05 | 72030 | 72.03 | 7.29 | 7.62 | 140 | 18 | 324 | 44 | 297 | 26 | NA | 400 | 0.3 | 24.47 | 1300000
2023-04-06 | 69030 | 69.03 | 7.27 | 7.65 | 145 | 19 | 328 | 48 | 283 | 25 | NA | 700 | 0.2 | 23.76 | 1700000
2023-04-07 | 70300 | 70.3 | 7.29 | 7.64 | 130 | 17 | 332 | 40 | 289 | 26 | NA | 500 | 0.3 | 23.22 | 1400000
2023-04-08 | 71400 | 71.4 | 7.38 | 7.63 | 135 | 18 | 336 | 40 | 290 | 26 | NA | 600 | 0.2 | 24.64 | 1700000
2023-04-09 | 74500 | 74.5 | 7.32 | 7.65 | 125 | 16 | 324 | 44 | 287 | 27 | NA | 700 | 0.3 | 24.88 | 1400000
2023-04-10 | 74300 | 74.3 | 7.27 | 7.64 | 130 | 17 | 332 | 48 | 307 | 26 | NA | 400 | 0.2 | 23.77 | 1700000
2023-04-11 | 70030 | 70.03 | 7.28 | 7.62 | 140 | 18 | 328 | 44 | 292 | 27 | NA | 500 | 0.3 | 23.9 | 1300000
2023-04-12 | 71200 | 71.2 | 7.31 | 7.61 | 130 | 17 | 336 | 40 | 298 | 26 | NA | 600 | 0.2 | 23.35 | 1400000
2023-04-13 | 73100 | 73.1 | 7.28 | 7.65 | 125 | 16 | 328 | 44 | 285 | 27 | NA | 700 | 0.3 | 23.29 | 1700000
2023-04-14 | 74090 | 74.09 | 7.26 | 7.6 | 135 | 18 | 316 | 40 | 282 | 26 | NA | 500 | 0.2 | 23.16 | 1400000
2023-04-15 | 74890 | 74.89 | 7.28 | 7.58 | 140 | 16 | 324 | 44 | 276 | 27 | NA | 600 | 0.3 | 24.03 | 1700000
2023-04-16 | 74350 | 74.35 | 7.31 | 7.62 | 130 | 17 | 320 | 40 | 295 | 26 | NA | 700 | 0.3 | 23.76 | 1300000
2023-04-17 | 72650 | 72.65 | 7.23 | 7.56 | 125 | 16 | 312 | 44 | 278 | 25 | NA | 500 | 0.2 | 23.98 | 1400000
2023-04-18 | 73880 | 73.88 | 7.26 | 7.63 | 135 | 17 | 316 | 40 | 286 | 27 | NA | 600 | 0.2 | 23.63 | 1300000
2023-04-19 | 78160 | 78.16 | 7.28 | 7.65 | 130 | 18 | 324 | 44 | 293 | 26 | NA | 700 | 0.3 | 23.84 | 1700000
2023-04-20 | 71230 | 71.23 | 7.31 | 7.63 | 135 | 16 | 332 | 36 | 296 | 25 | NA | 400 | 0.2 | 24.9 | 1300000
2023-04-21 | 74630 | 74.63 | 7.27 | 7.66 | 140 | 18 | 312 | 44 | 275 | 27 | NA | 600 | 0.3 | 23.35 | 1400000
2023-04-22 | 70780 | 70.78 | 7.18 | 7.63 | 130 | 17 | 316 | 40 | 286 | 26 | NA | 500 | 0.2 | 24.47 | 1700000
2023-04-23 | 69970 | 69.97 | 7.25 | 7.65 | 125 | 16 | 324 | 44 | 297 | 25 | NA | 700 | 0.3 | 24 | 1400000
2023-04-24 | 75320 | 75.32 | 7.18 | 7.67 | 140 | 18 | 332 | 48 | 305 | 26 | NA | 400 | 0.3 | 23.24 | 1300000
2023-04-25 | 76810 | 76.81 | 7.21 | 7.66 | 130 | 17 | 328 | 44 | 272 | 25 | NA | 600 | 0.2 | 22.77 | 1700000
2023-04-26 | 74560 | 74.56 | 7.26 | 7.64 | 135 | 16 | 336 | 40 | 295 | 27 | NA | 500 | 0.3 | 24.09 | 1400000
2023-04-27 | 76810 | 76.81 | 7.22 | 7.67 | 130 | 18 | 324 | 44 | 284 | 26 | NA | 700 | 0.3 | 23.52 | 1700000
2023-04-28 | 74700 | 74.7 | 7.31 | 7.69 | 140 | 17 | 316 | 40 | 278 | 25 | NA | 400 | 0.2 | 24.07 | 1300000
2023-04-29 | 70300 | 70.3 | 7.33 | 7.71 | 145 | 16 | 312 | 36 | 282 | 26 | NA | 600 | 0.3 | 24.11 | 1400000
2023-04-30 | 71120 | 71.12 | 7.28 | 7.73 | 135 | 19 | 324 | 40 | 279 | 25 | NA | 500 | 0.3 | 24.57 | 1700000
Average | 73058.6667 | 73.0587 | 7.2793 | 7.6397 | 133.5 | 17.1 | 324.8 | 42.5333 | 289 | 26 | NA | 566.6667 | 0.25667 | 23.8487 | 1496666.6667
2191.76
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 68850 | 68.85 | 7.18 | 7.56 | 125 | 16 | 312 | 36 | 272 | 25 |  | 400 | 0.2 | 22.77 | 1300000
Max | 81420 | 81.42 | 7.38 | 7.73 | 145 | 19 | 336 | 48 | 307 | 27 |  | 700 | 0.3 | 24.9 | 1700000