## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-04-01 | 103790 | 103.79 | 7.25 | 7.5 | 140 | 22 | 296 | 40 | 272 | 35 | NA | 400 | 0.3 | 22.88 | 1700000
2024-04-02 | 104180 | 104.18 | 7.21 | 7.46 | 125 | 23 | 308 | 44 | 280 | 33 | NA | 600 | 0.3 | 23.72 | 1100000
2024-04-03 | 101490 | 101.49 | 7.2 | 7.41 | 135 | 21 | 312 | 40 | 278 | 36 | NA | 400 | 0.3 | 22.21 | 1400000
2024-04-04 | 103930 | 103.93 | 7.29 | 7.43 | 140 | 20 | 304 | 44 | 270 | 34 | NA | 500 | 0.3 | 23.8 | 1200000
2024-04-05 | 109360 | 109.36 | 7.34 | 7.48 | 130 | 19 | 308 | 40 | 280 | 36 | NA | 600 | 0.3 | 23.41 | 1700000
2024-04-06 | 108260 | 108.26 | 7.28 | 7.44 | 140 | 21 | 312 | 44 | 274 | 34 | NA | 700 | 0.3 | 22.08 | 1400000
2024-04-07 | 107860 | 107.86 | 7.25 | 7.42 | 130 | 20 | 316 | 40 | 278 | 36 | NA | 400 | 0.3 | 22.6 | 1200000
2024-04-08 | 108750 | 108.75 | 7.23 | 7.46 | 135 | 19 | 292 | 44 | 276 | 35 | NA | 800 | 0.3 | 23.05 | 1100000
2024-04-09 | 109710 | 109.71 | 7.29 | 7.44 | 140 | 22 | 300 | 44 | 270 | 36 | NA | 500 | 0.3 | 22.77 | 1200000
2024-04-10 | 110170 | 110.17 | 7.24 | 7.43 | 130 | 23 | 304 | 48 | 265 | 37 | NA | 700 | 0.3 | 23.69 | 1400000
2024-04-11 | 113140 | 113.14 | 7.21 | 7.45 | 135 | 21 | 296 | 40 | 268 | 38 | NA | 500 | 0.3 | 22.95 | 1200000
2024-04-12 | 108150 | 108.15 | 7.24 | 7.46 | 140 | 22 | 300 | 44 | 272 | 37 | NA | 600 | 0.3 | 22.21 | 1300000
2024-04-13 | 113380 | 113.38 | 7.21 | 7.42 | 130 | 23 | 296 | 40 | 270 | 36 | NA | 800 | 0.3 | 22.96 | 1700000
2024-04-14 | 107480 | 107.48 | 7.18 | 7.45 | 140 | 20 | 308 | 40 | 264 | 34 | NA | 400 | 0.3 | 23.7 | 1100000
2024-04-15 | 110920 | 110.92 | 7.22 | 7.44 | 125 | 22 | 312 | 48 | 276 | 33 | NA | 500 | 0.3 | 22.42 | 1400000
2024-04-16 | 111460 | 111.46 | 7.19 | 7.41 | 130 | 21 | 304 | 44 | 275 | 34 | NA | 700 | 0.3 | 22.9 | 1700000
2024-04-17 | 104960 | 104.96 | 7.16 | 7.43 | 135 | 20 | 308 | 40 | 266 | 36 | NA | 500 | 0.3 | 22.59 | 1200000
2024-04-18 | 107730 | 107.73 | 7.22 | 7.36 | 140 | 22 | 300 | 44 | 269 | 38 | NA | 400 | 0.3 | 23.21 | 1300000
2024-04-19 | 112160 | 112.16 | 7.17 | 7.39 | 125 | 24 | 312 | 48 | 284 | 35 | NA | 700 | 0.3 | 23.12 | 1400000
2024-04-20 | 102380 | 102.38 | 7.18 | 7.44 | 135 | 19 | 296 | 40 | 266 | 37 | NA | 600 | 0.3 | 23.72 | 1100000
2024-04-21 | 104450 | 104.45 | 7.21 | 7.35 | 130 | 20 | 300 | 44 | 273 | 33 | NA | 500 | 0.3 | 22.94 | 1300000
2024-04-22 | 101480 | 101.48 | 7.19 | 7.38 | 125 | 23 | 308 | 48 | 278 | 38 | NA | 800 | 0.3 | 22.99 | 1200000
2024-04-23 | 102570 | 102.57 | 7.15 | 7.35 | 140 | 21 | 312 | 48 | 274 | 43 | NA | 400 | 0.3 | 22.98 | 1700000
2024-04-24 | 103240 | 103.24 | 7.17 | 7.39 | 135 | 22 | 304 | 44 | 269 | 35 | NA | 600 | 0.3 | 24.1 | 1400000
2024-04-25 | 100140 | 100.14 | 7.24 | 7.37 | 130 | 20 | 296 | 40 | 274 | 33 | NA | 500 | 0.3 | 24.06 | 1300000
2024-04-26 | 99850 | 99.85 | 7.19 | 7.46 | 125 | 23 | 308 | 48 | 265 | 36 | NA | 400 | 0.3 | 23.9 | 1400000
2024-04-27 | 103890 | 103.89 | 7.16 | 7.33 | 135 | 21 | 304 | 44 | 277 | 34 | NA | 800 | 0.3 | 23.89 | 1200000
2024-04-28 | 107090 | 107.09 | 7.13 | 7.37 | 130 | 19 | 296 | 40 | 270 | 33 | NA | 700 | 0.3 | 23.45 | 1100000
2024-04-29 | 103960 | 103.96 | 7.19 | 7.44 | 135 | 24 | 308 | 48 | 278 | 35 | NA | 600 | 0.3 | 23.09 | 1700000
2024-04-30 | 100490 | 100.49 | 7.27 | 7.39 | 125 | 20 | 304 | 44 | 275 | 34 | NA | 400 | 0.3 | 23.06 | 1300000
Average | 106214 | 106.214 | 7.2153 | 7.4183 | 133 | 21.2333 | 304.1333 | 43.4667 | 272.8667 | 35.4667 |  | 566.6667 | 0.3 | 23.1483 | 1346666.6667
3186.42
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 99850 | 99.85 | 7.13 | 7.33 | 125 | 19 | 292 | 40 | 264 | 33 |  | 400 | 0.3 | 22.08 | 1100000
Max | 113380 | 113.38 | 7.34 | 7.5 | 140 | 24 | 316 | 48 | 284 | 43 |  | 800 | 0.3 | 24.1 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-04-01 | 71740 | 71.74 | 7.12 | 7.59 | 130 | 17 | 300 | 44 | 268 | 27 | NA | 400 | 0.3 | 23.65 | 1400000
2024-04-02 | 69490 | 69.49 | 7.08 | 7.49 | 125 | 16 | 304 | 44 | 276 | 26 | NA | 700 | 0.3 | 24.37 | 1200000
2024-04-03 | 76300 | 76.3 | 7.14 | 7.76 | 125 | 17 | 284 | 48 | 265 | 27 | NA | 600 | 0.2 | 23.74 | 1700000
2024-04-04 | 72250 | 72.25 | 7.11 | 7.87 | 130 | 16 | 288 | 44 | 259 | 25 | NA | 500 | 0.3 | 24.08 | 1400000
2024-04-05 | 75700 | 75.7 | 7.06 | 7.9 | 125 | 15 | 276 | 40 | 267 | 25 | NA | 400 | 0.3 | 23.75 | 1300000
2024-04-06 | 75970 | 75.97 | 7.05 | 7.93 | 130 | 16 | 292 | 44 | 271 | 27 | NA | 600 | 0.3 | 23.49 | 1200000
2024-04-07 | 74680 | 74.68 | 7.07 | 7.85 | 135 | 17 | 284 | 40 | 266 | 26 | NA | 500 | 0.2 | 22.81 | 1300000
2024-04-08 | 72830 | 72.83 | 7.04 | 7.89 | 135 | 18 | 296 | 48 | 263 | 28 | NA | 700 | 0.3 | 24.18 | 1700000
2024-04-09 | 76330 | 76.33 | 7.05 | 7.96 | 130 | 16 | 276 | 40 | 258 | 25 | NA | 600 | 0.3 | 24.45 | 1400000
2024-04-10 | 71880 | 71.88 | 6.98 | 7.93 | 125 | 17 | 284 | 44 | 269 | 27 | NA | 400 | 0.3 | 23.48 | 1300000
2024-04-11 | 78930 | 78.93 | 6.99 | 7.83 | 130 | 16 | 288 | 40 | 264 | 26 | NA | 700 | 0.2 | 24.66 | 1700000
2024-04-12 | 72620 | 72.62 | 6.97 | 7.85 | 125 | 16 | 276 | 44 | 265 | 27 | NA | 500 | 0.3 | 22.72 | 1400000
2024-04-13 | 76520 | 76.52 | 7.02 | 7.82 | 130 | 15 | 284 | 40 | 262 | 24 | NA | 600 | 0.3 | 24.33 | 1200000
2024-04-14 | 77590 | 77.59 | 7.02 | 7.61 | 125 | 17 | 272 | 44 | 270 | 26 | NA | 500 | 0.3 | 23.32 | 1400000
2024-04-15 | 72870 | 72.87 | 6.97 | 7.92 | 125 | 15 | 276 | 44 | 268 | 28 | NA | 700 | 0.2 | 23.56 | 1700000
2024-04-16 | 75690 | 75.69 | 6.95 | 7.57 | 120 | 16 | 292 | 48 | 273 | 27 | NA | 400 | 0.3 | 22.59 | 1300000
2024-04-17 | 74210 | 74.21 | 6.98 | 7.72 | 130 | 17 | 288 | 40 | 264 | 26 | NA | 600 | 0.3 | 24.08 | 1400000
2024-04-18 | 73580 | 73.58 | 7.03 | 7.67 | 125 | 16 | 284 | 44 | 272 | 28 | NA | 500 | 0.3 | 22.85 | 1700000
2024-04-19 | 75800 | 75.8 | 6.95 | 7.73 | 130 | 17 | 296 | 40 | 261 | 27 | NA | 700 | 0.3 | 23.18 | 1400000
2024-04-20 | 73530 | 73.53 | 7.03 | 7.65 | 125 | 16 | 300 | 44 | 273 | 28 | NA | 400 | 0.3 | 24.18 | 1200000
2024-04-21 | 67780 | 67.78 | 7.07 | 7.63 | 125 | 17 | 304 | 48 | 278 | 28 | NA | 600 | 0.3 | 23.35 | 1400000
2024-04-22 | 74820 | 74.82 | 7.03 | 7.79 | 135 | 17 | 292 | 40 | 271 | 26 | NA | 700 | 0.3 | 24.38 | 1700000
2024-04-23 | 74490 | 74.49 | 7.02 | 7.76 | 130 | 16 | 284 | 44 | 263 | 25 | NA | 500 | 0.3 | 22.78 | 1300000
2024-04-24 | 72950 | 72.95 | 7.04 | 7.83 | 135 | 18 | 288 | 48 | 273 | 27 | NA | 600 | 0.3 | 23.53 | 1700000
2024-04-25 | 72420 | 72.42 | 7.03 | 7.75 | 130 | 17 | 276 | 40 | 269 | 26 | NA | 500 | 0.3 | 22.82 | 1300000
2024-04-26 | 72220 | 72.22 | 7.06 | 7.85 | 140 | 18 | 296 | 44 | 272 | 25 | NA | 600 | 0.3 | 23.55 | 1400000
2024-04-27 | 72170 | 72.17 | 7.09 | 7.91 | 145 | 17 | 304 | 40 | 274 | 27 | NA | 700 | 0.3 | 23.24 | 1200000
2024-04-28 | 74280 | 74.28 | 7.24 | 7.81 | 155 | 17 | 284 | 44 | 291 | 26 | NA | 400 | 0.3 | 23.58 | 1300000
2024-04-29 | 73350 | 73.35 | 7.09 | 7.93 | 130 | 16 | 276 | 40 | 263 | 25 | NA | 500 | 0.3 | 24.22 | 1400000
2024-04-30 | 73400 | 73.4 | 7.07 | 7.94 | 140 | 18 | 288 | 44 | 272 | 24 | NA | 600 | 0.3 | 24.18 | 1700000
Average | 73879.6667 | 73.8797 | 7.045 | 7.7913 | 130.6667 | 16.5667 | 287.7333 | 43.2 | 268.6667 | 26.3 |  | 556.6667 | 0.28667 | 23.6367 | 1423333.3333
2216.39
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 67780 | 67.78 | 6.95 | 7.49 | 120 | 15 | 272 | 40 | 258 | 24 |  | 400 | 0.2 | 22.59 | 1200000
Max | 78930 | 78.93 | 7.24 | 7.96 | 155 | 18 | 304 | 48 | 291 | 28 |  | 700 | 0.3 | 24.66 | 1700000