## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-08-01 | 93610 | 93.61 | 7.33 | 7.47 | 120 | 24 | 294 | 36 | 286 | 27 | NA | 600 | 0.2 | 25.07 | 1100000
2023-08-02 | 108070 | 108.07 | 7.29 | 7.39 | 125 | 25 | 312 | 40 | 296 | 30 | NA | 400 | 0.3 | 25.3 | 1400000
2023-08-03 | 116700 | 116.7 | 7.33 | 7.47 | 130 | 26 | 294 | 38 | 286 | 27 | NA | 700 | 0.2 | 25.07 | 1700000
2023-08-04 | 97220 | 97.22 | 7.31 | 7.35 | 135 | 28 | 302 | 42 | 280 | 30 | NA | 500 | 0.3 | 24.8 | 1200000
2023-08-05 | 102210 | 102.21 | 7.28 | 7.41 | 120 | 24 | 296 | 40 | 269 | 29 | NA | 600 | 0.2 | 23.86 | 1400000
2023-08-06 | 112370 | 112.37 | 7.31 | 7.37 | 125 | 23 | 304 | 38 | 278 | 30 | NA | 700 | 0.3 | 25.1 | 1700000
2023-08-07 | 112120 | 112.12 | 7.27 | 7.39 | 130 | 26 | 300 | 36 | 273 | 31 | NA | 400 | 0.2 | 24.16 | 1300000
2023-08-08 | 110150 | 110.15 | 7.28 | 7.3 | 120 | 24 | 292 | 38 | 279 | 30 | NA | 500 | 0.3 | 24.8 | 1100000
2023-08-09 | 106030 | 106.03 | 7.26 | 7.35 | 125 | 25 | 312 | 42 | 298 | 28 | NA | 600 | 0.2 | 24.6 | 1200000
2023-08-10 | 104950 | 104.95 | 7.28 | 7.39 | 135 | 29 | 306 | 44 | 294 | 30 | NA | 500 | 0.3 | 25.6 | 1400000
2023-08-11 | 105600 | 105.6 | 7.27 | 7.33 | 140 | 25 | 308 | 42 | 288 | 32 | NA | 400 | 0.2 | 24.6 | 1200000
2023-08-12 | 107500 | 107.5 | 7.24 | 7.35 | 125 | 26 | 304 | 40 | 281 | 31 | NA | 500 | 0.3 | 24.8 | 1300000
2023-08-13 | 108910 | 108.91 | 7.25 | 7.37 | 120 | 25 | 316 | 38 | 287 | 33 | NA | 700 | 0.2 | 24.5 | 1700000
2023-08-14 | 110130 | 110.13 | 7.23 | 7.4 | 125 | 26 | 308 | 40 | 276 | 29 | NA | 600 | 0.3 | 24.3 | 1100000
2023-08-15 | 106010 | 106.01 | 7.24 | 7.35 | 135 | 29 | 320 | 44 | 294 | 31 | NA | 500 | 0.2 | 24.9 | 1400000
2023-08-16 | 105650 | 105.65 | 7.23 | 7.31 | 130 | 25 | 312 | 38 | 292 | 29 | NA | 700 | 0.2 | 24.3 | 1200000
2023-08-17 | 113370 | 113.37 | 7.2 | 7.38 | 120 | 24 | 304 | 40 | 285 | 28 | NA | 400 | 0.3 | 23.94 | 1700000
2023-08-18 | 114410 | 114.41 | 7.24 | 7.4 | 125 | 27 | 300 | 42 | 274 | 34 | NA | 600 | 0.3 | 24.17 | 1200000
2023-08-19 | 113860 | 113.86 | 7.27 | 7.35 | 120 | 29 | 296 | 48 | 270 | 41 | NA | 500 | 0.2 | 24.31 | 1400000
2023-08-20 | 113400 | 113.4 | 7.29 | 7.41 | 130 | 25 | 308 | 45 | 288 | 42 | NA | 400 | 0.3 | 24.9 | 1400000
2023-08-21 | 113000 | 113 | 7.31 | 7.37 | 120 | 23 | 314 | 38 | 295 | 32 | NA | 500 | 0.2 | 24.95 | 1700000
2023-08-22 | 117780 | 117.78 | 7.34 | 7.45 | 130 | 24 | 296 | 36 | 282 | 28 | NA | 600 | 0.3 | 24.63 | 1200000
2023-08-23 | 138980 | 138.98 | 7.28 | 7.25 | 123 | 25 | 296 | 40 | 284 | 31 | NA | 500 | 0.3 | 24.7 | 1300000
2023-08-24 | 115520 | 115.52 | 7.22 | 7.31 | 130 | 27 | 302 | 38 | 278 | 36 | NA | 700 | 0.2 | 24.6 | 1100000
2023-08-25 | 120150 | 120.15 | 7.19 | 7.32 | 120 | 24 | 314 | 39 | 284 | 37 | NA | 500 | 0.3 | 24.7 | 1700000
2023-08-26 | 119140 | 119.14 | 7.14 | 7.37 | 125 | 27 | 304 | 42 | 279 | 35 | NA | 800 | 0.3 | 25.12 | 1200000
2023-08-27 | 116020 | 116.02 | 7.09 | 7.36 | 135 | 26 | 306 | 43 | 294 | 36 | NA | 400 | 0.2 | 24.65 | 1400000
2023-08-28 | 121230 | 121.23 | 7.19 | 7.45 | 125 | 24 | 304 | 40 | 287 | 38 | NA | 700 | 0.2 | 24.7 | 1700000
2023-08-29 | 117390 | 117.39 | 7.25 | 7.34 | 130 | 25 | 312 | 42 | 295 | 35 | NA | 600 | 0.3 | 24.68 | 1200000
2023-08-30 | 116360 | 116.36 | 7.07 | 7.4 | 135 | 24 | 310 | 40 | 281 | 36 | NA | 800 | 0.3 | 25.2 | 1300000
2023-08-31 | 111960 | 111.96 | 7.22 | 7.39 | 125 | 23 | 318 | 41 | 293 | 39 | NA | 500 | 0.2 | 24.4 | 1400000
Average | 111929.0323 | 111.929 | 7.2484 | 7.3726 | 126.871 | 25.3871 | 305.2903 | 40.3226 | 284.7097 | 32.4194 | NA | 561.2903 | 0.25161 | 24.6906 | 1364516.129
3469.8
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 93610 | 93.61 | 7.07 | 7.25 | 120 | 23 | 292 | 36 | 269 | 27 |  | 400 | 0.2 | 23.86 | 1100000
Max | 138980 | 138.98 | 7.34 | 7.47 | 140 | 29 | 320 | 48 | 298 | 42 |  | 800 | 0.3 | 25.6 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-08-01 | 76890 | 76.89 | 7.37 | 7.61 | 130 | 17 | 308 | 44 | 271 | 25 | NA | 700 | 0.3 | 23.31 | 1700000
2023-08-02 | 83730 | 83.73 | 7.23 | 7.59 | 125 | 16 | 312 | 40 | 268 | 24 | NA | 400 | 0.2 | 23.24 | 1300000
2023-08-03 | 84130 | 84.13 | 7.38 | 7.52 | 135 | 18 | 324 | 44 | 263 | 23 | NA | 600 | 0.3 | 23.35 | 1400000
2023-08-04 | 80320 | 80.32 | 7.34 | 7.49 | 125 | 17 | 292 | 40 | 242 | 24 | NA | 500 | 0.3 | 23.73 | 1700000
2023-08-05 | 82190 | 82.19 | 7.38 | 7.63 | 130 | 16 | 296 | 40 | 251 | 23 | NA | 400 | 0.2 | 24.74 | 1300000
2023-08-06 | 78870 | 78.87 | 7.39 | 7.65 | 140 | 18 | 292 | 44 | 257 | 24 | NA | 500 | 0.3 | 23.43 | 1400000
2023-08-07 | 74760 | 74.76 | 7.37 | 7.62 | 135 | 16 | 304 | 36 | 262 | 23 | NA | 600 | 0.2 | 22.55 | 1700000
2023-08-08 | 74640 | 74.64 | 7.38 | 7.66 | 130 | 17 | 332 | 40 | 324 | 25 | NA | 400 | 0.2 | 22.83 | 1400000
2023-08-09 | 75340 | 75.34 | 7.59 | 7.57 | 125 | 16 | 328 | 44 | 337 | 23 | NA | 500 | 0.3 | 24.3 | 1300000
2023-08-10 | 80360 | 80.36 | 7.41 | 7.58 | 135 | 17 | 332 | 40 | 315 | 24 | NA | 600 | 0.2 | 23.22 | 1700000
2023-08-11 | 77730 | 77.73 | 7.39 | 7.62 | 140 | 18 | 340 | 44 | 307 | 25 | NA | 400 | 0.3 | 23.42 | 1400000
2023-08-12 | 81230 | 81.23 | 7.25 | 7.63 | 125 | 16 | 336 | 40 | 298 | 24 | NA | 500 | 0.2 | 24.02 | 1700000
2023-08-13 | 75630 | 75.63 | 7.24 | 7.61 | 130 | 17 | 328 | 40 | 308 | 25 | NA | 600 | 0.2 | 23.16 | 1400000
2023-08-14 | 79890 | 79.89 | 7.14 | 7.65 | 125 | 16 | 316 | 44 | 295 | 24 | NA | 400 | 0.3 | 23.72 | 1300000
2023-08-15 | 77050 | 77.05 | 7.12 | 7.63 | 135 | 18 | 344 | 48 | 317 | 25 | NA | 500 | 0.3 | 23.11 | 1700000
2023-08-16 | 77650 | 77.65 | 7.16 | 7.6 | 120 | 15 | 336 | 44 | 308 | 24 | NA | 400 | 0.2 | 23.15 | 1200000
2023-08-17 | 80560 | 80.56 | 7.18 | 7.59 | 130 | 17 | 324 | 40 | 289 | 23 | NA | 600 | 0.3 | 23.11 | 1300000
2023-08-18 | 80910 | 80.91 | 7.15 | 7.62 | 120 | 16 | 336 | 44 | 311 | 25 | NA | 500 | 0.3 | 23.22 | 1400000
2023-08-19 | 78970 | 78.97 | 7.18 | 7.61 | 125 | 17 | 332 | 40 | 309 | 24 | NA | 400 | 0.2 | 23.03 | 1700000
2023-08-20 | 80390 | 80.39 | 7.16 | 7.57 | 120 | 16 | 348 | 44 | 321 | 26 | NA | 500 | 0.3 | 24.32 | 1300000
2023-08-21 | 78760 | 78.76 | 7.13 | 7.59 | 130 | 17 | 340 | 40 | 317 | 25 | NA | 600 | 0.3 | 24.64 | 1700000
2023-08-22 | 80840 | 80.84 | 7.16 | 7.6 | 125 | 16 | 304 | 44 | 278 | 24 | NA | 400 | 0.3 | 23.93 | 1400000
2023-08-23 | 92420 | 92.42 | 7.33 | 7.51 | 130 | 17 | 292 | 40 | 257 | 23 | NA | 700 | 0.3 | 23.12 | 1200000
2023-08-24 | 87180 | 87.18 | 7.26 | 7.47 | 135 | 16 | 296 | 36 | 253 | 24 | NA | 500 | 0.2 | 23.16 | 1700000
2023-08-25 | 84120 | 84.12 | 7.29 | 7.51 | 140 | 18 | 304 | 40 | 261 | 23 | NA | 600 | 0.3 | 23.05 | 1300000
2023-08-26 | 81410 | 81.41 | 7.27 | 7.5 | 135 | 17 | 312 | 44 | 273 | 24 | NA | 400 | 0.3 | 23.15 | 1400000
2023-08-27 | 78840 | 78.84 | 7.23 | 7.53 | 125 | 16 | 296 | 40 | 272 | 25 | NA | 500 | 0.2 | 23.28 | 1700000
2023-08-28 | 77160 | 77.16 | 7.21 | 7.5 | 135 | 17 | 304 | 40 | 287 | 24 | NA | 600 | 0.3 | 24.44 | 1400000
2023-08-29 | 70440 | 70.44 | 7.19 | 7.54 | 130 | 16 | 292 | 44 | 268 | 22 | NA | 400 | 0.2 | 23.85 | 1200000
2023-08-30 | 70270 | 70.27 | 7.22 | 7.52 | 135 | 17 | 300 | 40 | 279 | 23 | NA | 600 | 0.2 | 23.78 | 1700000
2023-08-31 | 73420 | 73.42 | 7.18 | 7.47 | 140 | 18 | 304 | 44 | 281 | 24 | NA | 500 | 0.3 | 24.21 | 1400000
Average | 79229.0323 | 79.229 | 7.2671 | 7.5739 | 130.3226 | 16.7419 | 316.2581 | 41.6774 | 286.4194 | 24 | NA | 509.6774 | 0.25806 | 23.5345 | 1464516.129
2456.1
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 70270 | 70.27 | 7.12 | 7.47 | 120 | 15 | 292 | 36 | 242 | 22 |  | 400 | 0.2 | 22.55 | 1200000
Max | 92420 | 92.42 | 7.59 | 7.66 | 140 | 18 | 348 | 48 | 337 | 26 |  | 700 | 0.3 | 24.74 | 1700000