## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-12-01 | 101620 | 101.62 | 7.05 | 7.49 | 135 | 20 | 308 | 45 | 285 | 44 | NA | 700 | 0.2 | 23.46 | 1100000
2023-12-02 | 101290 | 101.29 | 7.03 | 7.54 | 140 | 20 | 286 | 44 | 282 | 39 | NA | 600 | 0.2 | 24.35 | 1700000
2023-12-03 | 103890 | 103.89 | 7.08 | 7.46 | 125 | 18 | 288 | 40 | 268 | 38 | NA | 600 | 0.3 | 24.49 | 1700000
2023-12-04 | 107890 | 107.89 | 7.03 | 7.52 | 130 | 21 | 292 | 40 | 265 | 38 | NA | 700 | 0.3 | 23.46 | 1200000
2023-12-05 | 105650 | 105.65 | 7.39 | 7.45 | 135 | 24 | 305 | 44 | 266 | 39 | NA | 500 | 0.2 | 24.22 | 1100000
2023-12-06 | 102950 | 102.95 | 7.52 | 7.58 | 140 | 18 | 294 | 41 | 253 | 40 | NA | 500 | 0.3 | 24.54 | 1200000
2023-12-07 | 113670 | 113.67 | 7.38 | 7.45 | 130 | 22 | 304 | 40 | 264 | 38 | NA | 400 | 0.2 | 24.5 | 1400000
2023-12-08 | 113020 | 113.02 | 7.52 | 7.59 | 135 | 20 | 292 | 44 | 277 | 39 | NA | 600 | 0.3 | 24.49 | 1100000
2023-12-09 | 110720 | 110.72 | 7.5 | 7.52 | 125 | 21 | 304 | 40 | 280 | 40 | NA | 500 | 0.3 | 23.9 | 1700000
2023-12-10 | 109190 | 109.19 | 7.36 | 7.47 | 140 | 23 | 296 | 44 | 265 | 39 | NA | 600 | 0.2 | 24.32 | 1100000
2023-12-11 | 110650 | 110.65 | 7.35 | 7.46 | 130 | 21 | 308 | 40 | 273 | 42 | NA | 700 | 0.2 | 24.12 | 1400000
2023-12-12 | 110060 | 110.06 | 7.28 | 7.52 | 135 | 20 | 312 | 40 | 276 | 45 | NA | 400 | 0.3 | 20.39 | 1200000
2023-12-13 | 102780 | 102.78 | 7.26 | 7.38 | 125 | 19 | 316 | 40 | 292 | 40 | NA | 600 | 0.2 | 22.74 | 1700000
2023-12-14 | 104100 | 104.1 | 7.31 | 7.47 | 130 | 20 | 304 | 44 | 268 | 38 | NA | 500 | 0.3 | 23.31 | 1100000
2023-12-15 | 107690 | 107.69 | 7.35 | 7.44 | 125 | 21 | 312 | 44 | 275 | 41 | NA | 400 | 0.2 | 23.76 | 1400000
2023-12-16 | 107420 | 107.42 | 7.42 | 7.45 | 130 | 23 | 308 | 40 | 270 | 40 | NA | 600 | 0.3 | 22.86 | 1200000
2023-12-17 | 108680 | 108.68 | 7.43 | 7.52 | 125 | 20 | 296 | 44 | 276 | 37 | NA | 500 | 0.2 | 23.11 | 1700000
2023-12-18 | 108160 | 108.16 | 7.5 | 7.42 | 130 | 19 | 300 | 40 | 271 | 40 | NA | 700 | 0.3 | 23.41 | 1300000
2023-12-19 | 111090 | 111.09 | 7.43 | 7.48 | 135 | 21 | 296 | 44 | 282 | 44 | NA | 500 | 0.3 | 22.86 | 1400000
2023-12-20 | 110060 | 110.06 | 7.19 | 7.41 | 120 | 28 | 292 | 40 | 264 | 39 | NA | 400 | 0.2 | 24.9 | 1200000
2023-12-21 | 110070 | 110.07 | 7.15 | 7.38 | 125 | 22 | 304 | 44 | 270 | 38 | NA | 600 | 0.3 | 24.3 | 1700000
2023-12-22 | 108460 | 108.46 | 7.13 | 7.44 | 130 | 20 | 308 | 40 | 277 | 40 | NA | 400 | 0.2 | 23.47 | 1100000
2023-12-23 | 113380 | 113.38 | 7.16 | 7.4 | 135 | 23 | 300 | 44 | 281 | 41 | NA | 700 | 0.3 | 23.8 | 1300000
2023-12-24 | 111660 | 111.66 | 7.19 | 7.28 | 125 | 20 | 292 | 40 | 267 | 42 | NA | 800 | 0.2 | 23.67 | 1700000
2023-12-25 | 108580 | 108.58 | 7.09 | 7.25 | 130 | 21 | 316 | 44 | 275 | 40 | NA | 500 | 0.2 | 23.6 | 1200000
2023-12-26 | 104170 | 104.17 | 7.06 | 7.33 | 135 | 22 | 304 | 40 | 273 | 38 | NA | 600 | 0.3 | 24.1 | 1400000
2023-12-27 | 100060 | 100.06 | 7.07 | 7.36 | 140 | 23 | 312 | 44 | 266 | 41 | NA | 400 | 0.2 | 23.18 | 1300000
2023-12-28 | 100920 | 100.92 | 7.02 | 7.28 | 125 | 22 | 292 | 40 | 272 | 38 | NA | 500 | 0.3 | 24.01 | 1100000
2023-12-29 | 98130 | 98.13 | 7.04 | 7.33 | 140 | 20 | 324 | 36 | 270 | 40 | NA | 700 | 0.2 | 23.86 | 1700000
2023-12-30 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | 23.85 | 1400000 | Naini-I STP was shutdown from 12:05 AM on 30.12.2023 for replacement of flowmeter in outlet line of STP. Subsequently, Gaughat MPS & Chacharnalla SPS were also shutdown.
2023-12-31 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | 23.93 | 1200000
Average | 100193.871 | 100.1939 | 7.2514 | 7.4369 | 131.2069 | 21.1034 | 302.2414 | 41.7241 | 272.5172 | 39.931 |  | 558.6207 | 0.24828 | 23.7084 | 1354838.7097
3106.01
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.02 | 7.25 | 120 | 18 | 286 | 36 | 253 | 37 |  | 400 | 0.2 | 20.39 | 1100000
Max | 113670 | 113.67 | 7.52 | 7.59 | 140 | 28 | 324 | 45 | 292 | 45 |  | 800 | 0.3 | 24.9 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-12-01 | 81150 | 81.15 | 7.2 | 7.73 | 130 | 18 | 288 | 40 | 261 | 23 | NA | 500 | 0.3 | 23.91 | 1200000
2023-12-02 | 77620 | 77.62 | 7.27 | 7.76 | 125 | 16 | 276 | 44 | 257 | 24 | NA | 600 | 0.3 | 24.73 | 1400000
2023-12-03 | 79150 | 79.15 | 7.21 | 7.78 | 135 | 17 | 288 | 40 | 263 | 26 | NA | 700 | 0.2 | 24.21 | 1700000
2023-12-04 | 77780 | 77.78 | 7.18 | 7.75 | 120 | 16 | 284 | 44 | 259 | 25 | NA | 400 | 0.3 | 23.52 | 1300000
2023-12-05 | 78230 | 78.23 | 7.25 | 7.79 | 130 | 17 | 292 | 40 | 265 | 24 | NA | 500 | 0.3 | 23.74 | 1400000
2023-12-06 | 76380 | 76.38 | 7.23 | 7.81 | 115 | 16 | 296 | 48 | 268 | 26 | NA | 600 | 0.2 | 24.04 | 1700000
2023-12-07 | 78730 | 78.73 | 7.21 | 7.78 | 135 | 17 | 284 | 44 | 261 | 25 | NA | 500 | 0.3 | 23.94 | 1400000
2023-12-08 | 77910 | 77.91 | 7.25 | 7.75 | 130 | 18 | 284 | 40 | 270 | 27 | NA | 700 | 0.3 | 24.53 | 1400000
2023-12-09 | 78940 | 78.94 | 7.26 | 7.76 | 125 | 16 | 276 | 44 | 262 | 26 | NA | 400 | 0.3 | 23.47 | 1300000
2023-12-10 | 77320 | 77.32 | 7.24 | 7.73 | 130 | 17 | 288 | 40 | 257 | 27 | NA | 600 | 0.2 | 24.94 | 1700000
2023-12-11 | 75520 | 75.52 | 7.27 | 7.74 | 135 | 18 | 292 | 48 | 253 | 28 | NA | 500 | 0.3 | 23.89 | 1400000
2023-12-12 | 77850 | 77.85 | 7.25 | 7.76 | 130 | 17 | 284 | 44 | 259 | 26 | NA | 600 | 0.3 | 23.65 | 1300000
2023-12-13 | 76520 | 76.52 | 7.26 | 7.78 | 125 | 16 | 280 | 44 | 263 | 25 | NA | 400 | 0.2 | 23.8 | 1200000
2023-12-14 | 76890 | 76.89 | 7.29 | 7.76 | 130 | 18 | 288 | 48 | 265 | 27 | NA | 500 | 0.3 | 24.28 | 1400000
2023-12-15 | 75820 | 75.82 | 7.24 | 7.78 | 125 | 17 | 284 | 40 | 267 | 25 | NA | 600 | 0.2 | 24.17 | 1700000
2023-12-16 | 79150 | 79.15 | 7.25 | 7.76 | 135 | 18 | 296 | 44 | 259 | 27 | NA | 400 | 0.3 | 24.43 | 1300000
2023-12-17 | 75910 | 75.91 | 7.27 | 7.78 | 130 | 17 | 292 | 40 | 268 | 26 | NA | 500 | 0.3 | 23.39 | 1200000
2023-12-18 | 76420 | 76.42 | 7.31 | 7.77 | 125 | 16 | 288 | 44 | 263 | 25 | NA | 600 | 0.3 | 24.67 | 1400000
2023-12-19 | 75230 | 75.23 | 7.32 | 7.79 | 135 | 17 | 300 | 40 | 266 | 26 | NA | 700 | 0.2 | 24.05 | 1700000
2023-12-20 | 72280 | 72.28 | 7.3 | 7.83 | 120 | 15 | 284 | 40 | 259 | 24 | NA | 500 | 0.3 | 23.38 | 1400000
2023-12-21 | 76630 | 76.63 | 7.31 | 7.76 | 125 | 17 | 292 | 44 | 262 | 26 | NA | 400 | 0.3 | 24.48 | 1300000
2023-12-22 | 73830 | 73.83 | 7.38 | 7.69 | 120 | 16 | 238 | 40 | 278 | 27 | NA | 600 | 0.2 | 23.43 | 1700000
2023-12-23 | 71620 | 71.62 | 7.29 | 7.8 | 135 | 17 | 284 | 44 | 265 | 26 | NA | 400 | 0.3 | 24.67 | 1400000
2023-12-24 | 76190 | 76.19 | 7.31 | 7.76 | 130 | 18 | 292 | 40 | 271 | 27 | NA | 500 | 0.3 | 23.71 | 1200000
2023-12-25 | 73660 | 73.66 | 7.34 | 7.69 | 125 | 18 | 288 | 44 | 268 | 26 | NA | 700 | 0.2 | 22.5 | 1700000
2023-12-26 | 76430 | 76.43 | 7.32 | 7.73 | 135 | 17 | 284 | 44 | 258 | 25 | NA | 600 | 0.3 | 24.03 | 1400000
2023-12-27 | 75740 | 75.74 | 7.3 | 7.74 | 130 | 18 | 288 | 48 | 263 | 27 | NA | 500 | 0.3 | 23.78 | 1300000
2023-12-28 | 73890 | 73.89 | 7.29 | 7.72 | 125 | 17 | 276 | 44 | 256 | 24 | NA | 600 | 0.2 | 23.52 | 1700000
2023-12-29 | 77210 | 77.21 | 7.32 | 7.75 | 135 | 18 | 284 | 44 | 263 | 27 | NA | 400 | 0.3 | 24.42 | 1400000
2023-12-30 | 65530 | 65.53 | 7.36 | 7.72 | 125 | 16 | 276 | 40 | 270 | 25 | NA | 600 | 0.2 | 23.21 | 1700000
2023-12-31 | 76950 | 76.95 | 7.3 | 7.78 | 130 | 17 | 272 | 40 | 274 | 26 | NA | 500 | 0.3 | 23.71 | 1400000
Average | 76209.0323 | 76.209 | 7.2768 | 7.759 | 128.3871 | 16.9677 | 284.4516 | 42.8387 | 263.6452 | 25.7419 |  | 535.4839 | 0.26774 | 23.9419 | 1441935.4839
2362.48
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 65530 | 65.53 | 7.18 | 7.69 | 115 | 15 | 238 | 40 | 253 | 23 |  | 400 | 0.2 | 22.5 | 1200000
Max | 81150 | 81.15 | 7.38 | 7.83 | 135 | 18 | 300 | 48 | 278 | 28 |  | 700 | 0.3 | 24.94 | 1700000