## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-02-01 | 101610 | 101.61 | 7.11 | 7.23 | 125 | 22 | 296 | 40 | 279 | 42 | NA | 600 | 0.2 | 23.11 | 1300000
2024-02-02 | 97650 | 97.65 | 7.05 | 7.26 | 140 | 23 | 312 | 40 | 284 | 40 | NA | 400 | 0.3 | 22.8 | 1100000
2024-02-03 | 102980 | 102.98 | 7.06 | 7.23 | 130 | 25 | 304 | 48 | 268 | 47 | NA | 500 | 0.2 | 23.59 | 1700000
2024-02-04 | 109200 | 109.2 | 7.09 | 7.27 | 135 | 23 | 312 | 44 | 275 | 41 | NA | 700 | 0.3 | 22.88 | 1200000
2024-02-05 | 115770 | 115.77 | 7.13 | 7.25 | 140 | 22 | 316 | 40 | 288 | 45 | NA | 600 | 0.2 | 22.27 | 1400000
2024-02-06 | 90580 | 90.58 | 7.17 | 7.29 | 125 | 21 | 304 | 48 | 275 | 43 | NA | 400 | 0.3 | 22.63 | 1700000
2024-02-07 | 98430 | 98.43 | 7.22 | 7.33 | 135 | 22 | 308 | 44 | 279 | 45 | NA | 500 | 0.2 | 23.4 | 1100000
2024-02-08 | 103240 | 103.24 | 7.25 | 7.36 | 125 | 20 | 294 | 40 | 274 | 42 | NA | 700 | 0.2 | 21.52 | 1300000
2024-02-09 | 110480 | 110.48 | 7.14 | 7.28 | 130 | 23 | 304 | 44 | 268 | 41 | NA | 400 | 0.3 | 22.5 | 1700000
2024-02-10 | 108610 | 108.61 | 7.15 | 7.29 | 140 | 21 | 312 | 44 | 271 | 40 | NA | 600 | 0.2 | 22.55 | 1200000
2024-02-11 | 109040 | 109.04 | 7.11 | 7.31 | 135 | 24 | 304 | 48 | 266 | 42 | NA | 800 | 0.3 | 23.07 | 1100000
2024-02-12 | 108420 | 108.42 | 7.05 | 7.23 | 130 | 25 | 312 | 44 | 276 | 40 | NA | 400 | 0.2 | 23.54 | 1200000
2024-02-13 | 110890 | 110.89 | 7.09 | 7.31 | 125 | 23 | 296 | 40 | 270 | 43 | NA | 500 | 0.3 | 22.4 | 1400000
2024-02-14 | 110720 | 110.72 | 7.29 | 7.35 | 130 | 24 | 308 | 48 | 278 | 41 | NA | 400 | 0.2 | 22.88 | 1700000
2024-02-15 | 107890 | 107.89 | 7.28 | 7.33 | 140 | 21 | 316 | 44 | 275 | 40 | NA | 700 | 0.3 | 23.4 | 1300000
2024-02-16 | 112890 | 112.89 | 7.19 | 7.29 | 135 | 23 | 304 | 40 | 282 | 43 | NA | 400 | 0.2 | 22.52 | 1200000
2024-02-17 | 111650 | 111.65 | 7.24 | 7.32 | 140 | 22 | 308 | 44 | 265 | 41 | NA | 800 | 0.3 | 22.61 | 1400000
2024-02-18 | 111000 | 111 | 7.21 | 7.35 | 125 | 24 | 312 | 48 | 274 | 40 | NA | 600 | 0.2 | 23.74 | 1100000
2024-02-19 | 110630 | 110.63 | 7.15 | 7.38 | 135 | 21 | 296 | 44 | 267 | 43 | NA | 700 | 0.2 | 23.54 | 1100000
2024-02-20 | 113200 | 113.2 | 7.19 | 7.37 | 140 | 23 | 312 | 40 | 260 | 40 | NA | 600 | 0.3 | 22.17 | 1300000
2024-02-21 | 111780 | 111.78 | 7.24 | 7.32 | 130 | 22 | 304 | 48 | 270 | 44 | NA | 500 | 0.2 | 23.08 | 1400000
2024-02-22 | 106890 | 106.89 | 7.49 | 7.44 | 140 | 21 | 316 | 44 | 282 | 41 | NA | 700 | 0.3 | 22.92 | 1100000
2024-02-23 | 104690 | 104.69 | 7.51 | 7.41 | 135 | 23 | 308 | 40 | 274 | 42 | NA | 500 | 0.2 | 22.44 | 1700000
2024-02-24 | 107930 | 107.93 | 7.27 | 7.39 | 140 | 24 | 312 | 44 | 279 | 39 | NA | 800 | 0.3 | 22.82 | 1200000
2024-02-25 | 111470 | 111.47 | 7.52 | 7.46 | 130 | 22 | 296 | 48 | 275 | 41 | NA | 400 | 0.2 | 22.39 | 1300000
2024-02-26 | 85360 | 85.36 | 7.55 | 7.51 | 125 | 21 | 312 | 44 | 266 | 40 | NA | 700 | 0.3 | 22.76 | 1400000 | On 26.02.2024, Naini-I STP and Gaughat MPS were stopped from 11:00 AM to 5:15 PM for extension of line in downstream of outlet flowmeter of Naini-I STP and maintenance of Air valve in Gaughat MPS. Here, Chacharnalla SPS was in operation and sewage was bypassed before Gaughat MPS
2024-02-27 | 110610 | 110.61 | 7.33 | 7.38 | 130 | 25 | 304 | 48 | 285 | 42 | NA | 500 | 0.2 | 23.43 | 1200000
2024-02-28 | 108630 | 108.63 | 7.26 | 7.35 | 135 | 20 | 296 | 40 | 271 | 41 | NA | 600 | 0.2 | 23.57 | 1100000
2024-02-29 | 114170 | 114.17 | 7.23 | 7.37 | 125 | 22 | 304 | 44 | 273 | 39 | NA | 400 | 0.3 | 23.43 | 1700000
Average | 107117.5862 | 107.1176 | 7.2266 | 7.3331 | 132.7586 | 22.4828 | 306.2759 | 43.8621 | 274.1034 | 41.6552 |  | 565.5172 | 0.24483 | 22.8952 | 1331034.4828
3106.41
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 85360 | 85.36 | 7.05 | 7.23 | 125 | 20 | 294 | 40 | 260 | 39 |  | 400 | 0.2 | 21.52 | 1100000
Max | 115770 | 115.77 | 7.55 | 7.51 | 140 | 25 | 316 | 48 | 288 | 47 |  | 800 | 0.3 | 23.74 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-02-01 | 83450 | 83.45 | 6.9 | 7.68 | 130 | 16 | 288 | 44 | 258 | 27 | NA | 600 | 0.3 | 23.34 | 1200000
2024-02-02 | 82590 | 82.59 | 6.85 | 7.67 | 135 | 18 | 284 | 48 | 264 | 28 | NA | 500 | 0.3 | 23.56 | 1400000
2024-02-03 | 80800 | 80.8 | 6.98 | 7.71 | 125 | 17 | 276 | 44 | 259 | 27 | NA | 400 | 0.3 | 22.54 | 1200000
2024-02-04 | 78980 | 78.98 | 6.99 | 7.65 | 130 | 16 | 280 | 44 | 265 | 29 | NA | 600 | 0.3 | 23.72 | 1700000
2024-02-05 | 88870 | 88.87 | 6.94 | 7.67 | 135 | 17 | 288 | 48 | 253 | 26 | NA | 700 | 0.3 | 23.47 | 1400000
2024-02-06 | 75510 | 75.51 | 7.02 | 7.66 | 140 | 18 | 292 | 44 | 265 | 27 | NA | 500 | 0.2 | 22.49 | 1300000
2024-02-07 | 79270 | 79.27 | 6.97 | 7.72 | 130 | 17 | 284 | 48 | 256 | 28 | NA | 400 | 0.3 | 23.63 | 1400000
2024-02-08 | 81930 | 81.93 | 6.95 | 7.71 | 135 | 18 | 288 | 44 | 267 | 29 | NA | 700 | 0.3 | 23.02 | 1700000
2024-02-09 | 81780 | 81.78 | 6.85 | 7.74 | 140 | 19 | 276 | 48 | 258 | 29 | NA | 600 | 0.3 | 22.69 | 1300000
2024-02-10 | 78820 | 78.82 | 6.84 | 7.77 | 130 | 18 | 284 | 44 | 266 | 27 | NA | 400 | 0.3 | 23.62 | 1200000
2024-02-11 | 77840 | 77.84 | 6.88 | 7.75 | 135 | 18 | 292 | 44 | 261 | 28 | NA | 500 | 0.2 | 22.62 | 1400000
2024-02-12 | 78150 | 78.15 | 6.94 | 7.75 | 140 | 19 | 280 | 48 | 262 | 27 | NA | 600 | 0.3 | 23.54 | 1700000
2024-02-13 | 82650 | 82.65 | 6.89 | 7.7 | 130 | 17 | 296 | 44 | 267 | 28 | NA | 700 | 0.3 | 23.25 | 1300000
2024-02-14 | 76480 | 76.48 | 7.05 | 7.69 | 125 | 17 | 276 | 44 | 258 | 26 | NA | 500 | 0.3 | 22.51 | 1200000
2024-02-15 | 78170 | 78.17 | 7.02 | 7.73 | 135 | 18 | 284 | 48 | 264 | 27 | NA | 600 | 0.3 | 23.08 | 1700000
2024-02-16 | 81620 | 81.62 | 7.08 | 7.65 | 130 | 17 | 288 | 44 | 259 | 28 | NA | 700 | 0.3 | 22.77 | 1300000
2024-02-17 | 80150 | 80.15 | 7.06 | 7.69 | 140 | 19 | 292 | 44 | 266 | 26 | NA | 400 | 0.3 | 23.45 | 1400000
2024-02-18 | 80260 | 80.26 | 7.05 | 7.72 | 130 | 17 | 280 | 48 | 261 | 27 | NA | 600 | 0.2 | 23.69 | 1200000
2024-02-19 | 78860 | 78.86 | 7.02 | 7.65 | 135 | 18 | 284 | 44 | 265 | 28 | NA | 500 | 0.3 | 23.78 | 1700000
2024-02-20 | 80730 | 80.73 | 7.03 | 7.69 | 125 | 17 | 288 | 48 | 269 | 26 | NA | 400 | 0.3 | 22.64 | 1400000
2024-02-21 | 80390 | 80.39 | 7.07 | 7.72 | 130 | 16 | 280 | 44 | 257 | 25 | NA | 600 | 0.2 | 23.6 | 1700000
2024-02-22 | 85290 | 85.29 | 7.12 | 7.68 | 135 | 17 | 284 | 48 | 265 | 27 | NA | 500 | 0.3 | 23.33 | 1300000
2024-02-23 | 81960 | 81.96 | 7.08 | 7.73 | 140 | 18 | 276 | 44 | 259 | 26 | NA | 400 | 0.3 | 22.74 | 1200000
2024-02-24 | 83130 | 83.13 | 7.13 | 7.76 | 130 | 17 | 280 | 48 | 261 | 27 | NA | 700 | 0.3 | 23.69 | 1700000
2024-02-25 | 78670 | 78.67 | 7.15 | 7.78 | 125 | 16 | 288 | 44 | 258 | 25 | NA | 500 | 0.3 | 23.52 | 1400000
2024-02-26 | 76470 | 76.47 | 7.12 | 7.74 | 130 | 17 | 284 | 44 | 265 | 26 | NA | 600 | 0.2 | 24.26 | 1700000
2024-02-27 | 76990 | 76.99 | 7.09 | 7.71 | 135 | 18 | 280 | 48 | 266 | 27 | NA | 400 | 0.3 | 23.6 | 1400000
2024-02-28 | 77560 | 77.56 | 7.07 | 7.76 | 140 | 19 | 284 | 44 | 259 | 26 | NA | 500 | 0.3 | 23.37 | 1700000
2024-02-29 | 73420 | 73.42 | 7.08 | 7.78 | 125 | 16 | 288 | 48 | 262 | 25 | NA | 700 | 0.3 | 22.86 | 1300000
Average | 80027.2414 | 80.0272 | 7.0076 | 7.7124 | 132.5862 | 17.4138 | 284.2759 | 45.6552 | 261.8966 | 26.9655 |  | 544.8276 | 0.28276 | 23.2545 | 1431034.4828
2320.79
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 73420 | 73.42 | 6.84 | 7.65 | 125 | 16 | 276 | 44 | 253 | 25 |  | 400 | 0.2 | 22.49 | 1200000
Max | 88870 | 88.87 | 7.15 | 7.78 | 140 | 19 | 296 | 48 | 269 | 29 |  | 700 | 0.3 | 24.26 | 1700000