## Naini I
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final BOD (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-01-01 | 114800 | 114.8 | 7.28 | 7.34 | 143 | 20 | 356 | 40 | 298 | 30 | NA | 500 | 0.2 | 22.8 | 1700000 | Sample for sludge testing is taken from sludge drying beds hence the value of sludge consistency cannot be deemed as accurate.
2022-01-02 | 113250 | 113.25 | 7.29 | 7.36 | 136 | 22 | 336 | 44 | 298 | 35 | NA | 600 | 0.3 | 23.2 | 1300000
2022-01-03 | 110430 | 110.43 | 7.32 | 7.41 | 126 | 20 | 340 | 40 | 307 | 33 | NA | 700 | 0.2 | 22.5 | 1400000
2022-01-04 | 113920 | 113.92 | 7.38 | 7.46 | 133 | 23 | 328 | 48 | 308 | 36 | NA | 400 | 0.3 | 23.5 | 1200000
2022-01-05 | 116740 | 116.74 | 7.29 | 7.33 | 129 | 22 | 336 | 44 | 301 | 32 | NA | 500 | 0.3 | 22.9 | 1700000
2022-01-06 | 115990 | 115.99 | 7.33 | 7.38 | 126 | 19 | 320 | 40 | 296 | 34 | NA | 600 | 0.2 | 22.8 | 1300000
2022-01-07 | 124400 | 124.4 | 7.29 | 7.36 | 133 | 18 | 340 | 36 | 294 | 31 | NA | 700 | 0.3 | 23.2 | 1400000
2022-01-08 | 129840 | 129.84 | 7.28 | 7.41 | 129 | 20 | 336 | 40 | 296 | 33 | NA | 500 | 0.2 | 23.3 | 1200000
2022-01-09 | 131340 | 131.34 | 7.32 | 7.38 | 126 | 22 | 328 | 44 | 291 | 30 | NA | 600 | 0.3 | 23.1 | 1300000
2022-01-10 | 120580 | 120.58 | 7.29 | 7.37 | 133 | 24 | 336 | 48 | 302 | 32 | NA | 400 | 0.2 | 23.2 | 1700000
2022-01-11 | 111680 | 111.68 | 7.36 | 7.42 | 136 | 19 | 340 | 40 | 307 | 35 | NA | 500 | 0.3 | 23.5 | 1200000
2022-01-12 | 121780 | 121.78 | 7.28 | 7.46 | 129 | 22 | 336 | 44 | 303 | 33 | NA | 700 | 0.2 | 23.6 | 1400000
2022-01-13 | 114240 | 114.24 | 7.33 | 7.36 | 136 | 20 | 344 | 40 | 308 | 31 | NA | 400 | 0.3 | 23.2 | 1300000
2022-01-14 | 116230 | 116.23 | 7.29 | 7.35 | 139 | 18 | 352 | 36 | 303 | 32 | NA | 700 | 0.2 | 23.5 | 1100000
2022-01-15 | 117750 | 117.75 | 7.33 | 7.36 | 126 | 21 | 332 | 40 | 306 | 30 | NA | 500 | 0.3 | 23.3 | 1200000
2022-01-16 | 116670 | 116.67 | 7.29 | 7.35 | 133 | 19 | 324 | 44 | 302 | 33 | NA | 400 | 0.2 | 23.2 | 1400000
2022-01-17 | 116670 | 116.67 | 7.33 | 7.38 | 126 | 24 | 336 | 48 | 299 | 30 | NA | 500 | 0.3 | 23.2 | 1300000
2022-01-18 | 116310 | 116.31 | 7.19 | 7.28 | 139 | 25 | 352 | 48 | 300 | 32 | NA | 600 | 0.3 | 23.7 | 1700000
2022-01-19 | 116080 | 116.08 | 7.33 | 7.36 | 129 | 23 | 340 | 44 | 306 | 34 | NA | 500 | 0.2 | 23.5 | 1200000
2022-01-20 | 118930 | 118.93 | 7.28 | 7.33 | 133 | 22 | 332 | 36 | 299 | 31 | NA | 600 | 0.3 | 23.6 | 1400000
2022-01-21 | 117020 | 117.02 | 7.33 | 7.35 | 126 | 24 | 336 | 40 | 302 | 32 | NA | 700 | 0.3 | 23.5 | 1300000
2022-01-22 | 115190 | 115.19 | 7.29 | 7.33 | 133 | 24 | 344 | 48 | 305 | 30 | NA | 500 | 0.2 | 23.6 | 1400000
2022-01-23 | 117080 | 117.08 | 7.36 | 7.44 | 126 | 20 | 328 | 40 | 308 | 32 | NA | 600 | 0.3 | 23.3 | 1300000
2022-01-24 | 116980 | 116.98 | 7.28 | 7.36 | 129 | 22 | 332 | 36 | 303 | 33 | NA | 500 | 0.2 | 23.5 | 1700000
2022-01-25 | 116160 | 116.16 | 7.36 | 7.35 | 136 | 20 | 336 | 40 | 306 | 30 | NA | 400 | 0.3 | 23.2 | 1200000
2022-01-26 | 113200 | 113.2 | 7.42 | 7.49 | 129 | 18 | 332 | 32 | 312 | 32 | NA | 700 | 0.2 | 23.7 | 1200000
2022-01-27 | 114330 | 114.33 | 7.28 | 7.36 | 133 | 21 | 344 | 44 | 304 | 34 | NA | 600 | 0.3 | 23.2 | 1700000
2022-01-28 | 108290 | 108.29 | 7.31 | 7.38 | 126 | 23 | 332 | 48 | 302 | 36 | NA | 500 | 0.2 | 23.6 | 1300000
2022-01-29 | 113310 | 113.31 | 7.33 | 7.36 | 129 | 21 | 328 | 44 | 305 | 32 | NA | 400 | 0.2 | - | 1400000 | Both dewatering feed pumps were in maintenance, hence dewatering unit was not operated.
2022-01-30 | 115530 | 115.53 | 7.28 | 7.35 | 136 | 19 | 340 | 40 | 298 | 35 | NA | 700 | 0.3 | 23.2 | 1200000
2022-01-31 | 116210 | 116.21 | 7.33 | 7.41 | 139 | 22 | 352 | 48 | 302 | 33 | NA | 600 | 0.2 | - | 1700000 | Both dewatering feed pumps were in maintenance, hence dewatering unit was not operated.
Average | 116804.1935 | 116.8042 | 7.3113 | 7.3752 | 131.6774 | 21.1935 | 337.0323 | 42.0645 | 302.2903 | 32.4516 | NA | 551.6129 | 0.25161 | 23.2966 | 1380645.1613
3620.93
Source: | Logbook of Labarotory at Sewage Treament Plant

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <30 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-01-01 | 75490 | 75.49 | 7.45 | 7.69 | 125 | 18 | 321 | 48 | 265 | 29 | NA | 900 | 0.2 | 24.25 | 1700000 | Retaining wall of tapping point for Rajapur SPS is broken hence raw water is going directly into the river.
2022-01-02 | 76360 | 76.36 | 7.43 | 7.66 | 130 | 17 | 328 | 44 | 286 | 27 | NA | 700 | 0.2 | 22.84 | 1400000
2022-01-03 | 76200 | 76.2 | 7.48 | 7.67 | 155 | 19 | 348 | 48 | 295 | 28 | NA | 700 | 0.3 | 24.54 | 1700000
2022-01-04 | 75780 | 75.78 | 7.46 | 7.6 | 135 | 16 | 328 | 40 | 265 | 26 | NA | 500 | 0.4 | 22.42 | 1100000
2022-01-05 | 77450 | 77.45 | 7.48 | 7.65 | 130 | 18 | 312 | 36 | 240 | 24 | NA | 700 | 0.2 | 21.98 | 1700000
2022-01-06 | 87580 | 87.58 | 7.5 | 7.68 | 140 | 17 | 324 | 44 | 288 | 26 | NA | 600 | 0.2 | 23.52 | 1400000
2022-01-07 | 94490 | 94.49 | 7.45 | 7.63 | 125 | 15 | 320 | 48 | 246 | 28 | NA | 500 | 0.2 | 22.62 | 1200000
2022-01-08 | 88630 | 88.63 | 7.43 | 7.64 | 130 | 18 | 340 | 44 | 292 | 27 | NA | 700 | 0.3 | 24.68 | 1300000
2022-01-09 | 94280 | 94.28 | 7.46 | 7.62 | 140 | 16 | 332 | 40 | 284 | 25 | NA | 600 | 0.2 | 23.48 | 1100000
2022-01-10 | 90010 | 90.01 | 7.45 | 7.68 | 145 | 15 | 336 | 48 | 288 | 26 | NA | 600 | 0.2 | 21.95 | 1400000
2022-01-11 | 79720 | 79.72 | 7.49 | 7.69 | 160 | 14 | 352 | 48 | 324 | 29 | NA | 500 | 0.2 | 25.42 | 1300000
2022-01-12 | 81610 | 81.61 | 7.5 | 7.67 | 135 | 16 | 332 | 44 | 295 | 27 | NA | 400 | 0.2 | 24.58 | 1700000
2022-01-13 | 79470 | 79.47 | 7.52 | 7.68 | 140 | 15 | 328 | 40 | 326 | 25 | NA | 700 | 0.2 | 26.34 | 1700000
2022-01-14 | 81000 | 81 | 7.5 | 7.75 | 145 | 17 | 324 | 40 | 302 | 28 | NA | 700 | 0.3 | 23.58 | 1100000
2022-01-15 | 78190 | 78.19 | 7.48 | 7.78 | 135 | 15 | 320 | 36 | 275 | 24 | NA | 500 | 0.2 | 24.82 | 1400000
2022-01-16 | 75310 | 75.31 | 7.56 | 7.72 | 120 | 13 | 316 | 36 | 256 | 21 | NA | 600 | 0.3 | 23.54 | 1300000
2022-01-17 | 77190 | 77.19 | 7.52 | 7.78 | 125 | 14 | 324 | 40 | 280 | 23 | NA | 700 | 0.2 | 26.58 | 1400000
2022-01-18 | 78090 | 78.09 | 7.5 | 7.75 | 135 | 16 | 328 | 44 | 292 | 25 | NA | 400 | 0.2 | 24.42 | 1700000
2022-01-19 | 76230 | 76.23 | 7.56 | 7.68 | 130 | 18 | 316 | 36 | 258 | 24 | NA | 600 | 0.2 | 23.62 | 1700000
2022-01-20 | 78070 | 78.07 | 7.48 | 7.67 | 140 | 18 | 320 | 40 | 264 | 26 | NA | 500 | 0.3 | 22.95 | 1200000
2022-01-21 | 81710 | 81.71 | 7.35 | 7.69 | 145 | 17 | 328 | 40 | 298 | 25 | NA | 700 | 0.2 | 25.48 | 1400000
2022-01-22 | 78650 | 78.65 | 7.3 | 7.72 | 120 | 15 | 272 | 44 | 240 | 27 | NA | 400 | 0.2 | 26.58 | 1300000
2022-01-23 | 85690 | 85.69 | 7.4 | 7.69 | 130 | 18 | 308 | 48 | 285 | 28 | NA | 500 | 0.2 | 24.94 | 1700000
2022-01-24 | 78540 | 78.54 | 7.36 | 7.62 | 124 | 16 | 324 | 48 | 264 | 26 | NA | 700 | 0.3 | 23.18 | 1700000
2022-01-25 | 82120 | 82.12 | 7.32 | 7.63 | 125 | 17 | 304 | 40 | 276 | 24 | NA | 600 | 0.2 | 22.52 | 1200000
2022-01-26 | 79620 | 79.62 | 7.41 | 7.62 | 140 | 18 | 328 | 44 | 296 | 27 | NA | 600 | 0.2 | 25.42 | 1400000
2022-01-27 | 81280 | 81.28 | 7.45 | 7.6 | 155 | 18 | 348 | 40 | 312 | 25 | NA | 400 | 0.2 | 21.98 | 1200000
2022-01-28 | 82320 | 82.32 | 7.42 | 7.61 | 145 | 16 | 340 | 44 | 308 | 28 | NA | 500 | 0.2 | 22.53 | 1400000
2022-01-29 | 80950 | 80.95 | 7.56 | 7.56 | 135 | 14 | 332 | 40 | 312 | 24 | NA | 700 | 0.3 | 23.18 | 1700000
2022-01-30 | 82150 | 82.15 | 7.5 | 7.68 | 125 | 17 | 324 | 26 | 286 | 26 | NA | 600 | 0.2 | 21.56 | 1300000
2022-01-31 | 80920 | 80.92 | 7.45 | 7.69 | 130 | 15 | 328 | 24 | 292 | 24 | NA | 700 | 0.2 | 24.08 | 1200000
Average | 81132.2581 | 81.1323 | 7.4587 | 7.671 | 135.2903 | 16.3226 | 325.3226 | 41.3548 | 283.5484 | 25.871 | NA | 596.7742 | 0.22903 | 23.8574 | 1419354.8387
2515.1
Source: | Logbook of Labarotory at Sewage Treament Plant