## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-01-01 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | 23.06 | 1400000 | Naini-I STP was shutdown from 12:05 AM on 30.12.2023 for replacement of flowmeter in outlet line of STP. Subsequently, Gaughat MPS & Chacharnalla SPS were also shutdown.
2024-01-02 | 28320 | 28.32 | 7.09 | 7.33 | 130 | 23 | 312 | 48 | 278 | 44 | NA | - | - | 23.84 | 1700000 | Naini-I STP was started at 12:00 PM with single pump from Gaughat MPS for supplying water for irrigation purpose only as shutdown work was not completed. Chacharnalla SPS was not started. Since the effluent was not taken into CCT, chlorine dosing was not started and fecal coliform of elluent was not tested.
2024-01-03 | 32380 | 32.38 | 7.07 | 7.29 | 135 | 22 | 304 | 40 | 282 | 38 | NA | - | - | 23.8 | 1100000
2024-01-04 | 54540 | 54.54 | 7.11 | 7.42 | 125 | 21 | 292 | 44 | 266 | 40 | NA | 600 | 0.3 | 23.4 | 1400000 | 100% operations of Naini-I STP was started at 3:00 PM on 04.01.2024. Subsequently, Gaughat MPS & Chacharnalla SPS were also started.
2024-01-05 | 99110 | 99.11 | 7.17 | 7.25 | 130 | 20 | 304 | 40 | 273 | 39 | NA | 700 | 0.3 | 24.11 | 1200000
2024-01-06 | 99320 | 99.32 | 7.21 | 7.24 | 135 | 21 | 300 | 44 | 278 | 40 | NA | 400 | 0.3 | 23.8 | 1700000
2024-01-07 | 99930 | 99.93 | 7.15 | 7.22 | 125 | 24 | 308 | 48 | 275 | 38 | NA | 600 | 0.2 | 23.58 | 1100000
2024-01-08 | 102840 | 102.84 | 7.05 | 7.17 | 130 | 23 | 304 | 40 | 271 | 37 | NA | 600 | 0.3 | 23.5 | 1400000
2024-01-09 | 100110 | 100.11 | 7.07 | 7.21 | 140 | 24 | 312 | 48 | 268 | 45 | NA | 500 | 0.3 | 24.03 | 1200000
2024-01-10 | 99670 | 99.67 | 7.06 | 7.16 | 125 | 22 | 304 | 44 | 278 | 40 | NA | 700 | 0.2 | 23.1 | 1300000
2024-01-11 | 101360 | 101.36 | 7.21 | 7.24 | 135 | 25 | 296 | 48 | 273 | 39 | NA | 600 | 0.3 | 22.85 | 1200000
2024-01-12 | 101790 | 101.79 | 7.19 | 7.22 | 125 | 23 | 304 | 40 | 267 | 38 | NA | 400 | 0.2 | 24.05 | 1700000
2024-01-13 | 101960 | 101.96 | 7.22 | 7.24 | 130 | 21 | 300 | 40 | 273 | 40 | NA | 500 | 0.3 | 23.6 | 1100000
2024-01-14 | 101360 | 101.36 | 7.18 | 7.23 | 140 | 22 | 312 | 44 | 275 | 39 | NA | 700 | 0.2 | 22.98 | 1200000
2024-01-15 | 97790 | 97.79 | 7.21 | 7.26 | 125 | 24 | 292 | 44 | 268 | 40 | NA | 400 | 0.3 | 23.06 | 1400000
2024-01-16 | 99780 | 99.78 | 7.14 | 7.19 | 135 | 21 | 308 | 40 | 278 | 37 | NA | 700 | 0.2 | 22.91 | 1300000
2024-01-17 | 102420 | 102.42 | 7.12 | 7.17 | 135 | 23 | 296 | 44 | 269 | 39 | NA | 600 | 0.3 | 23.1 | 1100000
2024-01-18 | 97940 | 97.94 | 7.19 | 7.15 | 140 | 22 | 304 | 40 | 279 | 40 | NA | 400 | 0.2 | 22.6 | 1700000
2024-01-19 | 104550 | 104.55 | 7.23 | 7.26 | 125 | 20 | 292 | 36 | 284 | 38 | NA | 500 | 0.3 | 23.7 | 1300000
2024-01-20 | 102420 | 102.42 | 7.24 | 7.28 | 130 | 23 | 296 | 40 | 265 | 37 | NA | 700 | 0.2 | 23.1 | 1200000
2024-01-21 | 106340 | 106.34 | 7.19 | 7.23 | 135 | 25 | 304 | 48 | 271 | 41 | NA | 500 | 0.2 | 22.79 | 1200000
2024-01-22 | 103640 | 103.64 | 7.17 | 7.19 | 130 | 21 | 288 | 44 | 267 | 42 | NA | 700 | 0.3 | 22.6 | 1400000
2024-01-23 | 97950 | 97.95 | 7.13 | 7.17 | 140 | 23 | 304 | 40 | 270 | 39 | NA | 400 | 0.2 | 23.12 | 1100000
2024-01-24 | 102880 | 102.88 | 7.15 | 7.19 | 125 | 20 | 308 | 44 | 276 | 41 | NA | 500 | 0.3 | 22.71 | 1300000
2024-01-25 | 104930 | 104.93 | 7.17 | 7.22 | 130 | 19 | 296 | 44 | 263 | 44 | NA | 600 | 0.2 | 23.1 | 1300000
2024-01-26 | 103530 | 103.53 | 7.19 | 7.26 | 125 | 20 | 312 | 36 | 275 | 39 | NA | 500 | 0.2 | 23.14 | 1200000
2024-01-27 | 107020 | 107.02 | 7.11 | 7.23 | 135 | 21 | 304 | 44 | 269 | 43 | NA | 400 | 0.3 | 22.91 | 1700000
2024-01-28 | 104750 | 104.75 | 7.09 | 7.17 | 130 | 23 | 296 | 40 | 274 | 41 | NA | 700 | 0.3 | 22.85 | 1400000
2024-01-29 | 106010 | 106.01 | 7.21 | 7.29 | 125 | 25 | 312 | 48 | 267 | 42 | NA | 500 | 0.2 | 23.13 | 1100000
2024-01-30 | 103650 | 103.65 | 7.19 | 7.26 | 140 | 22 | 292 | 44 | 273 | 42 | NA | 800 | 0.2 | 22.66 | 1700000
2024-01-31 | 99360 | 99.36 | 7.13 | 7.19 | 130 | 24 | 308 | 48 | 277 | 41 | NA | 400 | 0.3 | 22.89 | 1300000
Average | 92504.8387 | 92.5048 | 7.1547 | 7.231 | 131.3333 | 22.2333 | 302.1333 | 43.0667 | 272.7333 | 40.1 |  | 557.1429 | 0.25357 | 23.2281 | 1335483.871
2867.65
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.05 | 7.15 | 125 | 19 | 288 | 36 | 263 | 37 |  | 400 | 0.2 | 22.6 | 1100000
Max | 107020 | 107.02 | 7.24 | 7.42 | 140 | 25 | 312 | 48 | 284 | 45 |  | 800 | 0.3 | 24.11 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-01-01 | 76830 | 76.83 | 7.28 | 7.76 | 135 | 18 | 284 | 44 | 265 | 25 | NA | 400 | 0.3 | 24.37 | 1300000
2024-01-02 | 74220 | 74.22 | 7.29 | 7.74 | 130 | 16 | 292 | 40 | 268 | 27 | NA | 600 | 0.3 | 23.57 | 1400000
2024-01-03 | 69310 | 69.31 | 7.24 | 7.75 | 135 | 17 | 288 | 44 | 258 | 26 | NA | 700 | 0.2 | 23.35 | 1200000
2024-01-04 | 77390 | 77.39 | 7.22 | 7.76 | 125 | 16 | 276 | 40 | 262 | 24 | NA | 500 | 0.3 | 22.86 | 1700000
2024-01-05 | 70810 | 70.81 | 7.16 | 7.77 | 130 | 17 | 272 | 44 | 259 | 25 | NA | 600 | 0.3 | 23.58 | 1300000
2024-01-06 | 74810 | 74.81 | 7.21 | 7.74 | 120 | 16 | 284 | 40 | 263 | 26 | NA | 400 | 0.2 | 23.74 | 1400000
2024-01-07 | 76150 | 76.15 | 7.23 | 7.75 | 125 | 17 | 288 | 40 | 261 | 25 | NA | 500 | 0.3 | 22.52 | 1200000
2024-01-08 | 74150 | 74.15 | 7.25 | 7.73 | 130 | 18 | 284 | 44 | 265 | 24 | NA | 600 | 0.3 | 22.9 | 1700000
2024-01-09 | 72520 | 72.52 | 7.18 | 7.76 | 125 | 17 | 276 | 40 | 258 | 25 | NA | 400 | 0.3 | 22.44 | 1400000
2024-01-10 | 75130 | 75.13 | 7.24 | 7.72 | 135 | 18 | 292 | 44 | 253 | 26 | NA | 700 | 0.2 | 23.37 | 1300000
2024-01-11 | 72080 | 72.08 | 7.26 | 7.75 | 130 | 16 | 288 | 44 | 265 | 24 | NA | 600 | 0.3 | 22.5 | 1400000
2024-01-12 | 68350 | 68.35 | 7.28 | 7.77 | 135 | 17 | 284 | 40 | 257 | 26 | NA | 500 | 0.2 | 23.02 | 1700000
2024-01-13 | 71160 | 71.16 | 7.29 | 7.86 | 140 | 17 | 296 | 44 | 264 | 25 | NA | 400 | 0.2 | 22.76 | 1300000
2024-01-14 | 75370 | 75.37 | 7.17 | 7.81 | 135 | 16 | 292 | 40 | 253 | 26 | NA | 600 | 0.3 | 22.67 | 1200000
2024-01-15 | 74920 | 74.92 | 7.16 | 7.79 | 130 | 17 | 276 | 40 | 257 | 25 | NA | 700 | 0.3 | 23.56 | 1700000
2024-01-16 | 73850 | 73.85 | 7.14 | 7.78 | 140 | 18 | 284 | 48 | 267 | 28 | NA | 400 | 0.2 | 23.04 | 1300000
2024-01-17 | 71860 | 71.86 | 7.18 | 7.75 | 145 | 19 | 292 | 44 | 256 | 28 | NA | 500 | 0.3 | 22.63 | 1200000
2024-01-18 | 72150 | 72.15 | 7.17 | 7.69 | 135 | 17 | 280 | 40 | 264 | 27 | NA | 500 | 0.3 | 23.11 | 1400000
2024-01-19 | 73220 | 73.22 | 7.2 | 7.57 | 125 | 16 | 260 | 44 | 265 | 28 | NA | 600 | 0.2 | 22.71 | 1700000
2024-01-20 | 73720 | 73.72 | 7.08 | 7.75 | 130 | 17 | 276 | 40 | 259 | 26 | NA | 400 | 0.3 | 23.5 | 1400000
2024-01-21 | 74440 | 74.44 | 7.06 | 7.69 | 135 | 18 | 284 | 44 | 263 | 27 | NA | 500 | 0.3 | 23.23 | 1300000
2024-01-22 | 73070 | 73.07 | 7.03 | 7.68 | 125 | 17 | 288 | 48 | 263 | 28 | NA | 700 | 0.2 | 23.59 | 1200000
2024-01-23 | 73960 | 73.96 | 7.09 | 7.7 | 135 | 19 | 280 | 44 | 265 | 27 | NA | 600 | 0.3 | 23.6 | 1400000
2024-01-24 | 74190 | 74.19 | 7.14 | 7.71 | 130 | 18 | 292 | 48 | 271 | 29 | NA | 400 | 0.3 | 22.56 | 1700000
2024-01-25 | 81740 | 81.74 | 7.16 | 7.74 | 135 | 18 | 284 | 44 | 264 | 27 | NA | 500 | 0.3 | 23 | 1200000
2024-01-26 | 82930 | 82.93 | 7.11 | 7.67 | 130 | 17 | 280 | 44 | 261 | 26 | NA | 700 | 0.3 | 23.4 | 1700000
2024-01-27 | 78340 | 78.34 | 7.07 | 7.66 | 140 | 18 | 276 | 48 | 257 | 27 | NA | 400 | 0.3 | 22.53 | 1400000
2024-01-28 | 82260 | 82.26 | 7.04 | 7.63 | 125 | 17 | 288 | 44 | 265 | 28 | NA | 600 | 0.3 | 22.87 | 1300000
2024-01-29 | 84010 | 84.01 | 7.06 | 7.62 | 130 | 18 | 284 | 48 | 267 | 27 | NA | 500 | 0.2 | 23.34 | 1700000
2024-01-30 | 84460 | 84.46 | 7.04 | 7.63 | 125 | 16 | 280 | 44 | 263 | 26 | NA | 700 | 0.3 | 22.52 | 1400000
2024-01-31 | 82400 | 82.4 | 7.02 | 7.65 | 135 | 17 | 296 | 48 | 261 | 28 | NA | 400 | 0.3 | 23.66 | 1300000
Average | 75477.4194 | 75.4774 | 7.1629 | 7.7219 | 131.6129 | 17.1935 | 283.7419 | 43.4839 | 261.9032 | 26.3226 |  | 535.4839 | 0.27097 | 23.1129 | 1412903.2258
2339.8
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 68350 | 68.35 | 7.02 | 7.57 | 120 | 16 | 260 | 40 | 253 | 24 |  | 400 | 0.2 | 22.44 | 1200000
Max | 84460 | 84.46 | 7.29 | 7.86 | 145 | 19 | 296 | 48 | 271 | 29 |  | 700 | 0.3 | 24.37 | 1700000